SOAH DOCKET NO. 473-99-0821

PUC DOCKET NO. 20516

APPLICATION OF BRAZOS ELECTRIC	§		BEFORE THE STATE OFFICE

POWER COOPERATIVE, INC. TO 	§

AMEND A CERTIFICATE OF 	§

CONVENIENCE AND NECESSITY TO	§				OF

CONSTRUCT A PROPOSED 	§

TRANSMISSION LINE WITHIN	§

COOKE COUNTY	§		ADMINISTRATIVE HEARINGS

TABLE OF CONTENTS

(Filename: nelsnbrf.wpd)

I.	Introduction	3

II.	Governing Legal Principles	4

A.	Jurisdiction	4

B.	Criteria for Granting or Denying A Certificate of Convenience and Necessity	5

C.	Burden of Proof	6

III.	Need	7

A.	Adequacy of Existing Service	7

B.	Need for Additional Service	8

C.	Effect of Granting the Certificate on the Recipient of the Certificate and any

Electric Utility Serving the Proximate Area. . . . . . . . . . . . . . . . . . . . . . . . . . . . . .11

IV.	Routing	13

A.	Selection of Alternatives	13

B.	Other Factors	15

1.	Community Values	15

2.	Recreational and Park Areas	15

3.	Historical and Aesthetic Values	16

a.	Archeological Areas	16

b.	Historical Areas	17

c.	Aesthetics	18

4.	Environmental Integrity	19

a.	Prudent Avoidance	19

5.	Probable Improvement of Service or Lowering of Cost to Consumers

in the Area if the Certificate is Granted	21

C.	Balancing Competing Factors	21

V.	Conclusion	26

Certificate of Service . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .27

SOAH DOCKET NO. 473-99-0821

PUC DOCKET NO. 20516

APPLICATION OF BRAZOS ELECTRIC	§		BEFORE THE STATE OFFICE

POWER COOPERATIVE, INC. TO 	§

AMEND A CERTIFICATE OF 	§

CONVENIENCE AND NECESSITY TO	§				OF

CONSTRUCT A PROPOSED 	§

TRANSMISSION LINE WITHIN	§

COOKE COUNTY	§		ADMINISTRATIVE HEARINGS

POST HEARING BRIEF OF THE NELSON FAMILY

The Nelson Family files this, its Post Hearing Brief in opposition to the application of Brazos Electric Power Cooperative, Inc. (“Brazos Electric”) for a Certificate of Convenience and Necessity, and would respectfully show the following:

I.	Introduction

Brazos Electric has failed to meet its burden of proof in this certificate proceeding.  Brazos Electric has failed to demonstrate need beyond the fact that any looped line is more reliable than a radial line.  Certainly Brazos Electric has failed to demonstrate immediate need.  If looping a line to improve reliability is all that is required to establish need, then there should be no radial lines in Texas.  Stating the converse, an electric utility would fail to meet its obligation to serve the public if it allows radial lines on its system, exposes the flaw.  Obviously, it is not true.  All systems have radial lines serving loads and most are indeed reliable.  In this case, Brazos Electric wants to construct new facilities to market its services to new load, and the customers served by Cooke County Electric Cooperative will bear the burden of the line and be, at best, just incidental beneficiaries.

Brazos Electric has failed to identify and evaluate reasonable alternatives.  It has failed to fairly and fully evaluate the alternatives selected.  Based on Brazos Electric’s position regarding the reliability of double circuiting lines, Brazos Electric has biased the evaluation process and predetermined the outcome of what little evaluation it did perform.  Brazos Electric has ignored known historical sites, failed to understand or apply prudent avoidance criteria and does not support its conclusions regarding its preferred route.  As will be more fully explained below, Brazos Electric’s application for a certificate should be denied.

II.	Governing Legal Principles

A.	Jurisdiction

Brazos Electric is an electric utility for purposes of Tex. Util. Code Chapter 37 relating to Certificates of Convenience and Necessity (“CCN”).  Generally, an electric utility is required to obtain a CCN from the PUCT to provide service to the public.  More specifically, Tex. Util. Code §37.051(a) states:

An electric utility may not directly or indirectly provide service to the public under a franchise or permit unless the utility first obtains from the commission a certificate that states that the public convenience and necessity requires or will require the installation, operation, or extension of the service.

The term “service” is defined in Tex. Util. Code §11.003 as follows:

(19)	“Service” has its broadest and most inclusive meaning.  The term includes any act performed, anything supplied, and any facilities used or supplied by a public utility in the performance of the utility’s duties under this title to its patrons, employees, other public utilities, an electric cooperative, and the public.  The term also includes the interchange of facilities between two or more public utilities.  The term does not include the printing, distribution, or sale of advertising in a telephone directory.

An electric utility that wants to obtain or amend a certificate must submit an application to the Commission.  The distinction between obtaining a CCN and obtaining an amendment to a CCN is merely that a CCN is granted to a new electric utility while an amendment is granted to an existing certificate holder.  The legal requirements are the same for either a new certificate or an amendment to an existing certificate.  More specifically, the PUCT can grant a CCN, or an amendment to an existing CCN, only if the Commission finds that the CCN, or an amendment to an existing CCN, is necessary for the service, accommodation, and convenience, or safety of the public.  The Commission may grant the certificate, or an amendment to an existing CCN, as requested, grant a portion of the request, or refuse to grant the certificate or amendment.  In addition, the Commission has the general power to regulate and supervise the business of each public utility under its jurisdiction and to do anything specifically designated or implied by the Texas Utilities Code that is necessary or convenient to the exercise of the power and jurisdiction granted to the PUCT by the Texas Legislature.

B.	Criteria for Granting or Denying A Certificate of Convenience and Necessity

The criteria for granting or denying an application for a certificate is contained in Tex. Util. Code §37.056.  An application can be granted only if the Commission affirmatively finds that the certificate is necessary for the service, accommodation, convenience, or safety of the public.  In addition, the Commission must consider the following: (1) the adequacy of existing service; (2) the need for additional service; (3) the effect of granting the certificate on the recipient of the certificate and any electric utility serving the proximate area; and (4) other factors such as community values, recreational and park areas, historical and aesthetic values, environmental integrity, and the probable improvement of service or lowering of cost to consumers in the area if the certificate is granted.

C.	Burden of Proof

The burden of proof is on the applicant, Brazos Electric.  To meet its burden of proof,  Brazos Electric has placed its application into evidence.  In addition, Brazos Electric offered the testimony of three witnesses, Mr. Townsend, Mr. Beckman, and Mr. Petter.  They make essentially bald statements concluding that Brazos Electric’s preferred route is the best route for the proposed transmission line.  Brazos Electric provided little or nothing to explain how the general information contained in the application was evaluated.  Brazos Electric provided little or nothing to explain the many significant inconsistencies in its application.  Brazos Electric provided no workpapers, analyses or other supporting documents beyond that contained in its application to explain its conclusions.  Unchallenged, Brazos Electric’s meager and elusive evidentiary showing might be viewed as sustaining its minimum burden of proof.  But Brazos Electric’s application regarding need and routing has been challenged.  The burden of persuasion shifts to the challenging parties to show that Brazos Electric has failed to support its conclusions regarding need and preferred route, but the burden of proof remains with Brazos Electric to demonstrate by a preponderance of the evidence that the requested certificate should be granted.  Brazos Electric chose not to file rebuttal evidence and, instead, relied upon its witnesses to sustain its burden of proof during cross-examination.  As a result, Brazos Electric failed to provide record evidence to adequately support its requested certificate and its conclusions regarding the best route.  Brazos Electric’s application should be denied because it failed to meet its burden of proof.

III.	Need

A.	Adequacy of Existing Service

The existing service provided by Brazos Electric to Cooke County Electric Cooperative is certainly very good and perhaps even excellent.  The outage history for the Salem substation from January 1, 1989, through July 1, 1999, is contained in Nelson Exhibit No. 5.  There have been a total of fourteen outages during the ten year period reviewed with most outages lasting one to two minutes.  The longest outage was eighty-seven minutes.  In Nelson Exhibit No. 6, Brazos states that there have been no major transmission system reliability problems in the area to be served by the proposed line.  The Salem substation has experienced an average of 7.2 minutes of outage per year while Brazos Electric’s total system averaged 40.9 minutes of outage per year.   Existing service at the Salem substation exceeds the adequacy of Brazos Electric’s system as a whole.

There are neither distribution system reliability problems nor distribution voltage level problems in the area served by the Salem substation. Therefore, Brazos Electric has not identified any existing problems with the existing transmission or distribution service in the area of the proposed transmission line that will be alleviated by constructing a new transmission line.

B.	Need for Additional Service

Brazos Electric relies on the BEPC Planning Criteria and its projections of growth to establish the need for the proposed transmission line.  In addition, Brazos Electric proposes to build another substation, the Mountain Springs substation, that will be served off the existing Salem substation line and, based on the way Brazos Electric proposes to construct facilities, Brazos Electric asserts that both substations would benefit from the proposed transmission line.   Mr. Townsend testified that “the latest load on the existing Salem substation in 1998 was approximately 18MW.”  However, on cross-examination, Mr. Townsend admitted that the actual load on the existing Salem substation was “probably about 16MW” and that he knew what the actual load was in 1998 when he prepared his prefiled testimony in 1999.  The actual load was confirmed by ORA witness Ethridge.

Although Brazos Electric bases its need for the proposed transmission line on Brazos Electric’s Transmission Requirements Study for the years 1998-2000, Brazos Electric chose not to include the study as part of its record evidence.  Instead, the application contains selected excerpts from the study.  The excerpts provided by Brazos Electric consist of summary statements with no underlying support in the application.  Brazos Electric did not provide a load study, only a bare forecast.  When asked about the specific requirements for Cooke County, Mr. Townsend stated that “it is not in this study.”  The bare forecast is part of Appendix B of the application.  When asked to provide a copy of all documents supporting the load forecasts in Appendix B, Brazos Electric provided Cooke County Electric Cooperative data that was updated only through 1995 and forecasted for all years after 1995.  When asked to provide all information, including public records and demographic studies that validates the old load forecast with actual load growth data, Brazos provided nothing, but instead referred back to the old forecast.

The BEPC Planning Criteria states: “Whenever feasible, radial transmission loads of 5MW or greater with good growth potential will be provided loop transmission service to improve reliability”.  Brazos Electric relies heavily on its planning document as demonstrating a need for the additional transmission line.  There are several interesting things to note.  First, of course, is the “5MW or greater” criteria.  Clearly, the load at the Salem substation is greater than 5MW.  It is equally clear that the Salem substation did not just begin to exceed the 5MW criteria.  Yet, Brazos Electric has not been in a rush to loop the line.  In fact, Brazos Electric has thirteen radially-fed substations on its system with a load in excess of 5MW.  Perhaps the explanation for not looping the line relates to the qualifying phrase “with good growth potential.”  Mr. Townsend testified that one of the reasons that Brazos did not like the western routes was because of its proximity to an area with more potential for growth.  However, Mr. Townsend also had to admit that “growth potential” is not a PUC criteria, even though he felt it was part of community values.  Equally telling is the fact that Brazos Electric provided no studies or other evidence supporting growth or potential growth except the bare forecast already discussed.

Even though Brazos Electric has made a poor showing regarding need, the Nelson Family believes that supported growth projections, if they were in the record, might actually demonstrate a need for looping the Salem substation.  At 16MW the Salem substation is approaching the more reasonable guideline used by the Lower Colorado River Authority and other cooperatives such as Pedernales Electric Cooperative which requires looping substations with loads in excess of 20MW.  However, the important point here is simply that the need is not immediate.  If the ALJ finds that Brazos Electric has failed to meet its burden of proof, then Brazos Electric has time to prepare and support a new application and construct facilities.

C.	Effect of Granting the Certificate on the Recipient of the Certificate and any Electric Utility Serving the Proximate Area

It is perhaps here, under the heading of effect on the applicant,  that the real “need” for the new transmission line is best identified.  Brazos Electric has not demonstrated need based on the needs of Cooke County Electric Cooperative customers, but instead on the need perceived by Brazos Electric -- outside the scope of the PUC criteria -- to position itself to compete in the future.

Starting at page 13 of Brazos Electric’s application, under the heading “System Deficiencies and Analysis”, is the following statement: “Reliability of service is of increasing importance not only because of our increasing reliance on electricity, but also because of the continuing deregulation of the  utility industry and the advent of competition.”  In testimony, Brazos Electric witness Beckman states that his conclusion the proposed project best meets the need identified by Brazos Electric was based on providing “enhanced reliability in the area of the Salem substation” comparable to that experienced by most other electric customers in Texas and that “under SB7 providing comparable levels of service to all customers will be extremely important”.

SB7 is the electric industry restructuring bill passed by the Texas Legislature that became law on September 1, 1999.  In a nutshell, it provides for retail competition effective January 1, 2002, as well as a framework for the transition period.  The vast majority of SB7 does not apply to cooperatives unless and until they choose to compete.

The Nelson Family asked Brazos Electric to explain how competition in electricity impacts the need for the proposed transmission line and their response is indeed revealing.  Here are Brazos Electric’s words:

While competition was not directly considered in evaluating the need for this project, competition affects the need for this project because competition will increase the need for reliable electric service.  Any electric company perceived by the public as providing unreliable service risks losing its current and potential customers to other suppliers in a deregulated environment. (Emphasis added).

It’s all about Brazos Electric getting ready to compete in the future.  Although Brazos Electric attempts to spin a story about improved reliability to Cooke County Electric Cooperative customers in testimony prepared for the PUC in 1999, the unsanitized truth is contained in Brazos Electric’s Borrower’s Environmental Report, prepared in September, 1998.  Brazos states:

1.2   PURPOSE OF THE PROJECT

The purpose of the proposed project is to provide additional capacity and improve service and reliability to the southeastern portion of CoServ Electric’s (a member of the Brazos Electric system) service territory in the vicinity of the City of Woodbine and Lake Kiowa (Cooke County), Texas.

The improvement of service and reliability referred to by Brazos Electric in the statement above is not to the public served by the Salem substation, but is part of a marketing strategy to lure a potential future customer at the Mountain Springs substation.  Brazos Electric is using its monopoly market power to get a competitive edge at the expense of Cooke County farms and farm families.  Brazos Electric’s application should be denied because the certificate is not necessary for the service, accommodation, convenience, or safety of the public.

IV.	Routing

A.	Selection of Alternatives

There are two very troubling aspects to the alternative routes selected for study by Brazos Electric.  First, all of the routes included in the application are only a few miles apart and therefore only slightly improve reliability, yet Brazos Electric chose not to consider and evaluate at least three routes that would provide even greater reliability.  The three alternatives selected by Brazos Electric are about three miles apart.  Mr. Townsend testified that the distance between the existing Salem line and the Woodbine-to-Jordan line, at the closest point, is probably a little over four miles.  The evidence shows, and Mr. Townsend confirmed, that in the past a tornado has taken out lines approximately ten miles apart.  Where the existing and the proposed lines essentially form a rectangle of this size, a tornado on the ground in the area would potentially cross two sides of the rectangle under many scenarios and impair reliability.  Reliability could easily be improved by enlarging the rectangle, but Brazos Electric did not include such possibilities.  For example, Nelson Exhibit No. 43 shows that a loop could have been considered by Brazos Electric by connecting the Spring switching station with the proposed Mountain Springs substation and then connecting the Mountain Springs substation to the Salem substation from the south.  This would enlarge the rectangle to about five miles as well as put the proposed line in the vicinity of the folks that will be the primary beneficiaries of the looped service.

An even more reliable alternative would be to have the lines looping the Salem substation be close to 180° apart.  Nelson Exhibit No. 41 is a one line diagram of the Brazos system in the vicinity of the Salem substation and shows that the Jordan substation is to the northeast of the Salem substation.  Brazos chose not to consider looping the line to the Jordan substation.  It is a little longer, perhaps a total of ten miles, but it would be significantly more reliable because the lines looping the Salem substation would be close to 180° apart.  In fact, as a preliminary choice, it would be the most reliable of all known choices.  Mr. Townsend testified that reliability could not be quantified, but he believed that industry standards recognize that two single circuits are more reliable than a double circuit and he agreed that two single circuits at 90° to each other is less reliable than two circuits 180° apart.  Mr. Townsend also agreed that Brazos Electric could have run the line from the Jordan substation to provide looped service to the Salem substation.

Another alternate that would provide increased reliability would involve continuing the  P to B section of the eastern alternative straight north until it intercepts the TXU transmission line.  Reliability would be increased because the loop would include a feed from a line not interconnected to the existing Salem line.  It would have the added advantage of avoiding the Nelson historic farm.  However, Brazos did not include this significant alternative for study and evaluation.

The second and most troubling aspect of Brazos Electric’s application is the fact that the preferred route is viewed by Brazos Electric as significantly better than their first and second alternate routes primarily because both the first and second alternate routes require double circuiting for a portion of the routes.  This is not something that Brazos Electric discovered as it evaluated the alternatives; it is something they knew when they selected the alternatives.  Brazos Electric’s selection of alternatives is a sham if the thing that “without question” determines the best route is the fact that the other choices involve some double circuiting.   Mr. Townsend went so far as to state that in his opinion double circuiting did not even meet Brazos Electric’s planning criteria.   If double circuiting was not acceptable for planning purposes, then Brazos Electric should not have initially selected alternatives that included double circuits.  To do so taints the alternatives, biases the evaluation and predetermines the outcome.  Brazos Electric’s application should be denied because of their flawed selection and evaluation of alternative routes.

B.	Other Factors

1.	Community Values

This is a farming community and the land is of paramount important to the community.

2.	Recreational and Park Areas

There are no recreational or park areas on any of the alternative routes.

3.	Historical and Aesthetic Values

a.	Archeological Areas

Incredibly, Brazos Electric has taken the position in this proceeding that by sending a letter to the Texas Historical Commission regarding the proposed project, they have somehow fully discharged their obligation regarding identification of historic areas.  First, in response to Brazos Electric’s letter, the Historical Commission states that no survey has ever been conducted within the boundaries of the study area.  Second, the Historical Commission indicates their belief that the project area may contain archeological sites and a archeological survey should be conducted by a qualified professional.  Even though the letter from the Historical Commission is dated in June, 1998, and Brazos fully understands that one of the statutory criteria for granting or denying a certificate involves consideration of historic areas, to date Brazos Electric has chosen not to perform such a survey.  In the tradition of Nixon, Brazos Electric witness Townsend essentially says trust me and states that Brazos intends to perform an archeological survey once a final route is selected and it is committed to “mitigate anything that is found where it would not be bothered”.

Brazos Electric chooses to not distinguish between historic sites and archeological sites.  Perhaps because the name of the Commission is the Historical Commission, Brazos Electric did not seem to notice that the only thing discussed in the letter is archeological sites.  In any event, Mr. Townsend agreed that archeological sites and historical sites are not synonymous terms.  The statutory criteria requires Brazos Electric to meet its burden of proof regarding historical sites, which would necessarily include archeological sites, along the alternate routes.  However, Brazos Electric has provided no evidence of either the existence or absence of archeological or historical sites on any of the alternate routes.  Brazos Electric did indicate that it believed that the PUC guidelines only required that it contact the Historical Commission; however, the PUC guidelines for a CCN application are included as Exhibit AP-1 to the testimony of Mr. Petter and do not provide such a limited obligation.  Brazos Electric has failed to meet its burden of proof regarding archeological sites unless, of course, the ALJ determines that the notion “ignorance is bliss” applies to CCN applications in Texas.

b.	Historical Areas

There are two known historical sites on Brazos Electric’s preferred route.  The Nelson Farm and the Ware Farm are Family Land Heritage farms certificated by the Texas Department of Agriculture as being operated by the same family as a family agricultural enterprise for over 100 years.  Although both farms have log buildings of historical note, it is the farms, not the buildings, that are the subject of historical significance recognized by the Texas Department of Agriculture. Although Brazos Electric may not have known about the historical sites when it first selected the route alternatives, it certainly knew about them by the time of hearing.  Yet, it has made no effort to revise its selection of a preferred route or even revise the route to avoid the historical properties.

During cross-examination, Mr. Townsend seemed to believe that if Brazos Electric did not cross over the log buildings, then it has adequately avoided the historical sites.  Mr. Townsend fails to distinguish between historic structures and historic farms.  In Mr. Townsend’s view, all the land in Texas has some historical significance.  Contrary to Brazos Electric’s effort to minimize the significance of an important Texas cultural resource, the Commission is obligated by statute to consider historical values in deciding to grant or deny the requested certificate.  The little piece of paper issued by the Texas Department of Agriculture is a tribute to the blood, sweat and tears of Texas pioneers and their descendants that have worked the soil to make Texas great.  Its importance should not be diminished by those who fail to appreciate the significance of the family farm to our heritage and those who are blinded by greed.  Brazos Electric has options that would avoid these historical sites.  Brazos Electric has stated that it is unaware of any historical sites on either of the first or second  alternative routes.

c.	Aesthetics

Brazos Electric takes the position that if it doesn’t touch a historical site, and just cross over it, that neither the historical site nor the agricultural use of the land are really affected.  Brazos Electric ignores aesthetics.  Placing towers well above the tree line affects aesthetics generally, and certainly interferes with the visual impact associated with Heritage Farms.  Brazos Electric intends to put 60-70 poles in the ground; poles that are much taller than local trees.  With regard to the Nelson Family property specifically, the proposed line will complete a big “Z” of transmission lines across their property.  Further, Brazos electric proposes to put a switching station occupying about four acres on the Nelson property.  Brazos Electric has already done a gross disservice to the Nelsons when, many years ago, they crossed the property diagonally.  The proposed transmission line adds insult to injury and should not be allowed.

Mr. Petter testified that no matter what line is tapped some landowner will have more than one transmission line on their property.  Certainly that is true.  However, no landowner with an operating farm should be burdened with three transmission lines and a switching station on their land, much less a family that has operated a farm for well over 100 years.  This is the Nelsons only opportunity to preserve their land.  In condemnation proceedings the only question considered is the value of the land.  The right to obtain the land is decided here in this proceeding.  The power of condemnation can only be exercised if this Commission say that the taking of this land is in the public interest.  In this instance, Brazos Electric should not be given the power to take the Nelson Family land, land recognized for its historical significance, so that Brazos Electric can compete better for new loads in a future unregulated environment.  Our forefathers would turn in their graves at such a result.

4.	Environmental Integrity

a.	Prudent Avoidance

Brazos Electric recognizes that the PUC has a “prudent avoidance” policy and that it is  obligated to follow it.  Unfortunately, Brazos Electric management doesn’t have a clue what it means.  Nonetheless, all three of Brazos Electric’s witnesses testify that they believe their preferred route best meets the PUC criteria, and Mr. Petter testifies specifically about prudent avoidance.  According to Mr. Petter, prudent avoidance “describes a preferred method of routing transmission lines that minimizes, to the extent possible, the proximity of transmission lines to habitable structures, population centers, historical sites, archeological sites, [and] parks and recreational areas.”

Mr. Petter was asked whether or not prudent avoidance has anything to do with the effects of electromagnetic fields and he said that he did not think prudent avoidance addresses electromagnetic fields.  However, it does address the potential adverse health risks associated with both the  electric and magnetic fields associated with transmission lines.  Studies, starting in the late 1970s have suggested a relationship between prolonged exposure to EMFs and childhood cancers.  Other studies are to the contrary.  Experts have done battle over the issue for over twenty years with no accepted conclusions.   Every study has had its critics.  In April, 1988, the PUC commissioned a blue ribbon committee made up of professionals from several discipline to review the existing literature and monitor the ongoing research.  The Committee issued its report in March, 1992.  The Committee concluded that the evidence at that time was insufficient to conclude that exposure to EMFs pose an imminent or significant public health risk.  The term “prudent avoidance” means to limit exposures that can be avoided by making small investments of money and effort.  The PUC has followed that policy and one of the key applications of the policy is to avoid habitable structures within 200 feet of a new transmission line.  As can be seen in the chart below, Brazos Electric has failed to select a preferred route that best avoids habitable structures within 200 feet of the proposed line.

CORRECTED LIST OF HABITABLE STRUCTURES

|  | Alternate A DFEGINORST (Brazos 2nd Alternate Route) | Alternate B DCHKLMNORST (Brazos 1st Alternate Route) | Alternate C ABPQT (Brazos Preferred Route) |
| --- | --- | --- | --- |
| HABITABLE STRUCTURES |  |  |  |
| Affected Houses | 10 | 5 | 18 |
| 500 feet | 6 | 4 | 4 |
| 200 feet | 1 | 0 | 2 |

Brazos Electric’s application should be denied, as filed, because Brazos Electric has failed to follow the Commission’s prudent avoidance policy.

5.	Probable Improvement of Service or Lowering of Cost to Consumers in the Area if the Certificate is Granted

C.	Balancing Competing Factors

Brazos Electric has the burden of proof to demonstrate that its preferred route is the best alternative.  However, instead of providing reasoned analysis, quantified evaluations and understandable comparisons of the alternatives in its application and testimony, Brazos Electric has provided only summary conclusions supported by generalizations.  The record made by Brazos Electric is void of any balancing of the competing statutory factors. There is no demonstration of the burdens or benefits associated with any routing alternative.  There are no workpapers to show how Brazos Electric reached its conclusions.

The routing study provides raw data, including some incorrect data.  It also included a weighting element that Brazos Electric apparently did not use.  During cross-examination Mr. Townsend was asked to calculate the weighted factors.  The chart below shows the results of his calculations.

WEIGHTED ALTERNATE ROUTE EVALUATION

|  | Alternate A DFEGINORST (Brazos 2nd Alternate Route) | Alternate B DCHKLMNORST (Brazos 1st Alternate Route) | Alternate C ABPQT (Brazos Preferred Route) | Alternate D CHJINORST (Brazos Eliminated Route) |
| --- | --- | --- | --- | --- |
| TERRAIN/OTHER | SCORE | SCORE | SCORE | SCORE |
| Open Pasture/Range | 17400 | 17000 | 7100 | 12600 |
| Parallel Transmission Line | --- | --- | --- | --- |
| Parallel Pipe Lines | --- | --- | --- | --- |
| Parallel Railroad Lines | --- | --- | --- | --- |
| Parallel Hwy or Roads | --- | --- | --- | --- |
| Parallel Fence Lines | 8500 | 6000 | 4000 | 7600 |
| Cultivated Land-Irrigated | --- | --- | --- | --- |
| Cultivated Land - Dry | 2500 | 21750 | 10000 | 17000 |
| Potential Wetland | --- | --- | --- | --- |
| Wooded Corridor | 10500 | 8400 | 18400 | 12500 |
| Residential Area | --- | --- | --- | --- |
| Public Area | --- | --- | --- | --- |
| TOTAL SCORE | 38900 | 53150 | 39500 | 49700 |

Although these are not all of the factors to be considered, at least as to these factors Brazos Electric’s preferred route is not the best route.  The best route is Brazos Electric’s second alternate route.

Based on Brazos Electric’s prefiled testimony and the cross-examination of its witnesses, it becomes clear that for Brazos Electric the determination of the preferred route is a matter of selecting the route that does not involve double circuiting any part of the line.  Its conclusions should be firmly rejected.  Double circuiting is consistent with the PUC’s policy of using existing right-of -ways to the extent possible and minimizes the amount of new land to be burdened with a transmission line.  Contrary to some of the statements made by Mr. Townsend, double circuiting is consistent with Brazos Electric’s planning criteria and acceptable to it.  The Nelson Family certainly respects the fact that double circuiting is less reliable than two single circuits, but as discussed above, if the difference in reliability is that significant and that important, and it may be, then Brazos Electric has stacked the deck and provided only one alternative that meets its planning criteria at the point of initial selection.  Such gamesmanship is inexcusable and should not be tolerated.

Brazos Electric’s application should be denied because it failed to provide acceptable alternatives and failed to reasonably evaluate the alternatives selected to determine the best alternative.  In the event the Commission wishes to grant a CCN in this proceeding, and it accepts Brazos Electric’s statements that, in fact, all three of the routes are acceptable (but not equally acceptable) to Brazos, then the only quantified analysis in the record supports selection of Brazos Electric’s second alternative as the best route.

Brazos Electric’s position that they never designated the blue route (now the second alternate route) as the preferred route, except in a notice typo, is not credible.  Mr. Townsend hangs his hat, and his credibility, on the statement in the notice that the final route had not been selected.  Mr. Townsend conveniently equates final route with preferred route.  Mr. Townsend states without reservation that the blue route was never its preferred route and that nobody was ever told that the blue route was the preferred route.  Mr. Townsend, however, was not at the public meeting.  Three witnesses who were at the public meeting testified that Brazos Electric personnel did in fact tell them that the blue route was Brazos Electric’s preferred route.

Why is the designation of the blue route as the initial preferred route important?  First, it indicates that Brazos Electric, using its best judgement and best engineering practices initially came to a different conclusion than that represented in testimony at hearing.  Second, the Commission, and the affected landowners are entitled to know what the basis is for changing the preferred route to that sponsored by Brazos Electric at hearing.  Finally, if there is no credible reason or reasons for changing the preferred route from what is now Brazos Electric’s second alternate route, then if a certificate is granted, it should be for that route.

The evidence beyond the blatant statement in the notice supports the belief that Brazos did indeed initially select the blue route as it preferred route.  The application, and other Brazos Electric documents, contain references to approximately 5 miles of new transmission line.  All of the alternatives proposed by Brazos Electric are greater than five miles, ranging from 6.3 to 7.59 miles.  The Woodbine switch is directly north of the proposed Mountain Springs substation that Brazos wants to build to attract CoServ as a new customer in Cooke County.  The distance from the Woodbine switch, straight south to the point that it intercepts the Salem switch to Salem substation line is about 5 miles.  The notices talk about the new line going south out of the Woodbine substation.  The Borrower’s Environmental Report states that the purpose of the new line is to serve CoServ in the vicinity of Woodbine and Lake Kiowa.  And finally, The Appendix B Options contained in the application itself states: “(1) Constructing an approximate 5 mile 138 KV (operate at 69 KV) single pole 795 MCM line from Salem to Woodbine. (2) Install a switching station to include 3-138 KV breakers at Woodbine. (3) Open the existing line from Salem Switch to Redmond Switch.”  This explains Brazos Electric’s initial solution, it explains the confusion about what facilities needed to be built and why the inconsistencies exist and it makes clear that the initial intent was to feed from Woodbine but use the Woodbine to Redmond switch line, not the Woodbine to Whitesboro line as the power source.

Brazos Electric has not been forthcoming regarding the evolution of its plans.  It has failed to meet its burden of proof to establish the best route.

V.	Conclusion

Brazos Electric has failed to meet its burden of proof to demonstrate need for the service, accommodation, convenience, or safety of the public.  Brazos Electric has failed to provide convincing evidence regarding the best route for a new transmission line.  Brazos Electric has failed to explain how it evaluated competing statutory factors to arrive at its conclusions.

Brazos has stacked the deck in its selection of alternatives that were not equally acceptable to it at the time of selection.  Brazos Electric has failed to consider alternative routes that initially appear to provide even greater looped reliability.  Brazos has changed it plans and its preferred alternatives without explanation or support.  Finally, Brazos Electric has attempted to meet its burden of proof through the use of generalities and a serious lack of commitment to specific positions and specific data..  For Brazos Electric, everything from the centerline of the proposed project to the number of habitable structures along the proposed alternate routes is an estimate – and not even a consistent estimate.

For all theses reasons, the application for a CCN filed in the instant docket should be denied.

Respectfully submitted,

__________________________________________

Robert A. Rima (Bar No. 16932500)

Law Offices of Robert A. Rima

8140 N. MoPac Expressway, Suite II-120

Austin, TX 78759

(512) 349-9449

(512) 343-9339 FAX

Attorney for the Nelson Family

CERTIFICATE OF SERVICE

I hereby certify that a copy of the foregoing document was served on all parties of record in this proceeding by U.S. mail, postage prepaid, facsimile, or hand delivery this, the 15th day of November, 1999.

_____________________________________

Robert A. Rima

Tex. Util. Code §37.001(2).

Id. at §37.053(a).

Id. at §37.056(a).

Id. at §37.056(b).

Id. at §14.001.

Brazos witness Townsend testified that the outage record was “pretty good”.  Tr. at 187.

The actual information provided by Brazos Electric was for periods of different lengths and compared total outages at the Salem substation with average outages for the system.  The mismatches were discussed with and confirmed by Mr. Townsend.  Tr. at 189-190.

Nelson  Ex. 39 and Nelson  Ex. 40.

A new looped line may improve reliability over a radial line, but it does not provide a distinguishing need.

Brazos Ex. 1 at 11.

Tr. at 110-111.

ORA Ex. 1 at 9.  See also Nelson Ex. 23 that includes Brazos Electric’s forecasts.

Brazos Ex. 1 at 10.  Tr. at 99-103.

Brazos Ex. 2 at 10-17.

Tr. 103.

Rima: “And have you provided as part of the evidence for Brazos Electric in your application any underlying support for any of these statements?”

Townsend: “Not offhand – I would say no.”

Brazos Ex. 2 at 13.

Tr. at 101-102.

Nelson Ex. 33.

Nelson Ex. 34.

Brazos Ex. 4 at DFB-1.  See also Nelson Ex. 35.

Nelson Ex. 31 contains KW load information for the Salem substation during the period 1986-1996.  1000 KW = 1 MW.  Therefore, for all years since at least 1986 the load at the Salem substation has exceeded 5 MW with the low of 9.7 MW in 1991 and a high of 18.2 MW in 1996.

Nelson Ex. 32.

Tr. at 74.

Id.

See, Application of Pedernales Electric Cooperative, Inc. to Amend a Certificate of Convenience and Necessity for Proposed Transmission Line Within Hays County, SOAH Docket No. 473-95-1165, PUC Docket No. 11014, Final Order October 25, 1995.  Finding of Fact No. 56 states: “The criteria used by LCRA for its transmission system, and adopted by Pedernales, require that no more than 20MW of peak load shall be interrupted for a single anticipated event.  The criteria define a single anticipated event to include ‘the loss of any transmission conductor, transformer, or structure,’ meaning that any substation experiencing in excess of 20MW of load should be on a loop feed (two transmission lines), rather than a radial line (one transmission line).

Brazos Ex. 2.

Brazos Ex. 4 at 12.

Nelson Ex. 42.

Brazos Ex. 2 at 217.

Tr. at 109-110.

Truty Ex. 5 includes a color map of the proposed routes.  From Brazos Electric’s Routing Study (Brazos Ex. 2 at 43) we know that the double circuited portion of the alternatives is 2.46 miles and covers almost all of the distance between the alternative furthest to the west and the alternative furthest to the east.

Tr. at 265.

Id.

A discussion of tornado causing damage to two lines can be found in Tr. at 266-268. Whether an outage would occur at the Salem substation would depend upon where the two lines were damaged.

Nelson Ex. 18.

Tr. at 269-271.

Tr. at 93.

Nelson Ex. 2.

Brazos Ex. 1 at 18.  Brazos Ex. 3 at 14.

Tr. at 93.

Tr. at 157.

Id.

Tr. at 158.

Brazos Ex. 2 at 277.  Tr. at 155-156.

Tr. at 156-157.

Tr. at 197.

Tr. at 152.

Id.

Tr. at 196.

Nelson Ex. 30.  Tr. at 353-354.

Brazos Ex. 3 at 13.

Brazos Ex. 3 at 7.

Tr. at 329.

See, Application of Central Power and Light Company for a Certificate of Convenience and Necessity for a Proposed 345 kV Transmission Line in Nueces, San Patricio, Bee and Goliad Counties, Docket No. 9305, 18 P.U.C. Bull. 1699 (March 11, 1993).  The statements regarding EMF that follow this footnote are from the cited case.

The number of habitable structures listed is incorrect in three different calculations.  See, Tr. at 43-56.

Tr. at 37-43.

D-F-E-G-I-N-O-R-S-T.

Mr. Townsend acknowledged that the PUC’s criteria includes using existing transmission corridors to the extent possible.  Tr. at 278.

Tr. at 151.

Tr. at 149.

Truty Ex. 6.

Tr. at 132.

Tr. at 133.

Nelson Ex. 1 at 5; Tr. at 380-381; Tr. at 410-411.

Brazos Ex. 2 at 14-15, 22, 23, 216, 261, 262, 263, 264, and 272.  Nelson Ex. 3 at third page top left.

Brazos Ex. 2 at 43.

Nelson Ex. 43.

Brazos Ex. 2 at 14.