## CPL--Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | CSW - Central Power & Light
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 657
Due: |  | February 15, 2000
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 21972
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Industry Analysis Division
Office of Regulatory Affairs
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mel.eckhoff@puc.state.tx.us

## CPL--Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
1998 And 1999
CSW - Central Power & Light
Project 21972

## CPL--System-SAIFI
CSW - Central Power & Light
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 1.0853 | 0.036766 | 0.10829 | 0.084846 | 0.037881 | 0.080544 | 0.1322 | 0.1093 | 0.15725 | 0.14574 | 0.1019 | 0.052473 | 0.050636
1999 | 1.1721 | 0.10142 | 0.036452 | 0.075599 | 0.10144 | 0.24576 | 0.11006 | 0.095585 | 0.095498 | 0.058445 | 0.063822 | 0.085581 | 0.10099
Scheduled
1998 | 0.021392 | 0.00031935 | 0.00050841 | 0.0002332 | 0.00038846 | 0.010098 | 0.0030244 | 0.0023696 | 0.0018435 | 0.0020803 | 0.00053135 | 0.00015852 | 8.6502e-05
1999 | 0.0055994 | 2.6207e-05 | 7.3852e-05 | 0.00048839 | 0.0036851 | 6.0512e-05 | 6.3598e-05 | 0.00017052 | 0.00023098 | 0.00034105 | 3.1004e-05 | 2.1703e-05 | 0.0003922
Outside Causes
1998 | 0.66596 | 0.020351 | 0.0085167 | 0.0083844 | 0.0090185 | 0.081946 | 0.052666 | 0.1718 | 0.23402 | 0.018552 | 0.016831 | 0.016995 | 0.035399
1999 | 0.27453 | 0.014183 | 0.039391 | 0.018998 | 0.0035336 | 0.047645 | 0.010717 | 0.015538 | 0.0026121 | 0.015946 | 0.0073325 | 0.063641 | 0.034483
Major Events
1998 | 0.026953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014963 | 0 | 0.012352 | 0 | 0
1999 | 0.14151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14151 | 0 | 0 | 0 | 0

## CPL--System-SAIDI
CSW - Central Power & Light
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 62.9429 | 1.7308 | 6.3385 | 4.6035 | 3.1485 | 4.3182 | 8.5348 | 5.1483 | 8.4076 | 7.8326 | 6.9733 | 3.3689 | 3.2456
1999 | 70.5473 | 4.0657 | 1.9389 | 5.5632 | 4.7179 | 15.4953 | 5.2456 | 4.5561 | 4.5077 | 3.0965 | 4.8159 | 9.2826 | 7.1807
Scheduled
1998 | 0.74212 | 0.027806 | 0.041924 | 0.016907 | 0.024445 | 0.30283 | 0.06605 | 0.065684 | 0.05705 | 0.090248 | 0.040374 | 0.012539 | 0.0047653
1999 | 0.20673 | 0.0013489 | 0.0062467 | 0.026961 | 0.045437 | 0.0045306 | 0.0045542 | 0.011644 | 0.018451 | 0.02115 | 0.0023191 | 0.00068209 | 0.062993
Outside Causes
1998 | 44.5248 | 0.60319 | 0.70087 | 0.25782 | 0.36029 | 3.9691 | 3.1799 | 15.5846 | 15.6443 | 1.0652 | 1.2306 | 0.88303 | 1.6425
1999 | 13.4892 | 0.43277 | 1.4708 | 0.83266 | 0.15479 | 4.2274 | 0.27564 | 0.46971 | 0.082913 | 0.79496 | 0.080331 | 1.8278 | 2.8216
Major Events
1998 | 15.5047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8355 | 0 | 7.875 | 0 | 0
1999 | 27.5171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5171 | 0 | 0 | 0 | 0

## CPL--Feeder-SAIFI
Distribution Feeder Indices for Forced Interruptions
Distribution Feeders on Texas System (10 or more customers) |  |  |  | Total Number of Feeders
657
CSW - Central Power & Light
1999 SAIFI Ranking | Substation Identification | Feeder Identification | # Of Customers | 1999 SAIFI Value
1 | Raymondville #2 | 3250 | 40 | 12.2
2 | Freer | 1500 | 201 | 11.13
3 | Palmhurst | 2820 | 1979 | 11.11
4 | Devine | 7100 | 850 | 8.1
5 | Blessing | 1030 | 146 | 7.99
6 | Tatton | 8490 | 130 | 7.07
7 | Weslaco Unit | 8195 | 1752 | 7.01
8 | Taft | 1260 | 85 | 6.52
9 | Alazan | 620CS | 222 | 6.24
10 | Elsa | 710 | 563 | 6.11
11 | West McAllen | 4515 | 1307 | 6.06
12 | Victoria Power Plant 69KV Bus #1 | 8170 | 740 | 6.06
13 | Rangerville | 3410 | 2276 | 6.04
14 | Stadium | 7800 | 925 | 6.02
15 | West McAllen | 4595 | 894 | 6.01
16 | Laredo Plant | 8695 | 1200 | 6
17 | Elsa | 690 | 1703 | 5.16
18 | Elsa | 700 | 1050 | 5.15
19 | Raymondville #2 | 1280 | 1698 | 5.12
20 | Stadium | 7490 | 1350 | 5.12
21 | Nueces Bay Plant 69KV Bus #2 | 7755 | 111 | 5.1
22 | Weslaco Unit | 7630 | 1557 | 5.06
23 | Elsa | 3500 | 1066 | 5.06
24 | Bishop | 7180 | 1005 | 5.05
25 | McColl Road | 4400 | 793 | 5.01
26 | Goodwin | 4390 | 2421 | 5
27 | Columbus | 930CN | 945 | 4.8
28 | Haine Drive | 270 | 30 | 4.53
29 | North Victoria | 7860 | 1387 | 4.39
30 | Kenedy | 6270 | 1046 | 4.35
31 | Continental | 4080 | 162 | 4.31
32 | San Benito | 4030 | 1169 | 4.19
33 | Nixon | 5990 | 524 | 4.18
34 | Morris Street 138KV Bus #2 | 8715 | 2058 | 4.14
35 | Goliad | 8220 | 1057 | 4.13
36 | Raymondville #1 | 620S | 613 | 4.09
37 | Raymondville #2 | 3240 | 1040 | 4.05
38 | San Benito | 3910 | 1806 | 4.05
39 | Eagle Pass City | 2770 | 1475 | 4.04
40 | Alice | 2530 | 900 | 4.04
41 | Port Lavaca | 2490 | 675 | 4.03
42 | Rangerville | 4060 | 446 | 4.03
43 | West McAllen | 6385 | 1448 | 4.02
44 | Mustang Island | 8510CS | 47 | 4.02
45 | Armstrong | 6050 | 48 | 4.02
46 | Kingsville | 1130 | 1684 | 4.02
47 | Washington Street 69KV Bus #3 | 6525 | 2000 | 4.02
48 | McColl Road | 4780 | 1697 | 4.01
49 | San Benito | 4135 | 653 | 4
50 | Bishop | 2690 | 779 | 4
51 | Laredo Heights Bank #1 | 2100 | 2000 | 4
52 | Dilley | 510 | 440 | 4
53 | South McAllen | 3850 | 965 | 4
54 | Aransas Pass 69KV Bus #2 | 9130 | 300 | 4
55 | Laredo Heights Bank #2 | 2450 | 2000 | 4
56 | Mathis | 1410 | 152 | 4
57 | North Edinburg 69KV Bus #2 | 560 | 414 | 3.64
58 | O'Conner | 390CN | 120 | 3.59
59 | Columbus | 6180 | 876 | 3.58
60 | Refugio | 1210 | 333 | 3.48
61 | Causeway | 4775 | 967 | 3.36
62 | Kenedy | 1970 | 140 | 3.36
63 | Weslaco Unit | 8610 | 1863 | 3.33
64 | Foster Field | 2550 | 118 | 3.31
65 | Port Lavaca | 2480CN | 750 | 3.27
66 | Malone | 7550 | 144 | 3.26
67 | Santa Rosa | 4040 | 1362 | 3.23
68 | Raymondville #1 | 630 | 761 | 3.2
69 | Raymondville #2 | 3170 | 543 | 3.2
70 | Los Fresnos | 3280 | 1573 | 3.19
71 | Devine | 7090 | 901 | 3.17
72 | Arcadia 69KV Bus #1 | 6930 | 899 | 3.16
73 | Pleasanton | 2080 | 1305 | 3.12
74 | Uvalde 138KV Bus | 6620 | 1500 | 3.12
75 | Goodwin | 3530 | 1253 | 3.12
76 | Woodsboro | 8330CN | 1095 | 3.11
77 | Magruder | 7870 | 1283 | 3.1
78 | Seawall | 9450 | 155 | 3.08
79 | Holly | 7620 | 1384 | 3.08
80 | Dilley | 6400 | 970 | 3.08
81 | Causeway | 4795 | 1496 | 3.08
82 | Eagle Pass Hydro | 1340 | 180 | 3.07
83 | North Pharr | 3090 | 1540 | 3.07
84 | Kenedy S.S. 69KV Bus | 8320 | 583 | 3.07
85 | Pueblo | 95 | 1289 | 3.06
86 | North Mercedes | 3770 | 1460 | 3.06
87 | Devine | 8100 | 1261 | 3.06
88 | Del Rio City | 9790 | 2450 | 3.06
89 | Falfurrias 69KV Bus | 2830 | 1344 | 3.06
90 | Port Aransas | 990CS | 565 | 3.05
91 | Premont | 2730 | 213 | 3.05
92 | South East Edinburg | 4570 | 1538 | 3.05
93 | South East Edinburg | 4015 | 1702 | 3.04
94 | South Mission | 5215 | 997 | 3.04
95 | Rio Bravo | 5 | 1850 | 3.04
96 | Aransas Pass 69KV Bus #2 | 8280 | 350 | 3.03
97 | Arcadia 69KV Bus #2 | 1440 | 2200 | 3.03
98 | Weslaco Unit | 5970 | 1752 | 3.03
99 | McColl Road | 4790 | 1397 | 3.03
100 | Randado | 8360 | 193 | 3.03
101 | Aransas Pass 69KV Bus #2 | 1250 | 300 | 3.02
102 | Crestonio | 260 | 1449 | 3.01
103 | North Pharr | 3010 | 677 | 3.01
104 | South McAllen | 3790 | 1916 | 3.01
105 | Laredo Heights Bank #2 | 2390 | 1000 | 3.01
106 | Sharyland | 2020 | 1867 | 3.01
107 | Asherton | 2660 | 633 | 3.01
108 | Polk Avenue | 4170 | 1432 | 3.01
109 | South East Edinburg | 6580 | 2233 | 3
110 | Port Aransas | 1000 | 897 | 3
111 | Santo Nino | 80 | 500 | 3
112 | Raymondville #2 | 4160 | 774 | 3
113 | Laredo Heights Bank #2 | 9080 | 1000 | 3
114 | San Benito | 3860 | 1164 | 3
115 | South Mission | 3980 | 4020 | 3
116 | Kingsville | 1350 | 280 | 2.99
117 | Edroy | 6990 | 230 | 2.93
118 | La Pryor | 570 | 55 | 2.76
119 | Markham | 5550 | 85 | 2.74
120 | West Oso | 9085 | 868 | 2.62
121 | Wadsworth | 8630 | 589 | 2.47
122 | North Edinburg 69KV Bus #1 | 3570 | 437 | 2.4
123 | Santa Rosa | 3270 | 1045 | 2.36
124 | Morris Street 138KV Bus #1 | 8830 | 1454 | 2.32
125 | Carrizo Springs | 910 | 1584 | 2.31
126 | Bonnieview | 8020CN | 407 | 2.29
127 | North Mercedes | 3840 | 720 | 2.26
128 | Cabaniss | 80 | 1102 | 2.26
129 | North Padre Island | 7900 | 1100 | 2.25
130 | Odem | 385 | 262 | 2.24
131 | Port Lavaca | 8310 | 230 | 2.24
132 | Bruni | 1100 | 659 | 2.24
133 | Bay City | 5960 | 1917 | 2.21
134 | Placedo | 7970 | 387 | 2.18
135 | Pearsall | 7050 | 1334 | 2.18
136 | Morris Street 138KV Bus #2 | 8840 | 775 | 2.14
137 | Odem | 375 | 735 | 2.14
138 | North Alamo | 3610 | 1849 | 2.12
139 | Fulton Bank #1 | 440CS | 1581 | 2.12
140 | Pearsall | 5580 | 1906 | 2.1
141 | Laguna | 9590 | 1693 | 2.1
142 | Clarkwood | 5525 | 470 | 2.1
143 | Bay City | 1110CN | 974 | 2.1
144 | Jourdanton | 880 | 345 | 2.09
145 | North Alamo | 4370 | 780 | 2.09
146 | North Victoria | 7440 | 2232 | 2.09
147 | Fulton Bank #2 | 9050 | 980 | 2.08
148 | Palmhurst | 3890 | 609 | 2.08
149 | Moore Field | 3960 | 891 | 2.08
150 | Parker | 9010 | 14 | 2.07
151 | Morris Street 138KV Bus #2 | 5655 | 1373 | 2.07
152 | Ingleside City | 6040 | 800 | 2.07
153 | Beeville | 2200 | 802 | 2.06
154 | Knippa | 6365 | 274 | 2.05
155 | South Padre Island | 4695 | 3079 | 2.05
156 | El Campo 69KV Bus | 2860 | 310 | 2.05
157 | Eagle Pass City | 2650 | 2950 | 2.05
158 | Tatton | 8200 | 1514 | 2.04
159 | North Mercedes | 4860 | 1459 | 2.04
160 | Airline 69KV Bus #2 | 8370 | 367 | 2.04
161 | Weslaco Unit | 7455 | 1460 | 2.03
162 | Crestonio | 6660 | 938 | 2.03
163 | Highway Nine 69KV Bus #1 | 7200 | 957 | 2.03
164 | West McAllen | 4555 | 1521 | 2.03
165 | South East Edinburg | 4550 | 1721 | 2.03
166 | Aransas Pass 69KV Bus #2 | 660CS | 350 | 2.03
167 | Rangerville | 7750 | 625 | 2.03
168 | Naval Base 69KV Bus #2 | 1380 | 1931 | 2.03
169 | North McAllen | 2750 | 1849 | 2.03
170 | South McAllen | 3640 | 1100 | 2.02
171 | Mathis | 1420 | 812 | 2.02
172 | La Pryor | 2440 | 562 | 2.02
173 | Mathis | 340CS | 1506 | 2.02
174 | Hamilton Road 138KV Bus #2 | 9655 | 560 | 2.02
175 | South Padre Island | 5850 | 880 | 2.02
176 | Live Oak | 1090 | 111 | 2.02
177 | McColl Road | 2810 | 1447 | 2.02
178 | Zapata | 7330 | 2139 | 2.01
179 | Loyola | 195 | 662 | 2.01
180 | Polk Avenue | 4180 | 2743 | 2.01
181 | Mines Road | 3745 | 3500 | 2.01
182 | Port Aransas | 3030CS | 600 | 2.01
183 | Freer | 6320W | 171 | 2.01
184 | East Harrison 69KV Bus #3 | 4360 | 1202 | 2.01
185 | McColl Road | 4910 | 1358 | 2.01
186 | Laredo Heights Bank #2 | 6810 | 2000 | 2.01
187 | West Harlingen | 3800 | 2248 | 2.01
188 | Polk Avenue | 4520 | 1974 | 2
189 | Morris Street 138KV Bus #2 | 7465 | 753 | 2
190 | Sharyland | 2150 | 1296 | 2
191 | Morris Street 138KV Bus #1 | 8850 | 511 | 2
192 | Berclair | 990C | 243 | 2
193 | Live Oak | 1080 | 111 | 2
194 | Kingsville | 1670 | 402 | 2
195 | Rio Grande City | 3230 | 2326 | 2
196 | Bruni | 5440 | 44 | 1.93
197 | North Victoria | 6390 | 1128 | 1.81
198 | Clarkwood | 7230 | 135 | 1.73
199 | Robstown | 1650 | 58 | 1.71
200 | Harlingen | 380 | 1216 | 1.63
201 | Stafford Hill | 1550 | 180 | 1.54
202 | Darst | 800 | 161 | 1.52
203 | West Harlingen | 3720 | 1595 | 1.45
204 | Edna | 5765 | 1100 | 1.41
205 | Kenedy S.S. 138KV Bus | 8340 | 702 | 1.37
206 | Hamilton Road 138KV Bus #2 | 9665W | 276 | 1.37
207 | Pleasanton | 9505 | 1250 | 1.33
208 | Palacios | 8550 | 43 | 1.33
209 | Greenlake | 2760 | 675 | 1.31
210 | Beeville | 1760 | 874 | 1.3
211 | Rodd Field | 3010 | 103 | 1.29
212 | Refugio | 1040 | 566 | 1.29
213 | Victoria Power Plant 69KV Bus #1 | 8070 | 444 | 1.27
214 | Pharaoh | 1285 | 1215 | 1.27
215 | Wesmer | 9705 | 1168 | 1.26
216 | Eagle Lake | 320CN | 692 | 1.25
217 | Ingleside City | 8060 | 800 | 1.25
218 | Southside 69KV Bus #4 | 8045 | 1036 | 1.24
219 | Rio Rico | 8330 | 1752 | 1.23
220 | Arcadia 69KV Bus #2 | 8570 | 1440 | 1.23
221 | Ganado | 5815 | 550 | 1.22
222 | Nixon | 810 | 543 | 1.22
223 | North Padre Island | 5170 | 860 | 1.2
224 | Eagle Lake | 310 | 828 | 1.2
225 | Pueblo | 275 | 1100 | 1.2
226 | Skidmore | 600 | 352 | 1.18
227 | Clarkwood | 9570 | 1187 | 1.18
228 | Buena Vista | 8965 | 755 | 1.17
229 | Southside 69KV Bus #4 | 5335 | 948 | 1.16
230 | Bay City | 2700 | 1375 | 1.16
231 | Wesmer | 4050 | 1557 | 1.16
232 | Los Fresnos | 3200 | 1806 | 1.15
233 | Greenlake | 2740CN | 20 | 1.15
234 | Bay City | 7480 | 2004 | 1.15
235 | Pettus | 1020 | 336 | 1.15
236 | Blessing | 8780 | 76 | 1.14
237 | Pettus | 8210 | 455 | 1.14
238 | Cavazos | 3550 | 633 | 1.14
239 | Yorktown | 8380 | 831 | 1.13
240 | North McAllen | 2980 | 1629 | 1.13
241 | Palmview | 3930 | 628 | 1.13
242 | Rodd Field | 205 | 1089 | 1.13
243 | El Campo 69KV Bus | 5745 | 1104 | 1.12
244 | Del Rio City | 430 | 1921 | 1.12
245 | Stadium | 7810 | 1310 | 1.12
246 | Wadsworth | 7660 | 1119 | 1.12
247 | Washington Street 69KV Bus #2 | 2350 | 1000 | 1.12
248 | Palmview | 9680 | 726 | 1.11
249 | Harlingen Switching Station | 4090 | 1013 | 1.1
250 | Seawall | 9420 | 1011 | 1.1
251 | Southside 69KV Bus #4 | 8055 | 1066 | 1.1
252 | Casa Blanca | 1300CS | 880 | 1.1
253 | Victoria Power Plant 69KV Bus #2 | 1390 | 1351 | 1.1
254 | Moore Field | 3110 | 1211 | 1.1
255 | West Oso | 9095 | 2507 | 1.1
256 | Sinton | 6860 | 1320 | 1.09
257 | Causeway | 4765 | 1100 | 1.09
258 | Crystal City | 190 | 1020 | 1.08
259 | Palacios | 6840 | 1387 | 1.08
260 | Airline 69KV Bus #1 | 2180 | 12 | 1.08
261 | Bay City | 6450 | 1072 | 1.08
262 | Garwood City | 2560 | 204 | 1.08
263 | Bay City | 2050 | 683 | 1.08
264 | Falfurrias 138KV Bus | 5210 | 959 | 1.08
265 | Southside 69KV Bus #3 | 8035 | 1147 | 1.07
266 | Rachal | 6595 | 474 | 1.07
267 | Kleberg 138KV Bus #2 | 6000 | 1552 | 1.07
268 | Morris Street 138KV Bus #1 | 2515 | 1829 | 1.07
269 | Port Isabel Switching Station | 3820 | 440 | 1.07
270 | Holly | 7740 | 1417 | 1.07
271 | Loyola | 120CS | 698 | 1.07
272 | Rodd Field | 2190 | 610 | 1.07
273 | Markham | 6440CN | 460 | 1.06
274 | Live Oak | 1070 | 1692 | 1.06
275 | Rockport | 5940 | 113 | 1.06
276 | Del Rio City | 420W | 1630 | 1.06
277 | Anna Street | 2250 | 1300 | 1.06
278 | West McAllen | 4535 | 1810 | 1.06
279 | Harlingen Switching Station | 4230 | 1511 | 1.05
280 | Los Fresnos | 3290 | 802 | 1.05
281 | Banquette | 9000 | 130 | 1.05
282 | Naval Base 69KV Bus #2 | 6330 | 262 | 1.05
283 | Carrizo Springs | 860 | 1372 | 1.05
284 | Zapata | 2710 | 41 | 1.05
285 | Harlingen | 660 | 1511 | 1.05
286 | Brackettville | 8460 | 1143 | 1.05
287 | Fulton Bank #2 | 3070CS | 1800 | 1.04
288 | Morris Street 138KV Bus #2 | 8820 | 917 | 1.04
289 | Woolridge | 1110 | 1057 | 1.04
290 | Del Rio City | 1930 | 963 | 1.04
291 | Uvalde 138KV Bus | 480 | 1610 | 1.04
292 | Jourdanton | 5685 | 630 | 1.04
293 | Ingleside City | 8050 | 1000 | 1.04
294 | North Victoria | 1470 | 542 | 1.04
295 | San Diego | 1980 | 650 | 1.04
296 | South Padre Island | 6440 | 1584 | 1.03
297 | Maverick | 9680W | 580 | 1.03
298 | La Pryor | 580 | 153 | 1.03
299 | Taft | 1180 | 928 | 1.03
300 | San Diego | 2890 | 1000 | 1.03
301 | Gregory | 5900 | 97 | 1.03
302 | Arcadia 69KV Bus #1 | 1450 | 2029 | 1.03
303 | Del Rio City | 9850 | 657 | 1.03
304 | Weaver Road | 1910 | 264 | 1.03
305 | North McAllen | 3830 | 2024 | 1.03
306 | Carancahua | 5870CN | 277 | 1.03
307 | Premont | 2720 | 928 | 1.03
308 | Crestonio | 270W | 599 | 1.03
309 | Del Rio City | 440W | 1388 | 1.03
310 | Ingleside City | 7310 | 40 | 1.02
311 | Government Wells | 7240 | 247 | 1.02
312 | Pueblo | 130W | 1050 | 1.02
313 | Casa Blanca | 55 | 1010 | 1.02
314 | Harlingen | 360 | 1624 | 1.02
315 | Leary Lane | 1430 | 1184 | 1.02
316 | Crystal City | 140W | 1630 | 1.02
317 | Kleberg 138KV Bus #1 | 280 | 1398 | 1.02
318 | Nueces Bay Plant 69KV Bus #1 | 7855 | 53 | 1.02
319 | Del Mar | 3440 | 2500 | 1.02
320 | Holly | 1480 | 1812 | 1.02
321 | Southside 69KV Bus #1 | 7905 | 2091 | 1.02
322 | Banquette | 740 | 175 | 1.02
323 | West Oso | 9090 | 1610 | 1.02
324 | Freer | 2900 | 304 | 1.02
325 | North Weslaco | 4810 | 1460 | 1.02
326 | West McAllen | 4965 | 709 | 1.02
327 | Nixon | 2620 | 590 | 1.02
328 | West McAllen | 4505 | 1886 | 1.01
329 | North McAllen | 9640 | 2579 | 1.01
330 | Sharyland | 2035 | 1482 | 1.01
331 | Pharaoh | 5185 | 1993 | 1.01
332 | South Mission | 3620 | 3300 | 1.01
333 | Santo Nino | 75 | 1800 | 1.01
334 | Mathis | 2870 | 1000 | 1.01
335 | Garwood City | 2570CN | 305 | 1.01
336 | San Diego | 2880 | 1438 | 1.01
337 | Freer | 5200 | 1245 | 1.01
338 | Santo Nino | 645 | 1500 | 1.01
339 | Hearn Road | 8990 | 812 | 1.01
340 | Polk Avenue | 4600 | 2009 | 1.01
341 | Sharyland | 2010 | 954 | 1.01
342 | Portland | 9370 | 1289 | 1
343 | North Edinburg 69KV Bus #2 | 3810 | 224 | 1
344 | Continental | 4880 | 227 | 1
345 | Morris Street 138KV Bus #1 | 7625 | 683 | 1
346 | South Mission | 4650 | 1618 | 1
347 | Carrizo Springs | 370W | 278 | 1
348 | Eagle Pass City | 2745 | 2150 | 1
349 | Eagle Pass City | 7060 | 1120 | 1
350 | Santo Nino | 70 | 1500 | 1
351 | Big Wells | 1570 | 478 | 1
352 | Port Isabel Switching Station | 4070 | 493 | 1
353 | Brookhollow | 7190 | 500 | 1
354 | Del Mar | 10 | 4700 | 1
355 | Nueces Bay Plant 69KV Bus #2 | 7765 | 790 | 1
356 | Washington Street 69KV Bus #3 | 6355 | 800 | 1
357 | Laredo Plant | 9305 | 1800 | 1
358 | Haine Drive | 8065 | 1455 | 1
359 | Continental | 3650 | 37 | 1
360 | Alazan | 2740CS | 40 | 1
361 | Amistad Dam | 5450 | 790 | 1
362 | Nordheim | 470 | 245 | 1
363 | Del Mar | 490 | 1500 | 1
364 | Three Rivers | 5100 | 40 | 1
365 | Thomaston | 9580 | 53 | 1
366 | Hamilton Road 138KV Bus #1 | 9645 | 260 | 1
367 | Weaver Road | 1900 | 105 | 1
368 | San Ygnacio | 16060 | 11 | 1
369 | North Pharr | 3100 | 117 | 1
370 | Nueces Bay Plant 69KV Bus #2 | 7795 | 790 | 1
371 | Hearn Road | 8980 | 971 | 0.9
372 | Highway Nine 69KV Bus #2 | 6780 | 881 | 0.89
373 | Hearn Road | 9665 | 1039 | 0.71
374 | Goliad | 6540 | 886 | 0.7
375 | Rio Bravo | 300W | 12 | 0.69
376 | Uvalde 138KV Bus | 550 | 370 | 0.64
377 | Campwood | 2610 | 880 | 0.61
378 | Edna | 5785 | 457 | 0.55
379 | Gateway | 390 | 1400 | 0.5
380 | Beeville | 8090 | 1281 | 0.44
381 | Karon Humble Pump | 9895 | 30 | 0.43
382 | El Campo 138KV Bus | 6370 | 724 | 0.42
383 | Bay City | 6670 | 1845 | 0.41
384 | Prairie Pump | 1940 | 38 | 0.39
385 | Brookhollow | 8950 | 650 | 0.36
386 | George West | 1320 | 593 | 0.36
387 | North Victoria | 7770 | 999 | 0.36
388 | Falfurrias 69KV Bus | 1080W | 419 | 0.32
389 | Arcadia 69KV Bus #2 | 5020 | 829 | 0.32
390 | Three Rivers | 8430 | 141 | 0.31
391 | Three Rivers | 5190 | 692 | 0.31
392 | Cavazos | 3560 | 1166 | 0.3
393 | Arcadia 69KV Bus #1 | 1460 | 1209 | 0.29
394 | Portland | 6505 | 1563 | 0.29
395 | North Victoria | 7430 | 524 | 0.28
396 | Gregory | 5920 | 375 | 0.28
397 | Lytle | 2850 | 630 | 0.28
398 | Rockport | 5950 | 252 | 0.28
399 | Palmhurst | 1300 | 842 | 0.28
400 | Uvalde 138KV Bus | 540 | 800 | 0.27
401 | Luling LCRA | 10CN | 167 | 0.27
402 | Harlingen Switching Station | 4110 | 751 | 0.27
403 | Southside 69KV Bus #3 | 8025 | 622 | 0.27
404 | Blessing | 8790 | 641 | 0.25
405 | East Harrison 69KV Bus #2 | 3950 | 301 | 0.24
406 | Wesmer | 4480 | 1946 | 0.24
407 | El Campo 69KV Bus | 7260 | 410 | 0.23
408 | Southside 69KV Bus #1 | 7925 | 1195 | 0.23
409 | Greenlake | 2750CN | 840 | 0.23
410 | Port Aransas | 6940 | 900 | 0.22
411 | Harlingen Switching Station | 320 | 519 | 0.22
412 | West McAllen | 4815 | 136 | 0.22
413 | Ganado | 5795 | 689 | 0.22
414 | Refugio | 5120 | 23 | 0.22
415 | El Campo 138KV Bus | 2800 | 1276 | 0.22
416 | Greta | 7890 | 304 | 0.21
417 | Malone | 7560 | 150 | 0.21
418 | Luling LCRA | 20 | 354 | 0.21
419 | Brownsville | 3050 | 1766 | 0.2
420 | Los Fresnos | 930S | 836 | 0.18
421 | Columbus | 9060 | 547 | 0.18
422 | Airline 69KV Bus #2 | 6970 | 1066 | 0.18
423 | Runge | 7320 | 598 | 0.18
424 | Three Rivers | 2010CN | 753 | 0.16
425 | Kenedy S.S. 138KV Bus | 6750 | 877 | 0.16
426 | North Victoria | 1580 | 703 | 0.16
427 | Eagle Lake | 9455 | 547 | 0.16
428 | Parker | 9260 | 70 | 0.16
429 | George West | 730 | 721 | 0.16
430 | Palacios | 6830 | 903 | 0.15
431 | Arcadia 69KV Bus #1 | 5030 | 1389 | 0.15
432 | Pearsall | 9905 | 180 | 0.15
433 | Holly | 1370 | 716 | 0.15
434 | Placedo | 7980 | 407 | 0.14
435 | Southside 69KV Bus #3 | 5345 | 432 | 0.14
436 | Rocksprings | 2600 | 349 | 0.13
437 | Matthews | 1740 | 39 | 0.13
438 | Hall Acres Road | 3670 | 981 | 0.13
439 | Woolridge | 1170 | 1416 | 0.12
440 | Polk Avenue | 4740 | 1282 | 0.12
441 | Sinton | 180 | 1151 | 0.11
442 | McKenzie Road | 330 | 1726 | 0.11
443 | Aransas Pass 69KV Bus #1 | 8270 | 450 | 0.11
444 | Rodd Field | 1730 | 910 | 0.11
445 | Arcadia 69KV Bus #2 | 1360 | 2361 | 0.11
446 | Beeville | 300CN | 1245 | 0.1
447 | Southside 69KV Bus #2 | 7955 | 979 | 0.1
448 | North Edinburg 69KV Bus #1 | 4240 | 600 | 0.1
449 | Highway Nine 69KV Bus #2 | 6760 | 825 | 0.1
450 | San Benito | 4945 | 745 | 0.1
451 | Magruder | 7690 | 907 | 0.1
452 | Stadium | 6950 | 610 | 0.1
453 | Magruder | 6700 | 1906 | 0.1
454 | Refugio | 1170CN | 1143 | 0.1
455 | Buena Vista | 9385 | 1380 | 0.09
456 | Polk Avenue | 4900 | 1464 | 0.09
457 | Government Wells | 7250 | 324 | 0.09
458 | Kingsville | 1660 | 1459 | 0.09
459 | Buena Vista | 9035 | 735 | 0.09
460 | Leary Lane | 7530 | 1553 | 0.09
461 | Magruder | 245 | 640 | 0.09
462 | Pleasanton | 120W | 1175 | 0.09
463 | Southside 69KV Bus #2 | 7995 | 1483 | 0.09
464 | Alice | 1770 | 1180 | 0.09
465 | Hall Acres Road | 5585 | 574 | 0.09
466 | Cabaniss | 240 | 1788 | 0.08
467 | West Harlingen | 3700 | 1267 | 0.08
468 | Anna Street | 780 | 1000 | 0.08
469 | Rio Grande City | 3220 | 1379 | 0.08
470 | El Campo 138KV Bus | 7710 | 990 | 0.08
471 | Kleberg 138KV Bus #1 | 9395 | 1107 | 0.08
472 | Magruder | 6690 | 544 | 0.08
473 | North Alamo | 3580 | 391 | 0.08
474 | Leary Lane | 1540 | 1107 | 0.08
475 | Alice | 2540 | 1045 | 0.08
476 | Sinton | 1750 | 373 | 0.08
477 | Edroy | 6980 | 354 | 0.07
478 | Highway Nine 69KV Bus #1 | 6720 | 1407 | 0.07
479 | Highway Nine 69KV Bus #2 | 6770 | 1605 | 0.07
480 | Portland | 9290 | 1007 | 0.07
481 | Polk Avenue | 4190 | 1901 | 0.07
482 | Uvalde 138KV Bus | 5060 | 1600 | 0.07
483 | Hidalgo | 3680 | 889 | 0.06
484 | Woolridge | 1120 | 1171 | 0.06
485 | East Harrison 69KV Bus #1 | 3080 | 1068 | 0.06
486 | Highway Nine 69KV Bus #1 | 7210 | 1069 | 0.06
487 | Portland | 9270 | 1047 | 0.06
488 | Weil Tract (138/12KV) | 2520 | 294 | 0.06
489 | Santa Rosa | 3430 | 1454 | 0.06
490 | Mines Road | 3680 | 1000 | 0.05
491 | Leary Lane | 6005 | 898 | 0.05
492 | Airline 69KV Bus #1 | 8260 | 1039 | 0.05
493 | Yorktown | 8420 | 917 | 0.05
494 | La Grulla | 5110 | 992 | 0.05
495 | Roma | 3060 | 2064 | 0.05
496 | Leary Lane | 1890 | 1396 | 0.05
497 | Crystal City | 330W | 920 | 0.05
498 | Polk Avenue | 4610 | 2029 | 0.05
499 | Seawall | 9325 | 1514 | 0.05
500 | Campwood | 3430W | 383 | 0.04
501 | Hall Acres Road | 3460 | 2344 | 0.04
502 | Gregory | 8560 | 229 | 0.04
503 | Asphalt Mines | 500 | 23 | 0.04
504 | Point Comfort | 2460 | 330 | 0.04
505 | Sabinal | 485 | 477 | 0.04
506 | North McAllen | 4995 | 2267 | 0.04
507 | Charlotte | 8120 | 145 | 0.04
508 | Stadium | 8540 | 1795 | 0.04
509 | Edna | 5775 | 870 | 0.04
510 | Charlotte | 2780 | 510 | 0.04
511 | Airline 69KV Bus #2 | 9390 | 1054 | 0.04
512 | Jourdanton | 5695 | 1030 | 0.04
513 | Alice | 1790 | 440 | 0.04
514 | Beeville | 2380 | 950 | 0.04
515 | Hearn Road | 870 | 982 | 0.04
516 | North McAllen | 9660 | 574 | 0.04
517 | Weslaco Unit | 9805 | 1460 | 0.04
518 | Cotulla | 90 | 593 | 0.04
519 | Pleasanton | 9475 | 1650 | 0.04
520 | Laredo Heights Bank #1 | 9400 | 1000 | 0.04
521 | East Harrison 69KV Bus #1 | 3030 | 975 | 0.03
522 | Port Lavaca | 6850 | 680 | 0.03
523 | Asherton | 2670 | 152 | 0.03
524 | North Weslaco | 4830 | 1243 | 0.03
525 | Kleberg 138KV Bus #1 | 1560 | 912 | 0.03
526 | East Harrison 69KV Bus #3 | 4310 | 977 | 0.03
527 | Naval Base 69KV Bus #2 | 8440 | 1289 | 0.03
528 | San Benito | 3920 | 1981 | 0.03
529 | Beeville | 490CN | 1020 | 0.03
530 | Southside 69KV Bus #2 | 8005 | 710 | 0.03
531 | Moore Field | 3120 | 392 | 0.03
532 | Holly | 1950 | 1423 | 0.03
533 | Brookhollow | 8960 | 700 | 0.03
534 | Hall Acres Road | 5465 | 958 | 0.03
535 | Uvalde 138KV Bus | 9770 | 1600 | 0.03
536 | Government Wells | 6800 | 228 | 0.03
537 | Holly | 5820 | 937 | 0.03
538 | Goodwin | 4625 | 508 | 0.03
539 | Pharaoh | 5175 | 1110 | 0.03
540 | Laguna | 9065 | 1697 | 0.02
541 | East Harrison 69KV Bus #2 | 4620 | 1285 | 0.02
542 | Airline 69KV Bus #2 | 7280 | 632 | 0.02
543 | West Harlingen | 4870 | 1949 | 0.02
544 | Laredo Plant | 8745 | 1000 | 0.02
545 | Big Wells | 2630W | 234 | 0.02
546 | Holly | 9675 | 1267 | 0.02
547 | Airline 69KV Bus #2 | 2210 | 285 | 0.02
548 | Weil Tract (138/12KV) | 5405 | 145 | 0.02
549 | Washington Street 69KV Bus #3 | 7015 | 1500 | 0.02
550 | Beeville | 8510CN | 979 | 0.02
551 | Kleberg 138KV Bus #2 | 8140 | 49 | 0.02
552 | Point Comfort | 6060 | 407 | 0.02
553 | East Harrison 69KV Bus #2 | 3190 | 1115 | 0.02
554 | Three Rivers | 2580 | 110 | 0.02
555 | Gateway | 350 | 1500 | 0.02
556 | La Grulla | 4120 | 728 | 0.02
557 | South Mission | 3590 | 2295 | 0.02
558 | Premont | 6570 | 1397 | 0.02
559 | Wesmer | 6900 | 1179 | 0.02
560 | Alice | 1780 | 1060 | 0.02
561 | Clarkwood | 7220 | 707 | 0.02
562 | Haine Drive | 9690 | 1023 | 0.01
563 | Rio Grande City | 3740 | 2481 | 0.01
564 | Kingsville | 1140 | 979 | 0.01
565 | Aransas Pass 69KV Bus #1 | 590 | 150 | 0.01
566 | Clarkwood | 7610 | 226 | 0.01
567 | Hearn Road | 2220 | 1604 | 0.01
568 | Airline 69KV Bus #2 | 9605 | 562 | 0.01
569 | Airline 69KV Bus #1 | 9030 | 328 | 0.01
570 | Weil Tract (138/12KV) | 1990 | 1003 | 0.01
571 | Pharaoh | 1185 | 1013 | 0.01
572 | Holly | 1220 | 2254 | 0.01
573 | Brownsville | 4280 | 1045 | 0.01
574 | Brownsville | 4290 | 2358 | 0.01
575 | Fulton Bank #2 | 6070 | 1921 | 0.01
576 | Anna Street | 900 | 1500 | 0.01
577 | North Victoria | 2240 | 814 | 0.01
578 | Del Mar | 7930 | 2500 | 0.01
579 | Highway Nine 69KV Bus #1 | 9830 | 106 | 0.01
580 | Laredo Plant | 8505 | 1000 | 0.01
581 | McKenzie Road | 140 | 116 | 0.01
582 | Gateway | 380 | 500 | 0.01
583 | Magruder | 6680 | 646 | 0.01
584 | Rio Rico | 8290 | 1217 | 0.01
585 | Harlingen | 370 | 1784 | 0.01
586 | Hall Acres Road | 9595 | 574 | 0.01
587 | Hidalgo | 4845 | 438 | 0.01
588 | Leary Lane | 6175 | 1051 | 0.01
589 | Encinal | 2160 | 625 | 0.01
590 | La Grulla | 5005 | 1257 | 0.01
591 | Cabaniss | 75 | 968 | 0.01
592 | Charlotte | 2790 | 170 | 0.01
593 | South McAllen | 3935 | 1096 | 0.01
594 | Bruni | 5160 | 188 | 0.01
595 | Highway Nine 69KV Bus #1 | 6730 | 380 | 0.01
596 | Sabinal | 200 | 400 | 0.01
597 | Taft | 5230 | 744 | 0
598 | Rockport | 5930 | 1011 | 0
599 | Sinton | 360CS | 277 | 0
600 | Zapata | 8290W | 2014 | 0
601 | Eagle Pass City | 450 | 1625 | 0
602 | Arcadia 69KV Bus #1 | 1400 | 351 | 0
603 | Airline 69KV Bus #1 | 7390 | 1408 | 0
604 | South Mission | 3940 | 2187 | 0
605 | Airline 69KV Bus #1 | 7270 | 985 | 0
606 | Fulton Bank #1 | 2020CS | 1530 | 0
607 | Hall Acres Road | 4895 | 1544 | 0
608 | Banquette | 130CS | 540 | 0
609 | Goodwin | 4380 | 1623 | 0
610 | Laredo Plant | 8565 | 1200 | 0
611 | Gregory | 420CS | 668 | 0
612 | Laredo Heights Bank #1 | 6820 | 1000 | 0
613 | Rio Grande City | 3210 | 1205 | 0
614 | Cotulla | 110 | 1345 | 0
615 | Roma | 3070S | 2068 | 0
616 | Airline 69KV Bus #1 | 5870 | 799 | 0
617 | Airline 69KV Bus #1 | 8890 | 411 | 0
618 | Anna Street | 5780 | 1500 | 0
619 | Anna Street | 850 | 1400 | 0
620 | Aransas Pass 69KV Bus #1 | 650 | 250 | 0
621 | Bandera Electric (Leakey) | L30 | 373 | 0
622 | Brookhollow | 7580 | 550 | 0
623 | Bruni | 1120W | 86 | 0
624 | Comstock | 290 | 191 | 0
625 | Conoco-Chittam Ranch | 8580 | 50 | 0
626 | Darst | 790 | 80 | 0
627 | Darst | 820 | 141 | 0
628 | Eagle Pass City | 2510 | 750 | 0
629 | East Harrison 69KV Bus #1 | 3000 | 1175 | 0
630 | Falfurrias 138KV Bus | 1070 | 881 | 0
631 | Foster Field | 8880 | 204 | 0
632 | Haine Drive | 9240 | 1290 | 0
633 | Hidalgo | 3400 | 814 | 0
634 | Kenedy | 1960 | 241 | 0
635 | Kleberg 138KV Bus #2 | 6410 | 370 | 0
636 | Knippa | 6535 | 14 | 0
637 | Laredo Plant | 8705 | 1000 | 0
638 | Lolita | 6320CN | 29 | 0
639 | McKenzie Road | 150 | 12 | 0
640 | Morris Street Network | 0 NET CC | 430 | 0
641 | Mustang Island | 9470 | 653 | 0
642 | Port Isabel Switching Station | 3760 | 800 | 0
643 | Randado | 8350 | 89 | 0
644 | Robstown | 7120 | 120 | 0
645 | Rocksprings | 8040 | 300 | 0
646 | San Diego | 2570CS | 600 | 0
647 | Santo Nino | 515 | 1500 | 0
648 | Skidmore | 380CN | 256 | 0
649 | Southside 69KV Bus #1 | 7935 | 43 | 0
650 | STP Construction Substation | 1010 | 10 | 0
651 | University | 920 | 60 | 0
652 | University | 930 | 100 | 0
653 | Victoria Power Plant 69KV Bus #2 | 7600 | 222 | 0
654 | Victoria Power Plant Network | 0 NET VIC | 192 | 0
655 | Washington Street 69KV Bus #1 | 0 NET LAR | 500 | 0
656 | Washington Street 69KV Bus #2 | 2360 | 700 | 0
657 | Washington Street 69KV Bus #2 | 2470 | 600 | 0

## CPL--Feeder-SAIDI
Distribution Feeder Indices for Forced Interruptions
Distribution Feeders on Texas System (10 or more customers) |  |  |  | Total Number of Feeders
657
CSW - Central Power & Light
1999 SAIDI Ranking | Substation Identification | Feeder Identification | # Of Customers | 1999 SAIDI Value
1 | Tatton | 8490 | 130 | 1177.62
2 | Elsa | 700 | 1050 | 1088.28
3 | Elsa | 3500 | 1066 | 1067.25
4 | Elsa | 710 | 563 | 1028.8
5 | Nueces Bay Plant 69KV Bus #2 | 7755 | 111 | 885.08
6 | Raymondville #2 | 3250 | 40 | 843.42
7 | Elsa | 690 | 1703 | 823.36
8 | Armstrong | 6050 | 48 | 753.4
9 | Blessing | 1030 | 146 | 740.42
10 | Kenedy | 1970 | 140 | 718.45
11 | Weslaco Unit | 5970 | 1752 | 655.25
12 | Freer | 1500 | 201 | 644.95
13 | Continental | 4080 | 162 | 470.5
14 | Rangerville | 3410 | 2276 | 461.8
15 | Alazan | 620CS | 222 | 420.16
16 | West McAllen | 4595 | 894 | 401.08
17 | Mustang Island | 8510CS | 47 | 395.72
18 | Moore Field | 3960 | 891 | 393.86
19 | Stadium | 7490 | 1350 | 385.01
20 | Rio Bravo | 5 | 1850 | 375.41
21 | Bishop | 7180 | 1005 | 345.97
22 | Foster Field | 2550 | 118 | 336.34
23 | Malone | 7550 | 144 | 323.86
24 | Mathis | 1410 | 152 | 320.21
25 | Victoria Power Plant 69KV Bus #1 | 8170 | 740 | 318.05
26 | Refugio | 1210 | 333 | 307.34
27 | Palmhurst | 2820 | 1979 | 304.35
28 | Alice | 2530 | 900 | 296.59
29 | Airline 69KV Bus #1 | 2180 | 12 | 293.92
30 | O'Conner | 390CN | 120 | 292.07
31 | Aransas Pass 69KV Bus #2 | 9130 | 300 | 291
32 | Haine Drive | 270 | 30 | 283.23
33 | Clarkwood | 7230 | 135 | 281.29
34 | Bishop | 2690 | 779 | 280.35
35 | Devine | 7100 | 850 | 279.78
36 | Dilley | 6400 | 970 | 279.36
37 | Causeway | 4775 | 967 | 277.75
38 | North Edinburg 69KV Bus #1 | 3570 | 437 | 274.83
39 | Taft | 1260 | 85 | 274.82
40 | North Padre Island | 7900 | 1100 | 270.51
41 | South East Edinburg | 4550 | 1721 | 267.15
42 | Randado | 8360 | 193 | 264.78
43 | Bruni | 5440 | 44 | 262.25
44 | West McAllen | 4515 | 1307 | 253.13
45 | Port Lavaca | 2490 | 675 | 252.21
46 | Goodwin | 3530 | 1253 | 252.09
47 | Columbus | 930CN | 945 | 249.2
48 | Falfurrias 69KV Bus | 2830 | 1344 | 242.41
49 | North Victoria | 7860 | 1387 | 239.74
50 | North Edinburg 69KV Bus #2 | 560 | 414 | 237.37
51 | Devine | 7090 | 901 | 232
52 | South East Edinburg | 4570 | 1538 | 228.94
53 | Nixon | 5990 | 524 | 227.55
54 | San Benito | 4030 | 1169 | 223.07
55 | Goodwin | 4390 | 2421 | 221.92
56 | Stadium | 7800 | 925 | 221.4
57 | Raymondville #2 | 3170 | 543 | 209.6
58 | Markham | 5550 | 85 | 204.78
59 | Dilley | 510 | 440 | 204
60 | Wadsworth | 8630 | 589 | 198.06
61 | South East Edinburg | 4015 | 1702 | 197.49
62 | Morris Street 138KV Bus #2 | 8715 | 2058 | 197.14
63 | Freer | 2900 | 304 | 196.95
64 | Mathis | 1420 | 812 | 196.78
65 | West Oso | 9085 | 868 | 194.29
66 | Kenedy | 6270 | 1046 | 191.91
67 | San Benito | 3910 | 1806 | 190.95
68 | Freer | 6320W | 171 | 190.45
69 | Darst | 800 | 161 | 179.66
70 | Live Oak | 1090 | 111 | 179.4
71 | Weslaco Unit | 7630 | 1557 | 179.33
72 | Crestonio | 260 | 1449 | 179.09
73 | Eagle Pass City | 2770 | 1475 | 178.8
74 | Washington Street 69KV Bus #3 | 6525 | 2000 | 175.53
75 | Placedo | 7970 | 387 | 174.65
76 | Garwood City | 2560 | 204 | 173.04
77 | Mathis | 340CS | 1506 | 168.34
78 | Magruder | 7870 | 1283 | 167.96
79 | McColl Road | 4780 | 1697 | 165.61
80 | Nixon | 810 | 543 | 165.29
81 | North Victoria | 6390 | 1128 | 161.8
82 | Los Fresnos | 3280 | 1573 | 161.22
83 | Aransas Pass 69KV Bus #2 | 1250 | 300 | 159.77
84 | Ingleside City | 6040 | 800 | 159.07
85 | Premont | 2730 | 213 | 154.16
86 | Wesmer | 9705 | 1168 | 153.15
87 | Pueblo | 95 | 1289 | 151.63
88 | Kenedy S.S. 69KV Bus | 8320 | 583 | 151.37
89 | West Harlingen | 3800 | 2248 | 150.7
90 | Kingsville | 1130 | 1684 | 149.81
91 | Odem | 385 | 262 | 149.04
92 | Raymondville #1 | 620S | 613 | 148.7
93 | Odem | 375 | 735 | 145.9
94 | Bonnieview | 8020CN | 407 | 145.64
95 | Morris Street 138KV Bus #1 | 8830 | 1454 | 144.82
96 | North Victoria | 7440 | 2232 | 142.62
97 | San Benito | 3860 | 1164 | 142
98 | Rangerville | 7750 | 625 | 141.97
99 | Rangerville | 4060 | 446 | 141.85
100 | Pleasanton | 2080 | 1305 | 141.12
101 | Carrizo Springs | 910 | 1584 | 141.05
102 | Wesmer | 4050 | 1557 | 140.9
103 | Maverick | 9680W | 580 | 140.67
104 | Robstown | 1650 | 58 | 139.14
105 | Crestonio | 6660 | 938 | 138.46
106 | Laredo Plant | 8695 | 1200 | 136.49
107 | Woolridge | 1110 | 1057 | 134.46
108 | Brackettville | 8460 | 1143 | 133.54
109 | McColl Road | 4400 | 793 | 133.17
110 | Santa Rosa | 4040 | 1362 | 132.08
111 | San Diego | 2890 | 1000 | 127.81
112 | Rodd Field | 3010 | 103 | 127.77
113 | San Ygnacio | 16060 | 11 | 127
114 | San Diego | 2880 | 1438 | 126.72
115 | Asherton | 2660 | 633 | 126.41
116 | Government Wells | 7240 | 247 | 125.85
117 | Edroy | 6990 | 230 | 125.61
118 | San Benito | 4135 | 653 | 124.66
119 | Crystal City | 140W | 1630 | 123.47
120 | Weaver Road | 1910 | 264 | 122.89
121 | La Pryor | 2440 | 562 | 122.78
122 | Uvalde 138KV Bus | 6620 | 1500 | 122.19
123 | Clarkwood | 5525 | 470 | 121.9
124 | Weslaco Unit | 8610 | 1863 | 119.61
125 | Weaver Road | 1900 | 105 | 119
126 | Santa Rosa | 3270 | 1045 | 118.9
127 | Pettus | 8210 | 455 | 118.89
128 | North McAllen | 3830 | 2024 | 118.43
129 | Naval Base 69KV Bus #2 | 6330 | 262 | 118.1
130 | Laguna | 9590 | 1693 | 117.48
131 | Goliad | 8220 | 1057 | 117.21
132 | Woodsboro | 8330CN | 1095 | 116.26
133 | Knippa | 6365 | 274 | 115.64
134 | La Pryor | 570 | 55 | 114.47
135 | Beeville | 2200 | 802 | 114.34
136 | Premont | 2720 | 928 | 113.23
137 | Columbus | 6180 | 876 | 112.18
138 | West Harlingen | 3720 | 1595 | 111.95
139 | Devine | 8100 | 1261 | 109.34
140 | Garwood City | 2570CN | 305 | 108.78
141 | Kenedy S.S. 138KV Bus | 8340 | 702 | 108.41
142 | South Mission | 5215 | 997 | 108.32
143 | Raymondville #1 | 630 | 761 | 107.88
144 | Harlingen | 380 | 1216 | 106.68
145 | Nueces Bay Plant 69KV Bus #2 | 7795 | 790 | 106
146 | Skidmore | 600 | 352 | 105.31
147 | Santo Nino | 645 | 1500 | 104.95
148 | Banquette | 9000 | 130 | 104.71
149 | Jourdanton | 880 | 345 | 104.11
150 | Kingsville | 1350 | 280 | 103.68
151 | North Alamo | 4370 | 780 | 102.86
152 | Berclair | 990C | 243 | 101
153 | Palmhurst | 3890 | 609 | 100.97
154 | Los Fresnos | 3290 | 802 | 100.89
155 | Leary Lane | 1430 | 1184 | 100.7
156 | Eagle Pass City | 2650 | 2950 | 99.96
157 | West McAllen | 6385 | 1448 | 98.62
158 | Campwood | 2610 | 880 | 97.85
159 | South McAllen | 3640 | 1100 | 97.73
160 | North Mercedes | 3840 | 720 | 97.39
161 | Southside 69KV Bus #4 | 8055 | 1066 | 97.21
162 | North Pharr | 3010 | 677 | 97.04
163 | Fulton Bank #2 | 9050 | 980 | 97.01
164 | Refugio | 1040 | 566 | 96.47
165 | Airline 69KV Bus #2 | 8370 | 367 | 95.92
166 | Karon Humble Pump | 9895 | 30 | 95.9
167 | Mathis | 2870 | 1000 | 95.47
168 | Raymondville #2 | 1280 | 1698 | 94.99
169 | Gregory | 5900 | 97 | 94.85
170 | Laredo Heights Bank #2 | 2450 | 2000 | 94.5
171 | Weslaco Unit | 8195 | 1752 | 94.4
172 | Palacios | 6840 | 1387 | 93
173 | Clarkwood | 9570 | 1187 | 92.97
174 | Zapata | 7330 | 2139 | 92.57
175 | Port Aransas | 3030CS | 600 | 92.43
176 | Parker | 9010 | 14 | 92.29
177 | Arcadia 69KV Bus #2 | 1440 | 2200 | 92.22
178 | Sinton | 6860 | 1320 | 92
179 | Eagle Lake | 310 | 828 | 91
180 | Markham | 6440CN | 460 | 90.27
181 | Bay City | 5960 | 1917 | 90.26
182 | Morris Street 138KV Bus #2 | 5655 | 1373 | 90.01
183 | South McAllen | 3850 | 965 | 87
184 | North Victoria | 1470 | 542 | 86.78
185 | Ganado | 5815 | 550 | 86.31
186 | Alazan | 2740CS | 40 | 85
187 | Morris Street 138KV Bus #2 | 8840 | 775 | 84.83
188 | Bay City | 1110CN | 974 | 84.73
189 | Sharyland | 2150 | 1296 | 84.07
190 | Eagle Pass Hydro | 1340 | 180 | 83.95
191 | Mines Road | 3745 | 3500 | 83.51
192 | Weslaco Unit | 7455 | 1460 | 83.38
193 | Live Oak | 1080 | 111 | 82.97
194 | Pharaoh | 5185 | 1993 | 82.32
195 | Arcadia 69KV Bus #1 | 6930 | 899 | 81.93
196 | West Oso | 9090 | 1610 | 81.9
197 | Continental | 4880 | 227 | 81.78
198 | South McAllen | 3790 | 1916 | 81.63
199 | Port Aransas | 990CS | 565 | 81.33
200 | Laredo Heights Bank #1 | 2100 | 2000 | 81.08
201 | Polk Avenue | 4520 | 1974 | 80.8
202 | North Mercedes | 3770 | 1460 | 79.84
203 | Stafford Hill | 1550 | 180 | 79.76
204 | Bruni | 1100 | 659 | 79.58
205 | Pharaoh | 1285 | 1215 | 79.34
206 | Morris Street 138KV Bus #2 | 7465 | 753 | 79.12
207 | South East Edinburg | 6580 | 2233 | 78.27
208 | Laredo Heights Bank #2 | 6810 | 2000 | 77.86
209 | McColl Road | 4790 | 1397 | 77.53
210 | North Alamo | 3610 | 1849 | 76.21
211 | Holly | 7620 | 1384 | 76.17
212 | Laredo Heights Bank #2 | 9080 | 1000 | 76
213 | Eagle Lake | 320CN | 692 | 75.88
214 | Aransas Pass 69KV Bus #2 | 660CS | 350 | 75.71
215 | Aransas Pass 69KV Bus #2 | 8280 | 350 | 75.47
216 | Cabaniss | 80 | 1102 | 75.35
217 | El Campo 69KV Bus | 2860 | 310 | 75.25
218 | Uvalde 138KV Bus | 550 | 370 | 75.04
219 | Laredo Heights Bank #2 | 2390 | 1000 | 74.91
220 | Edna | 5765 | 1100 | 73.43
221 | South Mission | 3980 | 4020 | 73.01
222 | Highway Nine 69KV Bus #2 | 6780 | 881 | 72.28
223 | Freer | 5200 | 1245 | 72.25
224 | Hamilton Road 138KV Bus #2 | 9665W | 276 | 72.03
225 | West McAllen | 4965 | 709 | 71.1
226 | Kingsville | 1670 | 402 | 71
227 | Raymondville #2 | 3240 | 1040 | 70.95
228 | Hamilton Road 138KV Bus #2 | 9655 | 560 | 70.62
229 | Kleberg 138KV Bus #1 | 280 | 1398 | 70.49
230 | Haine Drive | 8065 | 1455 | 69.14
231 | Del Rio City | 9790 | 2450 | 68.35
232 | North Weslaco | 4810 | 1460 | 67.62
233 | Washington Street 69KV Bus #2 | 2350 | 1000 | 67.5
234 | Naval Base 69KV Bus #2 | 1380 | 1931 | 67.34
235 | Zapata | 2710 | 41 | 67.34
236 | Cavazos | 3550 | 633 | 66.75
237 | Thomaston | 9580 | 53 | 66
238 | West McAllen | 4815 | 136 | 65.29
239 | Goliad | 6540 | 886 | 65.01
240 | Del Mar | 10 | 4700 | 64.74
241 | El Campo 69KV Bus | 5745 | 1104 | 64.3
242 | Moore Field | 3110 | 1211 | 64.3
243 | Polk Avenue | 4170 | 1432 | 64.19
244 | Three Rivers | 8430 | 141 | 63.09
245 | Causeway | 4795 | 1496 | 62.89
246 | Southside 69KV Bus #4 | 5335 | 948 | 62.76
247 | Rio Grande City | 3230 | 2326 | 62.64
248 | Rockport | 5940 | 113 | 62.5
249 | North McAllen | 2750 | 1849 | 62.44
250 | Pearsall | 7050 | 1334 | 62.12
251 | Port Isabel Switching Station | 4070 | 493 | 62.11
252 | West Oso | 9095 | 2507 | 61.67
253 | Seawall | 9450 | 155 | 60.49
254 | Rio Rico | 8330 | 1752 | 60.04
255 | West McAllen | 4555 | 1521 | 59.38
256 | Brookhollow | 8950 | 650 | 59.13
257 | Causeway | 4765 | 1100 | 58.91
258 | Beeville | 1760 | 874 | 58.71
259 | Banquette | 740 | 175 | 58.7
260 | Refugio | 5120 | 23 | 58.7
261 | Port Lavaca | 8310 | 230 | 58.58
262 | Harlingen Switching Station | 4090 | 1013 | 58.58
263 | Carancahua | 5870CN | 277 | 58.56
264 | Bay City | 2050 | 683 | 58.53
265 | Victoria Power Plant 69KV Bus #1 | 8070 | 444 | 58.44
266 | Big Wells | 1570 | 478 | 58.15
267 | North Mercedes | 4860 | 1459 | 56.17
268 | Continental | 3650 | 37 | 56
269 | Hearn Road | 8980 | 971 | 55.88
270 | Rachal | 6595 | 474 | 55.82
271 | Pearsall | 5580 | 1906 | 55.81
272 | South Padre Island | 5850 | 880 | 55.8
273 | Blessing | 8780 | 76 | 55.21
274 | Los Fresnos | 930S | 836 | 54
275 | Casa Blanca | 1300CS | 880 | 53.28
276 | Bay City | 7480 | 2004 | 52.81
277 | Falfurrias 138KV Bus | 5210 | 959 | 52.36
278 | Sharyland | 2020 | 1867 | 51.27
279 | McColl Road | 4910 | 1358 | 50.91
280 | Port Lavaca | 2480CN | 750 | 50.06
281 | Tatton | 8200 | 1514 | 49.67
282 | Bay City | 2700 | 1375 | 49.18
283 | Southside 69KV Bus #4 | 8045 | 1036 | 48.43
284 | North Pharr | 3090 | 1540 | 48.39
285 | Harlingen | 360 | 1624 | 48.21
286 | Washington Street 69KV Bus #3 | 6355 | 800 | 48.04
287 | McColl Road | 2810 | 1447 | 47.97
288 | Bay City | 6450 | 1072 | 47.06
289 | Victoria Power Plant 69KV Bus #2 | 1390 | 1351 | 46.51
290 | South Mission | 4650 | 1618 | 45.57
291 | San Diego | 1980 | 650 | 45.39
292 | Three Rivers | 5190 | 692 | 44.98
293 | Holly | 7740 | 1417 | 44.53
294 | Rodd Field | 205 | 1089 | 44.51
295 | Stadium | 7810 | 1310 | 44.47
296 | North Padre Island | 5170 | 860 | 44.4
297 | Yorktown | 8380 | 831 | 43.5
298 | Rio Bravo | 300W | 12 | 43.2
299 | Laredo Plant | 9305 | 1800 | 43.12
300 | Del Rio City | 430 | 1921 | 42.44
301 | Sharyland | 2010 | 954 | 42.06
302 | Buena Vista | 8965 | 755 | 41.99
303 | East Harrison 69KV Bus #2 | 3950 | 301 | 41.85
304 | Holly | 1480 | 1812 | 41.84
305 | Luling LCRA | 10CN | 167 | 41.8
306 | Fulton Bank #1 | 440CS | 1581 | 41.7
307 | Sharyland | 2035 | 1482 | 41.56
308 | Jourdanton | 5685 | 630 | 40.48
309 | Southside 69KV Bus #1 | 7905 | 2091 | 40.12
310 | George West | 1320 | 593 | 39.78
311 | Prairie Pump | 1940 | 38 | 39.66
312 | Pueblo | 130W | 1050 | 39.49
313 | Nueces Bay Plant 69KV Bus #1 | 7855 | 53 | 39.25
314 | Polk Avenue | 4600 | 2009 | 38.95
315 | Harlingen | 660 | 1511 | 37.94
316 | Kleberg 138KV Bus #2 | 6000 | 1552 | 37.75
317 | Palacios | 8550 | 43 | 37.12
318 | Bay City | 6670 | 1845 | 36.04
319 | Del Mar | 3440 | 2500 | 35.96
320 | Taft | 1180 | 928 | 35.54
321 | North Victoria | 7770 | 999 | 34.8
322 | Ingleside City | 7310 | 40 | 34.63
323 | Port Isabel Switching Station | 3820 | 440 | 34.41
324 | Del Rio City | 440W | 1388 | 34.29
325 | Arcadia 69KV Bus #2 | 5020 | 829 | 34.25
326 | Fulton Bank #2 | 3070CS | 1800 | 32.98
327 | Harlingen Switching Station | 4230 | 1511 | 32.96
328 | South Mission | 3620 | 3300 | 32.81
329 | Edna | 5785 | 457 | 32.12
330 | North Pharr | 3100 | 117 | 32
331 | Anna Street | 2250 | 1300 | 31.45
332 | Nueces Bay Plant 69KV Bus #2 | 7765 | 790 | 31.18
333 | Harlingen Switching Station | 4110 | 751 | 31.15
334 | Placedo | 7980 | 407 | 30.83
335 | Carrizo Springs | 860 | 1372 | 30.38
336 | Hearn Road | 9665 | 1039 | 29.95
337 | Arcadia 69KV Bus #1 | 1450 | 2029 | 29.62
338 | Los Fresnos | 3200 | 1806 | 29.33
339 | Southside 69KV Bus #1 | 7925 | 1195 | 29.08
340 | Greenlake | 2740CN | 20 | 29
341 | Santo Nino | 80 | 500 | 28.33
342 | Portland | 6505 | 1563 | 28
343 | Gateway | 390 | 1400 | 28
344 | East Harrison 69KV Bus #3 | 4360 | 1202 | 27.79
345 | Malone | 7560 | 150 | 27.65
346 | Del Rio City | 420W | 1630 | 27.41
347 | Morris Street 138KV Bus #1 | 8850 | 511 | 27
348 | Casa Blanca | 55 | 1010 | 26.95
349 | Morris Street 138KV Bus #2 | 8820 | 917 | 26.93
350 | North McAllen | 2980 | 1629 | 26.48
351 | Morris Street 138KV Bus #1 | 7625 | 683 | 26.36
352 | Ingleside City | 8050 | 1000 | 26.09
353 | Morris Street 138KV Bus #1 | 2515 | 1829 | 25.79
354 | Greta | 7890 | 304 | 25.48
355 | Cavazos | 3560 | 1166 | 25.31
356 | Pettus | 1020 | 336 | 24.97
357 | Nixon | 2620 | 590 | 24.88
358 | Falfurrias 69KV Bus | 1080W | 419 | 24.23
359 | Brookhollow | 7190 | 500 | 24.08
360 | Southside 69KV Bus #3 | 8025 | 622 | 24.04
361 | Arcadia 69KV Bus #2 | 8570 | 1440 | 23.39
362 | Port Aransas | 6940 | 900 | 23.13
363 | Carrizo Springs | 370W | 278 | 23.12
364 | Del Mar | 490 | 1500 | 23
365 | Southside 69KV Bus #3 | 5345 | 432 | 22.81
366 | Greenlake | 2760 | 675 | 22.73
367 | Hearn Road | 8990 | 812 | 22.56
368 | Wadsworth | 7660 | 1119 | 22.18
369 | Uvalde 138KV Bus | 480 | 1610 | 21.85
370 | Arcadia 69KV Bus #1 | 5030 | 1389 | 21.39
371 | Blessing | 8790 | 641 | 21.22
372 | Gregory | 5920 | 375 | 20.23
373 | Beeville | 8090 | 1281 | 20.1
374 | Nordheim | 470 | 245 | 20
375 | Santo Nino | 75 | 1800 | 19.97
376 | Brownsville | 3050 | 1766 | 19.76
377 | Luling LCRA | 20 | 354 | 19.54
378 | Polk Avenue | 4180 | 2743 | 19.27
379 | Portland | 9290 | 1007 | 19.1
380 | Hamilton Road 138KV Bus #1 | 9645 | 260 | 19
381 | Rockport | 5950 | 252 | 18.85
382 | North Victoria | 7430 | 524 | 18.7
383 | Live Oak | 1070 | 1692 | 18.7
384 | Magruder | 6700 | 1906 | 18.24
385 | George West | 730 | 721 | 18.22
386 | Greenlake | 2750CN | 840 | 18.21
387 | El Campo 138KV Bus | 6370 | 724 | 17.86
388 | Palmhurst | 1300 | 842 | 17.51
389 | Santo Nino | 70 | 1500 | 17.37
390 | Palmview | 3930 | 628 | 17.3
391 | Lytle | 2850 | 630 | 16.06
392 | Palmview | 9680 | 726 | 15.82
393 | Arcadia 69KV Bus #1 | 1460 | 1209 | 15.1
394 | Loyola | 195 | 662 | 15.05
395 | Pueblo | 275 | 1100 | 15.03
396 | Harlingen Switching Station | 320 | 519 | 14.9
397 | Kenedy S.S. 138KV Bus | 6750 | 877 | 14.7
398 | Ingleside City | 8060 | 800 | 14.53
399 | El Campo 69KV Bus | 7260 | 410 | 14.53
400 | Raymondville #2 | 4160 | 774 | 14.23
401 | West McAllen | 4505 | 1886 | 13.89
402 | South Padre Island | 4695 | 3079 | 13.81
403 | Airline 69KV Bus #2 | 2210 | 285 | 13.8
404 | Amistad Dam | 5450 | 790 | 13
405 | Airline 69KV Bus #2 | 6970 | 1066 | 12.81
406 | Pleasanton | 9505 | 1250 | 12.72
407 | San Benito | 4945 | 745 | 12.68
408 | Portland | 9370 | 1289 | 12.53
409 | Highway Nine 69KV Bus #2 | 6760 | 825 | 12.49
410 | Crystal City | 190 | 1020 | 12.49
411 | Arcadia 69KV Bus #2 | 1360 | 2361 | 12.49
412 | Rodd Field | 1730 | 910 | 12.26
413 | El Campo 138KV Bus | 2800 | 1276 | 12.26
414 | Del Rio City | 1930 | 963 | 12.21
415 | Runge | 7320 | 598 | 12.1
416 | Palacios | 6830 | 903 | 11.86
417 | Del Rio City | 9850 | 657 | 11.51
418 | Ganado | 5795 | 689 | 11.25
419 | Polk Avenue | 4900 | 1464 | 10.72
420 | Wesmer | 4480 | 1946 | 10.63
421 | North Edinburg 69KV Bus #1 | 4240 | 600 | 10.56
422 | Hall Acres Road | 3670 | 981 | 10.56
423 | Columbus | 9060 | 547 | 10.56
424 | Sinton | 1750 | 373 | 10.36
425 | Aransas Pass 69KV Bus #1 | 8270 | 450 | 10.27
426 | Seawall | 9420 | 1011 | 10.22
427 | Holly | 1370 | 716 | 10.09
428 | Loyola | 120CS | 698 | 9.93
429 | East Harrison 69KV Bus #2 | 4620 | 1285 | 9.58
430 | Highway Nine 69KV Bus #2 | 6770 | 1605 | 9.37
431 | Hall Acres Road | 5585 | 574 | 9.31
432 | Parker | 9260 | 70 | 9.01
433 | North Victoria | 1580 | 703 | 9
434 | Highway Nine 69KV Bus #1 | 7200 | 957 | 8.92
435 | La Grulla | 5110 | 992 | 8.85
436 | Mines Road | 3680 | 1000 | 8.79
437 | Matthews | 1740 | 39 | 8.64
438 | Woolridge | 1170 | 1416 | 8.56
439 | Magruder | 7690 | 907 | 8.54
440 | Southside 69KV Bus #2 | 7995 | 1483 | 8.48
441 | Eagle Lake | 9455 | 547 | 8.44
442 | Rio Grande City | 3220 | 1379 | 8.42
443 | Three Rivers | 2010CN | 753 | 8.27
444 | Charlotte | 8120 | 145 | 8.12
445 | Sinton | 180 | 1151 | 8.03
446 | Uvalde 138KV Bus | 540 | 800 | 7.98
447 | South Padre Island | 6440 | 1584 | 7.97
448 | Buena Vista | 9035 | 735 | 7.79
449 | Southside 69KV Bus #2 | 7955 | 979 | 7.78
450 | West McAllen | 4535 | 1810 | 7.6
451 | Crestonio | 270W | 599 | 7.41
452 | Polk Avenue | 4740 | 1282 | 7.04
453 | Highway Nine 69KV Bus #1 | 6720 | 1407 | 7.01
454 | Asphalt Mines | 500 | 23 | 7
455 | Polk Avenue | 4190 | 1901 | 6.94
456 | Airline 69KV Bus #1 | 8260 | 1039 | 6.92
457 | North Edinburg 69KV Bus #2 | 3810 | 224 | 6.88
458 | Santa Rosa | 3430 | 1454 | 6.87
459 | West Harlingen | 3700 | 1267 | 6.84
460 | Alice | 1790 | 440 | 6.8
461 | Beeville | 300CN | 1245 | 6.78
462 | Polk Avenue | 4610 | 2029 | 6.76
463 | North Alamo | 3580 | 391 | 6.56
464 | Edroy | 6980 | 354 | 6.55
465 | North McAllen | 9660 | 574 | 6.31
466 | Port Aransas | 1000 | 897 | 6.3
467 | North Weslaco | 4830 | 1243 | 6.27
468 | Refugio | 1170CN | 1143 | 6.15
469 | Laredo Heights Bank #1 | 9400 | 1000 | 6.01
470 | Hidalgo | 3680 | 889 | 6
471 | Southside 69KV Bus #3 | 8035 | 1147 | 6
472 | Airline 69KV Bus #1 | 9030 | 328 | 5.81
473 | Asherton | 2670 | 152 | 5.7
474 | Alice | 2540 | 1045 | 5.7
475 | Edna | 5775 | 870 | 5.56
476 | Hall Acres Road | 3460 | 2344 | 5.49
477 | Pearsall | 9905 | 180 | 5.45
478 | Leary Lane | 7530 | 1553 | 5.42
479 | East Harrison 69KV Bus #1 | 3030 | 975 | 5.17
480 | Kingsville | 1660 | 1459 | 5.14
481 | Stadium | 6950 | 610 | 5.13
482 | Pharaoh | 5175 | 1110 | 5.1
483 | Cabaniss | 240 | 1788 | 5.05
484 | Buena Vista | 9385 | 1380 | 4.99
485 | Highway Nine 69KV Bus #1 | 7210 | 1069 | 4.97
486 | La Pryor | 580 | 153 | 4.96
487 | Charlotte | 2780 | 510 | 4.96
488 | McKenzie Road | 330 | 1726 | 4.95
489 | Weil Tract (138/12KV) | 2520 | 294 | 4.94
490 | Rocksprings | 2600 | 349 | 4.82
491 | Alice | 1770 | 1180 | 4.8
492 | Leary Lane | 1540 | 1107 | 4.78
493 | Portland | 9270 | 1047 | 4.74
494 | Woolridge | 1120 | 1171 | 4.6
495 | Campwood | 3430W | 383 | 4.6
496 | Magruder | 245 | 640 | 4.5
497 | Rodd Field | 2190 | 610 | 4.49
498 | Cotulla | 90 | 593 | 4.25
499 | Anna Street | 780 | 1000 | 4.15
500 | Gregory | 8560 | 229 | 4.07
501 | Hall Acres Road | 5465 | 958 | 3.96
502 | Roma | 3060 | 2064 | 3.85
503 | West Harlingen | 4870 | 1949 | 3.84
504 | Brownsville | 4280 | 1045 | 3.81
505 | Point Comfort | 2460 | 330 | 3.59
506 | Kleberg 138KV Bus #1 | 9395 | 1107 | 3.58
507 | Laredo Plant | 8505 | 1000 | 3.54
508 | Government Wells | 6800 | 228 | 3.45
509 | North McAllen | 9640 | 2579 | 3.44
510 | Naval Base 69KV Bus #2 | 8440 | 1289 | 3.42
511 | Pleasanton | 120W | 1175 | 3.35
512 | East Harrison 69KV Bus #1 | 3080 | 1068 | 3.33
513 | East Harrison 69KV Bus #3 | 4310 | 977 | 3.3
514 | Goodwin | 4625 | 508 | 3.2
515 | North McAllen | 4995 | 2267 | 3.18
516 | Stadium | 8540 | 1795 | 3.05
517 | Yorktown | 8420 | 917 | 2.94
518 | Leary Lane | 6005 | 898 | 2.79
519 | Jourdanton | 5695 | 1030 | 2.79
520 | San Benito | 3920 | 1981 | 2.77
521 | Laguna | 9065 | 1697 | 2.75
522 | El Campo 138KV Bus | 7710 | 990 | 2.73
523 | Moore Field | 3120 | 392 | 2.73
524 | Southside 69KV Bus #2 | 8005 | 710 | 2.73
525 | Holly | 5820 | 937 | 2.64
526 | Holly | 1950 | 1423 | 2.61
527 | Magruder | 6690 | 544 | 2.54
528 | Wesmer | 6900 | 1179 | 2.28
529 | Seawall | 9325 | 1514 | 2.26
530 | Hearn Road | 870 | 982 | 2.25
531 | Beeville | 2380 | 950 | 2.25
532 | East Harrison 69KV Bus #2 | 3190 | 1115 | 2.22
533 | Government Wells | 7250 | 324 | 2.13
534 | Airline 69KV Bus #2 | 7280 | 632 | 2.02
535 | Zapata | 8290W | 2014 | 1.98
536 | Premont | 6570 | 1397 | 1.97
537 | Leary Lane | 1890 | 1396 | 1.97
538 | Crystal City | 330W | 920 | 1.96
539 | Laredo Plant | 8745 | 1000 | 1.9
540 | Brookhollow | 8960 | 700 | 1.8
541 | Rio Grande City | 3740 | 2481 | 1.76
542 | Airline 69KV Bus #2 | 9390 | 1054 | 1.75
543 | Clarkwood | 7610 | 226 | 1.74
544 | Eagle Pass City | 7060 | 1120 | 1.74
545 | Uvalde 138KV Bus | 5060 | 1600 | 1.73
546 | Gateway | 350 | 1500 | 1.64
547 | Weslaco Unit | 9805 | 1460 | 1.63
548 | Washington Street 69KV Bus #3 | 7015 | 1500 | 1.59
549 | Uvalde 138KV Bus | 9770 | 1600 | 1.57
550 | Kleberg 138KV Bus #1 | 1560 | 912 | 1.55
551 | Pleasanton | 9475 | 1650 | 1.55
552 | Weil Tract (138/12KV) | 5405 | 145 | 1.52
553 | Hearn Road | 2220 | 1604 | 1.44
554 | Big Wells | 2630W | 234 | 1.43
555 | Aransas Pass 69KV Bus #1 | 590 | 150 | 1.43
556 | Three Rivers | 2580 | 110 | 1.36
557 | Port Lavaca | 6850 | 680 | 1.35
558 | Holly | 9675 | 1267 | 1.32
559 | Airline 69KV Bus #2 | 9605 | 562 | 1.28
560 | Pharaoh | 1185 | 1013 | 1.27
561 | Haine Drive | 9690 | 1023 | 1.24
562 | South Mission | 3590 | 2295 | 1.22
563 | Eagle Pass City | 2745 | 2150 | 1.22
564 | Weil Tract (138/12KV) | 1990 | 1003 | 1.21
565 | North Victoria | 2240 | 814 | 1.17
566 | Brownsville | 4290 | 2358 | 1.13
567 | Anna Street | 900 | 1500 | 1.08
568 | Clarkwood | 7220 | 707 | 1.06
569 | Sabinal | 485 | 477 | 1.05
570 | Three Rivers | 5100 | 40 | 1
571 | Holly | 1220 | 2254 | 1
572 | Alice | 1780 | 1060 | 0.99
573 | Point Comfort | 6060 | 407 | 0.9
574 | Kleberg 138KV Bus #2 | 8140 | 49 | 0.88
575 | La Grulla | 4120 | 728 | 0.87
576 | Cabaniss | 75 | 968 | 0.84
577 | Kingsville | 1140 | 979 | 0.83
578 | La Grulla | 5005 | 1257 | 0.8
579 | Del Mar | 7930 | 2500 | 0.74
580 | Harlingen | 370 | 1784 | 0.72
581 | Fulton Bank #2 | 6070 | 1921 | 0.7
582 | Beeville | 8510CN | 979 | 0.7
583 | Beeville | 490CN | 1020 | 0.68
584 | South Mission | 3940 | 2187 | 0.67
585 | South McAllen | 3935 | 1096 | 0.67
586 | Rio Rico | 8290 | 1217 | 0.65
587 | Highway Nine 69KV Bus #1 | 9830 | 106 | 0.64
588 | Encinal | 2160 | 625 | 0.61
589 | Gateway | 380 | 500 | 0.59
590 | Leary Lane | 6175 | 1051 | 0.58
591 | Bruni | 5160 | 188 | 0.47
592 | Charlotte | 2790 | 170 | 0.45
593 | Hall Acres Road | 9595 | 574 | 0.44
594 | Magruder | 6680 | 646 | 0.41
595 | McKenzie Road | 140 | 116 | 0.41
596 | Hidalgo | 4845 | 438 | 0.38
597 | Highway Nine 69KV Bus #1 | 6730 | 380 | 0.37
598 | Sabinal | 200 | 400 | 0.34
599 | Taft | 5230 | 744 | 0.31
600 | Fulton Bank #1 | 2020CS | 1530 | 0.26
601 | Sinton | 360CS | 277 | 0.23
602 | Airline 69KV Bus #1 | 7390 | 1408 | 0.22
603 | Rockport | 5930 | 1011 | 0.19
604 | Eagle Pass City | 450 | 1625 | 0.17
605 | Laredo Plant | 8565 | 1200 | 0.15
606 | Banquette | 130CS | 540 | 0.14
607 | Arcadia 69KV Bus #1 | 1400 | 351 | 0.13
608 | Gregory | 420CS | 668 | 0.13
609 | Goodwin | 4380 | 1623 | 0.13
610 | Airline 69KV Bus #1 | 7270 | 985 | 0.13
611 | Roma | 3070S | 2068 | 0.11
612 | Hall Acres Road | 4895 | 1544 | 0.09
613 | Cotulla | 110 | 1345 | 0.05
614 | Rio Grande City | 3210 | 1205 | 0.05
615 | Laredo Heights Bank #1 | 6820 | 1000 | 0.02
616 | Airline 69KV Bus #1 | 5870 | 799 | 0.02
617 | Airline 69KV Bus #1 | 8890 | 411 | 0.02
618 | Anna Street | 5780 | 1500 | 0.02
619 | Anna Street | 850 | 1400 | 0.02
620 | Aransas Pass 69KV Bus #1 | 650 | 250 | 0.02
621 | Bandera Electric (Leakey) | L30 | 373 | 0.02
622 | Brookhollow | 7580 | 550 | 0.02
623 | Bruni | 1120W | 86 | 0.02
624 | Comstock | 290 | 191 | 0.02
625 | Conoco-Chittam Ranch | 8580 | 50 | 0.02
626 | Darst | 790 | 80 | 0.02
627 | Darst | 820 | 141 | 0.02
628 | Eagle Pass City | 2510 | 750 | 0.02
629 | East Harrison 69KV Bus #1 | 3000 | 1175 | 0.02
630 | Falfurrias 138KV Bus | 1070 | 881 | 0.02
631 | Foster Field | 8880 | 204 | 0.02
632 | Haine Drive | 9240 | 1290 | 0.02
633 | Hidalgo | 3400 | 814 | 0.02
634 | Kenedy | 1960 | 241 | 0.02
635 | Kleberg 138KV Bus #2 | 6410 | 370 | 0.02
636 | Knippa | 6535 | 14 | 0.02
637 | Laredo Plant | 8705 | 1000 | 0.02
638 | Lolita | 6320CN | 29 | 0.02
639 | McKenzie Road | 150 | 12 | 0.02
640 | Morris Street Network | 0 NET CC | 430 | 0.02
641 | Mustang Island | 9470 | 653 | 0.02
642 | Port Isabel Switching Station | 3760 | 800 | 0.02
643 | Randado | 8350 | 89 | 0.02
644 | Robstown | 7120 | 120 | 0.02
645 | Rocksprings | 8040 | 300 | 0.02
646 | San Diego | 2570CS | 600 | 0.02
647 | Santo Nino | 515 | 1500 | 0.02
648 | Skidmore | 380CN | 256 | 0.02
649 | Southside 69KV Bus #1 | 7935 | 43 | 0.02
650 | STP Construction Substation | 1010 | 10 | 0.02
651 | University | 920 | 60 | 0.02
652 | University | 930 | 100 | 0.02
653 | Victoria Power Plant 69KV Bus #2 | 7600 | 222 | 0.02
654 | Victoria Power Plant Network | 0 NET VIC | 192 | 0.02
655 | Washington Street 69KV Bus #1 | 0 NET LAR | 500 | 0.02
656 | Washington Street 69KV Bus #2 | 2360 | 700 | 0.02
657 | Washington Street 69KV Bus #2 | 2470 | 600 | 0.02

## CPL--Causes
CSW - Central Power & Light
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 10.63%
|  | Vegetation | 14.25%
|  | Animals and Birds | 14.53%
|  | People (Including cars and farm equip) | 2.163%
|  | Utility-owned Equipment | 42.71%
|  | Other | 3.253%
|  | Unknown | 12.47%
100%
24 Month Interim System-wide
Standards (01/01/1998 - 12/31/1999)
Interim System-wide SAIFI Standard
|  | CPL | 1.13
Interim System-wide SAIDI Standard
|  | CPL | 67

## SWEPCO--Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | CSW - Southwestern Elec. Power Co.
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 242
Due: |  | February 15, 2000
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 21972
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Industry Analysis Division
Office of Regulatory Affairs
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mel.eckhoff@puc.state.tx.us

## SWEPCO--Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
1998 And 1999
CSW - Southwestern Elec. Power Co.
Project 21972

## SWEPCO--System-SAIFI
CSW - Southwestern Elec. Power Co.
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 1.2991 | 0.074686 | 0.04235 | 0.096427 | 0.086974 | 0.16531 | 0.086312 | 0.13353 | 0.11882 | 0.14286 | 0.13745 | 0.11604 | 0.09788
1999 | 1.6288 | 0.1928 | 0.068521 | 0.061524 | 0.19585 | 0.20879 | 0.14403 | 0.15495 | 0.20086 | 0.10588 | 0.083525 | 0.58902 | 0.15244
Scheduled
1998 | 0.0085444 | 0.006649 | 0.0001476 | 0.0002362 | 0.0002362 | 0.0001417 | 0.0001535 | 0.0005019 | 0.000531 | 0.005905 | 3.54e-05 | 0 | 0
1999 | 0.001677 | 0 | 0.0004429 | 5.9e-06 | 5.9e-06 | 0 | 0.0003366 | 0.0003071 | 5.9e-06 | 4.72e-05 | 0.000189 | 0 | 0.0003248
Outside Causes
1998 | 0.030883 | 0.0036492 | 0.0010747 | 0.0003071 | 0.0008798 | 0.00062 | 0.0056746 | 0.0004665 | 0.0048066 | 0.0022084 | 0.0039091 | 0.0072099 | 7.68e-05
1999 | 0.17534 | 0.054071 | 0.0008798 | 0.0077236 | 0.0001063 | 0.034538 | 0.0041866 | 0.039917 | 0.0011869 | 0.0076045 | 0.01889 | 0.0037142 | 0.0025155
Major Events
1998 | 0.27647 | 0.040283 | 0.021175 | 0 | 0 | 0 | 0.097986 | 0.043159 | 0.30647 | 0.043206 | 0 | 0 | 0
1999 | 0.028893 | 0 | 0 | 0 | 0 | 0.028893 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## SWEPCO--System-SAIDI
CSW - Southwestern Elec. Power Co.
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 90.6009 | 3.3127 | 4.3288 | 8.7676 | 7.4369 | 11.7955 | 6.5652 | 7.3113 | 8.3859 | 8.2858 | 8.5322 | 6.8265 | 9.0649
1999 | 117.8778 | 18.2776 | 4.9468 | 4.1798 | 18.7477 | 17.7224 | 10.6488 | 8.311 | 11.5204 | 6.913 | 4.2068 | 3.1518 | 9.2357
Scheduled
1998 | 0.31577 | 0.15529 | 0.0092117 | 0.01181 | 0.01181 | 0.0086802 | 0.032755 | 0.042439 | 0.0041689 | 0.037201 | 0.0045822 | 0 | 0
1999 | 0.074709 | 0 | 0.011072 | 0.0001476 | 0.0001476 | 0 | 0.021648 | 0.005527 | 0.0002775 | 0.0030706 | 0.014249 | 0 | 0.018134
Outside Causes
1998 | 2.354 | 0.21927 | 0.10624 | 0.0081665 | 0.038317 | 0.031385 | 0.23684 | 0.034225 | 0.38286 | 0.47609 | 0.5788 | 0.23834 | 0.0034544
1999 | 7.9691 | 1.9144 | 0.04251 | 0.22172 | 0.0091467 | 2.6591 | 0.30942 | 1.3511 | 0.45435 | 0.21425 | 0.65775 | 0.068485 | 0.066968
Major Events
1998 | 27.7738 | 2.2711 | 1.163 | 0 | 0 | 0 | 14.237 | 5.7423 | 1.6336 | 2.7244 | 0 | 0 | 0
1999 | 9.518 | 0 | 0 | 0 | 0 | 9.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## SWEPCO--Feeder-SAIFI
Distribution Feeders on Texas System (10 or more customers) |  |  |  | Total Number of Feeders
242
CSW - Southwestern Elec. Power Co.
1999 SAIFI Ranking | Substation Identification | Feeder Identification | # Of Customers | 1999 SAIFI Value
1 | Leveretts Chapel | 10850 | 118 | 6.7034
2 | Friars Switch | 5790 | 95 | 6.5474
3 | Springhill | 8200 | 981 | 6.3619
4 | Carthage | 3350 | 259 | 6.3166
5 | Waskom | 7900 | 173 | 6.1156
6 | Whitney | 1480 | 1031 | 5.9079
7 | Tenaha | 2510 | 58 | 5.431
8 | Springhill | 6870 | 915 | 5.4219
9 | L.A.Pacific | 2260 | 190 | 5.3
10 | Pleasant Hill | 044 | 331 | 5.2477
11 | Turnertown | 1B10 | 306 | 5.2451
12 | Texarkana Plant | 6570 | 1236 | 4.9191
13 | South East Marshall | 7580 | 452 | 4.8208
14 | Pliler Road | 10380 | 1196 | 4.7584
15 | Texarkana Plant | 7960 | 753 | 4.5113
16 | Big Sandy | 7310 | 581 | 4.5077
17 | Leveretts Chapel | 5200 | 263 | 4.4905
18 | Friars Switch | 5920 | 42 | 4.4524
19 | Longview | 5520 | 613 | 4.4437
20 | Leveretts Chapel | 5700 | 126 | 4.3413
21 | Springhill | 8190 | 1021 | 4.3124
22 | Marshall | 580 | 799 | 4.2578
23 | South East Longview | 1780 | 180 | 4.2
24 | Whitney | 1490 | 880 | 4.1375
25 | Operations Center | 7240 | 804 | 4.1157
26 | Longview Heights | 8440 | 385 | 4.0078
27 | Lone Star Plant | 6120 | 16 | 4
28 | Evenside | 1G10 | 678 | 3.8687
29 | Sugar Hill | 2690 | 899 | 3.8198
30 | South East Marshall | 10160 | 1452 | 3.7748
31 | Carthage | 3360 | 710 | 3.7296
32 | Texarkana Plant | 6710 | 989 | 3.6734
33 | Airline | 1F00 | 497 | 3.66
34 | L.A.Pacific | 8030 | 372 | 3.5833
35 | Greggton | 1F70 | 328 | 3.564
36 | Center | 8140 | 1201 | 3.5387
37 | South East Marshall | 10920 | 1322 | 3.4614
38 | Howell | 2B80 | 348 | 3.4569
39 | Kilgore | 3090 | 826 | 3.4383
40 | Harrison Road | 8040 | 62 | 3.371
41 | South East Marshall | 10180 | 677 | 3.3619
42 | Friars Switch | 1900 | 206 | 3.2524
43 | Liberty City | 7990 | 374 | 3.1979
44 | Pilgrims Pride | 6150 | 300 | 3.1833
45 | Gilmer | 2490 | 1276 | 3.0815
46 | New Gladewater | 11980 | 600 | 2.9617
47 | Friars Switch | 5780 | 187 | 2.9519
48 | Pliler Road | 10370 | 1365 | 2.9128
49 | Hawkins | 9410 | 51 | 2.8824
50 | London | 5950 | 226 | 2.8628
51 | Clarksville | 9190 | 351 | 2.8575
52 | Big Sandy | 7300 | 586 | 2.8345
53 | Clarksville | 3670 | 236 | 2.822
54 | Kilgore | 7870 | 226 | 2.792
55 | Naples | 8730 | 905 | 2.7878
56 | Hughes Springs | 5650 | 469 | 2.7335
57 | Turnertown | 1B20 | 476 | 2.6534
58 | Lake Lamond | 1380 | 607 | 2.6326
59 | Taylor Street | 6760 | 1011 | 2.6133
60 | Waskom | 7890 | 451 | 2.5942
61 | Kilgore | 7190 | 399 | 2.594
62 | Kilgore | 7880 | 601 | 2.5691
63 | London | 5940 | 165 | 2.5636
64 | Naples | 3290 | 469 | 2.5565
65 | Evenside | 1G00 | 1003 | 2.4696
66 | Longview Heights | 1B40 | 816 | 2.451
67 | 39th Street | 2640 | 978 | 2.4366
68 | Texarkana Plant | 7980 | 337 | 2.4095
69 | Center | 2190 | 1132 | 2.4037
70 | Evenside | 1F90 | 691 | 2.3907
71 | Airline | 1E90 | 924 | 2.355
72 | Longview Heights | 8430 | 815 | 2.3337
73 | Clarksville | 3660 | 491 | 2.3218
74 | Daingerfield | 1960 | 671 | 2.3174
75 | Tatum | 10840 | 605 | 2.3174
76 | Longview Heights | 9000 | 1041 | 2.3007
77 | Sabine | 5110 | 153 | 2.2876
78 | Kilgore | 4650 | 524 | 2.2653
79 | Pittsburg | 5460 | 1117 | 2.2632
80 | Dekalb | 2430 | 723 | 2.2545
81 | Marshall | 2000 | 173 | 2.2428
82 | Marshall Uptown | 3210 | 193 | 2.228
83 | Hughes Springs | 1Z00 | 770 | 2.2234
84 | Poynter | 7800 | 163 | 2.2147
85 | Poynter | 7590 | 1017 | 2.2134
86 | Pliler Road | 12470 | 917 | 2.2017
87 | Sabine | 5130 | 1751 | 2.1239
88 | Hawkins | 2530 | 239 | 2.113
89 | Texarkana Plant | 7970 | 989 | 2.1001
90 | Kings Hwy | 9030 | 865 | 2.0948
91 | Cookville | 1E70 | 150 | 2.08
92 | New Gladewater | 11970 | 985 | 2.0609
93 | Winnsboro | 2040 | 592 | 2.0236
94 | London | 5930 | 176 | 1.9886
95 | New Boston | 1620 | 672 | 1.9449
96 | Richmond Road | 6980 | 641 | 1.9142
97 | Linden | 2540 | 784 | 1.9031
98 | Kilgore | 7860 | 382 | 1.8403
99 | IPC Jefferson | 8020 | 652 | 1.816
100 | Howell | 2B90 | 294 | 1.8027
101 | Winfield | 2B70 | 500 | 1.786
102 | New Boston | 9610 | 800 | 1.7725
103 | Jefferson 69KV | 9340 | 977 | 1.7554
104 | Atlanta | 4460 | 1000 | 1.71
105 | Bloomburg | 7350 | 238 | 1.7059
106 | 39th Street | 2630 | 1551 | 1.7054
107 | Whitney | 4080 | 932 | 1.6921
108 | Beckville | 1U50 | 390 | 1.6846
109 | Hooks | 10960 | 1180 | 1.6331
110 | Longview Heights | 9240 | 753 | 1.6202
111 | West Mount Pleasant | 1L00 | 634 | 1.5931
112 | Poynter | 3270 | 1041 | 1.5379
113 | Beckville | 9120 | 223 | 1.5202
114 | Daingerfield | 1950 | 707 | 1.5149
115 | Howell | 2B60 | 290 | 1.469
116 | Lake Lamond | 4400 | 1105 | 1.4507
117 | New Hope | 8000 | 1046 | 1.4465
118 | Hallsville | 5720 | 590 | 1.4407
119 | Taylor Street | 4290 | 674 | 1.4184
120 | Richmond Road | 4020 | 843 | 1.414
121 | Scottsville | 1J30 | 459 | 1.4074
122 | Atlanta | 2150 | 1224 | 1.3775
123 | Airline | 1N30 | 527 | 1.3757
124 | Mineola | 7130 | 864 | 1.3727
125 | Linden | 10020 | 473 | 1.3573
126 | Center | 9520 | 728 | 1.3475
127 | Longview | 6770 | 1164 | 1.3376
128 | North Marshall | 8670 | 1144 | 1.3322
129 | Poynter | 7680 | 978 | 1.3313
130 | Poynter | 9550 | 935 | 1.3209
131 | Carthage | 5760 | 1147 | 1.3139
132 | Lake Lamond | 8570 | 1173 | 1.2975
133 | Operation Center | 1S80 | 1090 | 1.2899
134 | Carthage | 10240 | 1080 | 1.2861
135 | Hawkins | 6310 | 158 | 1.2722
136 | New Hope | 2120 | 86 | 1.2558
137 | Lake Lamond | 6850 | 772 | 1.2526
138 | Kings Hwy | 9540 | 966 | 1.2453
139 | Mount Vernon | 9130 | 1181 | 1.2439
140 | Airline | 1S30 | 105 | 1.2095
141 | Sabine | 5120 | 739 | 1.18
142 | Marshall | 590 | 439 | 1.1731
143 | North Laneville | 10660 | 385 | 1.1558
144 | Harrison Road | 11870 | 909 | 1.1507
145 | Richmond Road | 8050 | 920 | 1.1435
146 | Harrison Road | 11880 | 1495 | 1.1351
147 | Sugar Hill | 2370 | 652 | 1.1288
148 | Greggton | 1F50 | 645 | 1.1271
149 | Greggton | 2A90 | 1290 | 1.107
150 | Kings Hwy | 9040 | 1090 | 1.1018
151 | Grand Saline | 7110 | 1128 | 1.0816
152 | Hallsville | 2380 | 559 | 1.0447
153 | Longview | 5510 | 1013 | 1.0385
154 | Taylor Street | 220 | 550 | 1
155 | Gilmer | 2450 | 555 | 0.97477
156 | Atlanta | 2140 | 1334 | 0.91679
157 | North Marshall | 8660 | 846 | 0.86761
158 | Daingerfield | 1970 | 426 | 0.82629
159 | Greggton | 1V20 | 932 | 0.82511
160 | Hawkins | 2520 | 280 | 0.825
161 | 12th Street | 2230 | 865 | 0.79769
162 | Lake Lamond | 4070 | 1068 | 0.7706
163 | Hooks | 10950 | 651 | 0.74962
164 | Gates | 1X70 | 841 | 0.73127
165 | Scottsville | 1J10 | 383 | 0.70757
166 | IPC 69KV | 1R60 | 27 | 0.66667
167 | Whitney | 4090 | 586 | 0.65358
168 | Naples | 8720 | 170 | 0.64118
169 | New Boston | 5140 | 1099 | 0.63057
170 | West Mount Pleasant | 1G70 | 74 | 0.62162
171 | North Marshall | 9800 | 1026 | 0.61696
172 | South East Marshall | 10170 | 1113 | 0.61635
173 | Whitney | 4420 | 369 | 0.61247
174 | Richmond Road | 5290 | 1472 | 0.60666
175 | Petty | 11470 | 780 | 0.60513
176 | Kilgore | 7850 | 306 | 0.57843
177 | 39th Street | 1V70 | 1360 | 0.56029
178 | Pittsburg | 5450 | 1259 | 0.55123
179 | Richmond Road | 1L40 | 1247 | 0.51724
180 | Atlanta | 8070 | 743 | 0.50202
181 | North Marshall | 7600 | 1106 | 0.5
182 | Carthage | 3370 | 384 | 0.4974
183 | Taylor Street | 9510 | 731 | 0.49248
184 | Taylor Street | 7920 | 1101 | 0.47684
185 | Alba | 12400 | 533 | 0.46529
186 | Dekalb | 2440 | 650 | 0.45385
187 | New Boston | 9620 | 630 | 0.44762
188 | 39th Street | 1V60 | 697 | 0.44476
189 | Mineola | 10990 | 1102 | 0.43739
190 | Operation Center | 7830 | 1180 | 0.41949
191 | Mineola | 3680 | 589 | 0.40747
192 | Waskom | 8180 | 787 | 0.38882
193 | Winnsboro | 1P00 | 613 | 0.37031
194 | Atlanta | 1U80 | 1071 | 0.35574
195 | Operation Center | 11630 | 3163 | 0.35567
196 | Airline | 1F10 | 674 | 0.3457
197 | Tenaha | 2500 | 434 | 0.3318
198 | Westwood | 3710 | 52 | 0.32692
199 | Grand Saline | 7120 | 926 | 0.32397
200 | Petty | 11460 | 1177 | 0.3237
201 | Gilmer | 2480 | 997 | 0.32297
202 | Clarksville | 9180 | 577 | 0.32062
203 | Turnertown | 1B00 | 227 | 0.31718
204 | Whitney | 1A00 | 682 | 0.31672
205 | Taylor Street | 5080 | 1079 | 0.2975
206 | Clarksville | 9200 | 650 | 0.27846
207 | Petty | 8370 | 588 | 0.27551
208 | Clarksville | 9210 | 1539 | 0.25081
209 | Kilgore | 3150 | 1045 | 0.24402
210 | Pittsburg | 8680 | 403 | 0.24318
211 | Gates | 1X40 | 716 | 0.22905
212 | Mount Pleasant | 1920 | 1292 | 0.2144
213 | Knox Lee Power Plant | 1U90 | 112 | 0.1875
214 | Mount Vernon | 9140 | 788 | 0.18401
215 | Lake Lamond | 9430 | 1079 | 0.1835
216 | Mount Pleasant | 1930 | 435 | 0.14483
217 | North Mineola | 5380 | 130 | 0.13846
218 | Lake Lamond | 6860 | 650 | 0.13231
219 | Mount Pleasant | 5360 | 831 | 0.11793
220 | Mount Pleasant | 5370 | 601 | 0.11647
221 | Dekalb | 3200 | 534 | 0.1161
222 | Operation Center | 1S90 | 787 | 0.11563
223 | 39th Street | 2610 | 1101 | 0.11444
224 | Winfield | 4100 | 258 | 0.1124
225 | Monroe Corners | 6520 | 117 | 0.11111
226 | Marshall | 4630 | 748 | 0.10829
227 | Cookville | 1E60 | 185 | 0.1027
228 | Lake Lamond | 9440 | 716 | 0.092179
229 | Marshall Uptown | 3220 | 471 | 0.089172
230 | Winnsboro | 2050 | 701 | 0.088445
231 | Jefferson 69KV | 9350 | 316 | 0.075949
232 | Mineola | 9360 | 445 | 0.065169
233 | Gates | 1X60 | 1136 | 0.064261
234 | Mount Pleasant | 5190 | 409 | 0.06357
235 | Greggton | 1F60 | 971 | 0.044284
236 | Lake Lamond | 9770 | 639 | 0.028169
237 | Longview | 5550 | 1222 | 0.023732
238 | Longview | 5530 | 1057 | 0.022706
239 | West Mount Pleasant | 1G90 | 436 | 0.016055
240 | Center | 2180 | 15 | 6.6667e-07
241 | Broad Street | 1B30 | 500 | 2e-08
242 | Longview | 5540 | 1019 | 9.8135e-09

## SWEPCO--Feeder-SAIDI
Distribution Feeders on Texas System (10 or more customers) |  |  |  | Total Number of Feeders
242
CSW - Southwestern Elec. Power Co.
1999 SAIDI Ranking | Substation Identification | Feeder Identification | # Of Customers | 1999 SAIDI Value
1 | Kilgore | 3090 | 826 | 823.6271
2 | Friars Switch | 5790 | 95 | 809.5895
3 | Turnertown | 1B10 | 306 | 808.4248
4 | South East Longview | 1780 | 180 | 758.7389
5 | Marshall | 580 | 799 | 647.607
6 | Friars Switch | 5780 | 187 | 560.7487
7 | Airline | 1F00 | 497 | 558.8471
8 | Longview | 5520 | 613 | 554.6036
9 | Kilgore | 7870 | 226 | 554.1549
10 | Tenaha | 2510 | 58 | 548.069
11 | L.A.Pacific | 8030 | 372 | 546.2097
12 | Leveretts Chapel | 5200 | 263 | 536.8289
13 | Friars Switch | 5920 | 42 | 527.881
14 | Marshall | 2000 | 173 | 511.8092
15 | Waskom | 7900 | 173 | 507.5954
16 | Turnertown | 1B20 | 476 | 477.0735
17 | Pliler Road | 10370 | 1365 | 460.7722
18 | Howell | 2B80 | 348 | 458.6897
19 | Leveretts Chapel | 10850 | 118 | 435.4407
20 | South East Marshall | 10180 | 677 | 429.9852
21 | London | 5950 | 226 | 419.115
22 | Carthage | 3360 | 710 | 414.1014
23 | L.A.Pacific | 2260 | 190 | 384.0632
24 | Springhill | 8200 | 981 | 383.1376
25 | Airline | 1E90 | 924 | 377.7543
26 | Greggton | 1F70 | 328 | 368.7378
27 | Lone Star Plant | 6120 | 16 | 346.5625
28 | Springhill | 8190 | 1021 | 343.6121
29 | Whitney | 1480 | 1031 | 342.5984
30 | Waskom | 7890 | 451 | 335.5299
31 | Leveretts Chapel | 5700 | 126 | 324.2698
32 | Pleasant Hill | 044 | 331 | 304.4562
33 | Kilgore | 7880 | 601 | 302.7171
34 | Kilgore | 7190 | 399 | 301.0376
35 | New Hope | 8000 | 1046 | 291.7447
36 | Pliler Road | 10380 | 1196 | 286.5184
37 | Kilgore | 4650 | 524 | 285.6794
38 | Carthage | 3350 | 259 | 279.0347
39 | Friars Switch | 1900 | 206 | 278.5583
40 | London | 5930 | 176 | 271.7216
41 | Whitney | 1490 | 880 | 266.8455
42 | Howell | 2B90 | 294 | 244.2381
43 | Longview Heights | 8430 | 815 | 235.5215
44 | Kilgore | 7860 | 382 | 221.8639
45 | Big Sandy | 7310 | 581 | 221.6299
46 | Evenside | 1F90 | 691 | 216.7844
47 | Marshall Uptown | 3210 | 193 | 215.8031
48 | Longview Heights | 8440 | 385 | 215.0961
49 | Operations Center | 7240 | 804 | 212.2338
50 | North Laneville | 10660 | 385 | 212.0182
51 | Hawkins | 2530 | 239 | 208.4561
52 | Big Sandy | 7300 | 586 | 205.5717
53 | Winfield | 2B70 | 500 | 199.852
54 | Clarksville | 9190 | 351 | 199.2051
55 | North Marshall | 8670 | 1144 | 198.2587
56 | Pilgrims Pride | 6150 | 300 | 195.7667
57 | South East Marshall | 7580 | 452 | 194.9248
58 | North Marshall | 8660 | 846 | 190.6123
59 | Sabine | 5130 | 1751 | 184.8858
60 | Tatum | 10840 | 605 | 184.3554
61 | Pliler Road | 12470 | 917 | 183.4646
62 | Evenside | 1G10 | 678 | 183.208
63 | Taylor Street | 4290 | 674 | 181.2418
64 | Hawkins | 9410 | 51 | 180.8627
65 | Naples | 3290 | 469 | 175.6461
66 | Cookville | 1E70 | 150 | 174.92
67 | Clarksville | 3670 | 236 | 173.928
68 | South East Marshall | 10160 | 1452 | 171.6832
69 | Springhill | 6870 | 915 | 170.9836
70 | Naples | 8730 | 905 | 170.0773
71 | Harrison Road | 8040 | 62 | 169.8065
72 | Kings Hwy | 9030 | 865 | 169.3064
73 | Longview Heights | 9000 | 1041 | 160.5793
74 | Liberty City | 7990 | 374 | 159.9973
75 | Sabine | 5120 | 739 | 159.6928
76 | South East Marshall | 10920 | 1322 | 158.9887
77 | Texarkana Plant | 7960 | 753 | 156.9814
78 | Linden | 2540 | 784 | 154.264
79 | Whitney | 4080 | 932 | 151.677
80 | Hughes Springs | 5650 | 469 | 151.2452
81 | Gilmer | 2490 | 1276 | 150.5024
82 | Pittsburg | 5460 | 1117 | 150.077
83 | Sugar Hill | 2690 | 899 | 147.3215
84 | Center | 8140 | 1201 | 146.7885
85 | New Boston | 1620 | 672 | 144.1756
86 | Texarkana Plant | 6570 | 1236 | 144.11
87 | Center | 2190 | 1132 | 141.4523
88 | Howell | 2B60 | 290 | 137.2207
89 | Evenside | 1G00 | 1003 | 136.9063
90 | Greggton | 1F50 | 645 | 135.5271
91 | Lake Lamond | 4400 | 1105 | 133.9891
92 | New Hope | 2120 | 86 | 133.8721
93 | London | 5940 | 165 | 132.4242
94 | Kings Hwy | 9540 | 966 | 132.2567
95 | Longview Heights | 1B40 | 816 | 127.8799
96 | Kilgore | 7850 | 306 | 127.6405
97 | 39th Street | 2640 | 978 | 124.9059
98 | Hughes Springs | 1Z00 | 770 | 122.5948
99 | Bloomburg | 7350 | 238 | 121.2395
100 | Lake Lamond | 4070 | 1068 | 120.6601
101 | Texarkana Plant | 6710 | 989 | 119.2417
102 | New Gladewater | 11980 | 600 | 119.15
103 | Daingerfield | 1960 | 671 | 118.4039
104 | Longview | 5510 | 1013 | 106.3396
105 | Harrison Road | 11880 | 1495 | 105.0903
106 | Beckville | 1U50 | 390 | 103.6385
107 | Marshall | 590 | 439 | 103.0091
108 | Hawkins | 6310 | 158 | 101.3797
109 | Sabine | 5110 | 153 | 97.7516
110 | Richmond Road | 6980 | 641 | 97.0296
111 | Mineola | 7130 | 864 | 94.4549
112 | Jefferson 69KV | 9340 | 977 | 93.259
113 | New Boston | 9610 | 800 | 89.8012
114 | Hooks | 10960 | 1180 | 89.2144
115 | Atlanta | 4460 | 1000 | 89.186
116 | Kings Hwy | 9040 | 1090 | 88.322
117 | Longview Heights | 9240 | 753 | 84.6521
118 | Poynter | 9550 | 935 | 84.4128
119 | Center | 9520 | 728 | 84.2527
120 | Poynter | 7800 | 163 | 83.8589
121 | New Gladewater | 11970 | 985 | 83.5655
122 | Scottsville | 1J30 | 459 | 82.7778
123 | Longview | 6770 | 1164 | 80.622
124 | Taylor Street | 6760 | 1011 | 80.1563
125 | Lake Lamond | 1380 | 607 | 79.9077
126 | Winnsboro | 2040 | 592 | 79.8868
127 | Daingerfield | 1950 | 707 | 79.6902
128 | Linden | 10020 | 473 | 78.2833
129 | Carthage | 5760 | 1147 | 77.1883
130 | Clarksville | 3660 | 491 | 74.7719
131 | Lake Lamond | 6850 | 772 | 73.7824
132 | Airline | 1S30 | 105 | 71.381
133 | Poynter | 7590 | 1017 | 71.0905
134 | Gilmer | 2450 | 555 | 70.8036
135 | Airline | 1N30 | 527 | 69.2676
136 | Dekalb | 2430 | 723 | 68.3624
137 | Richmond Road | 4020 | 843 | 67.8897
138 | Poynter | 7680 | 978 | 67.6667
139 | Gates | 1X70 | 841 | 66.497
140 | Hallsville | 5720 | 590 | 64.6508
141 | Naples | 8720 | 170 | 62.9118
142 | 39th Street | 2630 | 1551 | 61.5081
143 | South East Marshall | 10170 | 1113 | 61.2857
144 | Poynter | 3270 | 1041 | 60.7935
145 | Hawkins | 2520 | 280 | 60.7036
146 | Greggton | 1V20 | 932 | 59.7779
147 | Richmond Road | 8050 | 920 | 59.7674
148 | Grand Saline | 7110 | 1128 | 59.7615
149 | New Boston | 9620 | 630 | 58.8063
150 | 12th Street | 2230 | 865 | 58.6012
151 | Beckville | 9120 | 223 | 56.5112
152 | Petty | 11470 | 780 | 56.4115
153 | IPC Jefferson | 8020 | 652 | 55.5521
154 | Hooks | 10950 | 651 | 54.9278
155 | Daingerfield | 1970 | 426 | 53.5188
156 | Texarkana Plant | 7980 | 337 | 52.7092
157 | West Mount Pleasant | 1L00 | 634 | 52.3722
158 | Atlanta | 2140 | 1334 | 52.1529
159 | New Boston | 5140 | 1099 | 52.1429
160 | West Mount Pleasant | 1G70 | 74 | 51.8108
161 | Sugar Hill | 2370 | 652 | 48.4816
162 | Lake Lamond | 8570 | 1173 | 46.4672
163 | Carthage | 10240 | 1080 | 46.462
164 | North Marshall | 7600 | 1106 | 44.8128
165 | Gates | 1X40 | 716 | 44.1397
166 | Texarkana Plant | 7970 | 989 | 43.727
167 | Scottsville | 1J10 | 383 | 43.5144
168 | North Marshall | 9800 | 1026 | 42.2612
169 | Atlanta | 8070 | 743 | 41.4563
170 | Taylor Street | 220 | 550 | 39.1855
171 | Whitney | 4090 | 586 | 38.1195
172 | Taylor Street | 5080 | 1079 | 37.493
173 | Mount Vernon | 9130 | 1181 | 36.7671
174 | Atlanta | 2150 | 1224 | 36.4992
175 | Kilgore | 3150 | 1045 | 36.3828
176 | Waskom | 8180 | 787 | 35.9212
177 | 39th Street | 1V70 | 1360 | 33.9471
178 | Lake Lamond | 9430 | 1079 | 32.8981
179 | IPC 69KV | 1R60 | 27 | 32.5926
180 | Richmond Road | 5290 | 1472 | 32.502
181 | Greggton | 2A90 | 1290 | 32.3124
182 | Operation Center | 1S80 | 1090 | 31.7064
183 | Whitney | 4420 | 369 | 30.9837
184 | Pittsburg | 5450 | 1259 | 30.8737
185 | Mineola | 3680 | 589 | 30.0985
186 | Operation Center | 7830 | 1180 | 29.3797
187 | Richmond Road | 1L40 | 1247 | 29.1748
188 | Whitney | 1A00 | 682 | 28.5968
189 | Petty | 8370 | 588 | 27.3912
190 | Tenaha | 2500 | 434 | 26.5668
191 | Dekalb | 2440 | 650 | 25.4385
192 | Taylor Street | 7920 | 1101 | 25.3279
193 | Airline | 1F10 | 674 | 25.2908
194 | Harrison Road | 11870 | 909 | 25.0825
195 | Winnsboro | 1P00 | 613 | 25.0049
196 | Mount Pleasant | 1920 | 1292 | 23.3142
197 | Carthage | 3370 | 384 | 22.0781
198 | Atlanta | 1U80 | 1071 | 21.7096
199 | Taylor Street | 9510 | 731 | 21.3707
200 | Knox Lee Power Plant | 1U90 | 112 | 20.0089
201 | Turnertown | 1B00 | 227 | 19.63
202 | Clarksville | 9210 | 1539 | 19.627
203 | Gilmer | 2480 | 997 | 19.5135
204 | Westwood | 3710 | 52 | 18.5385
205 | Lake Lamond | 9440 | 716 | 17.9665
206 | Alba | 12400 | 533 | 17.7674
207 | Marshall Uptown | 3220 | 471 | 17.2887
208 | Pittsburg | 8680 | 403 | 16.9677
209 | Mount Vernon | 9140 | 788 | 15.6827
210 | Clarksville | 9180 | 577 | 15.4679
211 | Operation Center | 11630 | 3163 | 15.0076
212 | Grand Saline | 7120 | 926 | 14.6274
213 | 39th Street | 1V60 | 697 | 14.5725
214 | Petty | 11460 | 1177 | 14.4639
215 | Mineola | 10990 | 1102 | 13.6207
216 | Clarksville | 9200 | 650 | 12.9908
217 | Dekalb | 3200 | 534 | 12.6891
218 | Hallsville | 2380 | 559 | 11.9606
219 | Monroe Corners | 6520 | 117 | 9.9915
220 | Cookville | 1E60 | 185 | 9.9622
221 | Gates | 1X60 | 1136 | 9.9349
222 | Mount Pleasant | 5360 | 831 | 9.1203
223 | Jefferson 69KV | 9350 | 316 | 8.9494
224 | Mount Pleasant | 1930 | 435 | 8.8322
225 | North Mineola | 5380 | 130 | 8.3385
226 | Lake Lamond | 6860 | 650 | 7.3031
227 | Winnsboro | 2050 | 701 | 7.1626
228 | Mount Pleasant | 5370 | 601 | 7.025
229 | Marshall | 4630 | 748 | 6.5762
230 | Winfield | 4100 | 258 | 5.9574
231 | Mineola | 9360 | 445 | 5.6629
232 | Greggton | 1F60 | 971 | 5.4645
233 | Mount Pleasant | 5190 | 409 | 5.4597
234 | 39th Street | 2610 | 1101 | 4.861
235 | Operation Center | 1S90 | 787 | 4.5896
236 | Longview | 5530 | 1057 | 3.1514
237 | Lake Lamond | 9770 | 639 | 1.7997
238 | Longview | 5550 | 1222 | 1.4763
239 | West Mount Pleasant | 1G90 | 436 | 0.22477
240 | Center | 2180 | 15 | 6.6667e-07
241 | Broad Street | 1B30 | 500 | 2e-08
242 | Longview | 5540 | 1019 | 9.8135e-09

## SWEPCO--Causes
CSW - Southwestern Elec. Power Co.
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 25.52%
|  | Vegetation | 28.48%
|  | Animals and Birds | 22.58%
|  | People (Including cars and farm equip) | 1.98%
|  | Utility-owned Equipment | 12.07%
|  | Other | 0.8%
|  | Unknown | 8.57%
100%
24 Month Interim System-wide
Standards (01/01/1998 - 12/31/1999)
Interim System-wide SAIFI Standard
|  | SWEPCO (Texas) | 1.46
Interim System-wide SAIDI Standard
|  | SWEPCO (Texas) | 104

## WTU--Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | CSW - West Texas Utilities
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 396
Due: |  | February 15, 2000
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 21972
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Industry Analysis Division
Office of Regulatory Affairs
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mel.eckhoff@puc.state.tx.us

## WTU--Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
1998 And 1999
CSW - West Texas Utilities
Project 21972

## WTU--System-SAIFI
CSW - West Texas Utilities
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 0.50869 | 0.049678 | 0.015888 | 0.04262 | 0.024139 | 0.070544 | 0.043807 | 0.088884 | 0.069587 | 0.025446 | 0.033324 | 0.02555 | 0.019219
1999 | 0.40472 | 0.016589 | 0.012657 | 0.046782 | 0.040184 | 0.066403 | 0.05739 | 0.049124 | 0.036864 | 0.025822 | 0.024881 | 0.008684 | 0.019344
Scheduled
1998 | 0.026653 | 0.014487 | 0.0025566 | 0.00041825 | 0.00063784 | 0.0010247 | 0.0011136 | 0.00071626 | 0.0005385 | 0.00071626 | 0.0030585 | 0.00089402 | 0.00049145
1999 | 0.054593 | 0.0011973 | 0.0075966 | 0.0091023 | 0.015193 | 0.0016312 | 0.0011397 | 0.0020024 | 0.011648 | 0.00050191 | 0.001443 | 0.0009463 | 0.0021906
Outside Causes
1998 | 0.019825 | 0.00083128 | 0.00020913 | 0.00064829 | 0.00082082 | 0.00073195 | 6.2738e-05 | 4.1825e-05 | 0.00084174 | 0.011397 | 0.00019867 | 0.0031474 | 0.00089402
1999 | 0.034637 | 0.00025095 | 0.0009463 | 0.011533 | 0.00043917 | 0.00047054 | 0.00018299 | 0.0034924 | 0.00042871 | 0.0068698 | 0.00079991 | 0.0039891 | 0.0052334
Major Events
1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## WTU--System-SAIDI
CSW - West Texas Utilities
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 30.395 | 2.7088 | 0.89314 | 2.3925 | 1.686 | 3.4534 | 1.8655 | 6.369 | 5.1675 | 1.9898 | 1.3377 | 0.96084 | 1.5709
1999 | 25.8503 | 1.4539 | 0.41007 | 2.4012 | 4.1637 | 4.2818 | 5.2702 | 1.9539 | 1.9849 | 1.3167 | 1.1326 | 0.33063 | 1.1506
Scheduled
1998 | 0.85366 | 0.22151 | 0.22054 | 0.02474 | 0.029722 | 0.033539 | 0.060422 | 0.033256 | 0.026878 | 0.051728 | 0.094813 | 0.032007 | 0.024504
1999 | 3.4481 | 0.081079 | 0.22309 | 1.4032 | 0.52007 | 0.094296 | 0.067166 | 0.063339 | 0.80416 | 0.026878 | 0.057489 | 0.037915 | 0.069315
Outside Causes
1998 | 2.1069 | 0.17669 | 0.025576 | 0.11303 | 0.077675 | 0.039739 | 0.0036284 | 0.0017514 | 0.089909 | 1.3387 | 0.015413 | 0.10125 | 0.12352
1999 | 1.3706 | 0.010101 | 0.051722 | 0.09647 | 0.036116 | 0.031024 | 0.011607 | 0.10545 | 0.023705 | 0.4537 | 0.055272 | 0.09554 | 0.39987
Major Events
1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## WTU--Feeder-SAIFI
Distribution Feeders on Texas System (10 or more customers) |  |  |  | Total Number of Feeders
396
CSW - West Texas Utilities
1999 SAIFI Ranking | Substation Identification | Feeder Identification | # Of Customers | 1999 SAIFI Value
1 | SA GRAPE CREEK | 5365 | 132 | 3.3939
2 | HEDLEY | 5870 | 88 | 3.1477
3 | CONCHO 37.5 MVA 12KV | 1715 | 285 | 3.014
4 | SHAMROCK | 144 | 525 | 2.9505
5 | ABILENE PLANT SOUTH 12KV | 1565 | 284 | 2.4965
6 | ALPINE 12KV | 3160 | 1792 | 2.4342
7 | SA SOUTH 138/12KV | 2595 | 337 | 2.4125
8 | PRESIDIO | 6135 | 1017 | 2.2409
9 | SA EMERSON ST | 4630 | 371 | 2.2372
10 | RULE | 3396 | 525 | 2.1695
11 | SHELTON SOUTH 12 KV | 3045 | 470 | 2.1213
12 | CHILDRESS 69 SUB 12.5KV | 1800 | 449 | 2.098
13 | QUANAH | 100 | 52 | 2.0769
14 | STAMFORD | 4565 | 937 | 2.0566
15 | RIO PECOS 12KV | 513 | 40 | 2.05
16 | SHAMROCK | 1835 | 75 | 2.04
17 | WELLINGTON | 1765 | 856 | 2.0257
18 | MCELROY | 5165 | 164 | 1.8963
19 | CLYDE | 3630 | 840 | 1.6714
20 | OZONA 12.5 KV | 4185 | 1075 | 1.627
21 | CLYDE | 1755 | 955 | 1.6084
22 | ROTAN | 1860 | 706 | 1.4915
23 | NORTH ANGELO 12KV BUS | 3115 | 213 | 1.4883
24 | OZONA 12.5 KV | 3555 | 32 | 1.3125
25 | SA COKE ST | 4910 | 946 | 1.3097
26 | HASKELL 12KV | 3770 | 722 | 1.2964
27 | SA GRAPE CREEK | 4700 | 994 | 1.2757
28 | CISCO | 1690 | 1021 | 1.2723
29 | SA SOUTH 138/12KV | 4255 | 172 | 1.2674
30 | SA COKE ST | 3905 | 115 | 1.2522
31 | VERNON 12.5KV EAST | 4275 | 707 | 1.2489
32 | AB OVER STREET 12KV | 1635 | 357 | 1.2437
33 | CISCO | 1680 | 573 | 1.2356
34 | SPUDDER FLAT | 4180 | 65 | 1.2154
35 | RISING STAR | 5075 | 455 | 1.2
36 | SA LAKE DRIVE | 5865 | 1129 | 1.186
37 | HIGHLAND | 6375 | 188 | 1.1543
38 | CLARENDON | 4040 | 757 | 1.1493
39 | GRAYBACK | 3320 | 27 | 1.1481
40 | QUANAH | 1830 | 594 | 1.1094
41 | AB VOGEL ST. | 4650 | 1013 | 1.1037
42 | AB OIL MILL | 3900 | 651 | 1.0737
43 | SAND ROAD | 5290 | 753 | 1.0717
44 | SHELTON NORTH 12KV | 3145 | 930 | 1.071
45 | AB MCMURRY | 4360 | 1263 | 1.0562
46 | HASKELL 12KV | 3495 | 1220 | 1.05
47 | RULE | 3378 | 105 | 1.0381
48 | HEDLEY | 5845 | 322 | 1.0311
49 | MARFA | 1905 | 1034 | 1.0261
50 | ABILENE PLANT NORTH 12KV BUS | 1910 | 775 | 1.0206
51 | STAMFORD | 2815 | 729 | 1.0206
52 | CROWELL | 3490 | 52 | 1.0192
53 | MERKEL | 1890 | 465 | 1.0172
54 | SA LAKE DRIVE | 5880 | 1570 | 1.0159
55 | MATADOR 12.5KV | 3090 | 268 | 1.0149
56 | SHELTON SOUTH 12 KV | 3040 | 406 | 1.0049
57 | SPUDDER FLAT | 4175 | 60 | 1
58 | MARFA AIRPORT | 50100 | 18 | 1
59 | ROTAN | 1865 | 362 | 0.97514
60 | MUNDAY 12.5KV | 2015 | 56 | 0.96429
61 | MERTZON | 2905 | 209 | 0.96172
62 | MATADOR 12.5KV | 3030 | 545 | 0.92844
63 | FLOMOT | 4089 | 83 | 0.90361
64 | MCCAMEY 12..5KV | 2415 | 446 | 0.89013
65 | VERHALEN | 4465 | 22 | 0.86364
66 | AB CANYON ROCK | 5030 | 431 | 0.85151
67 | ROWENA | 4480 | 25 | 0.84
68 | DUNE FIELD (NO. CRANE) | 3885 | 52 | 0.80769
69 | TANKERSLY (CVEC) | 5260 | 688 | 0.79797
70 | AB VOGEL ST. | 4560 | 455 | 0.72088
71 | QUANAH | 3100 | 808 | 0.68193
72 | EOLA | 4950 | 235 | 0.68085
73 | WOODSON OIL FIELD | 30 | 40 | 0.675
74 | AB MAPLE ST | 5755 | 734 | 0.66349
75 | MORAN | 2108 | 202 | 0.60891
76 | CROSS PLAINS | 2920 | 541 | 0.57116
77 | SAND ROAD | 5195 | 646 | 0.55882
78 | NORTH ANGELO 12KV BUS | 3130 | 376 | 0.55319
79 | CROSS PLAINS | 2915 | 552 | 0.55254
80 | KNOX CITY | 3390 | 240 | 0.5375
81 | SA SOUTH (69/12.5KV) | 4795 | 207 | 0.52657
82 | BRADY | 5015 | 201 | 0.51244
83 | IRAAN | 2055 | 348 | 0.49425
84 | MARFA | 1900 | 566 | 0.48587
85 | SA JACKSON ST | 4685 | 2737 | 0.4852
86 | SAND ROAD | 5295 | 427 | 0.48478
87 | PECOS VALLEY | 4075 | 19 | 0.47368
88 | INDIAN MESA | 2695 | 15 | 0.46667
89 | AB MCMURRY | 3240 | 318 | 0.44025
90 | ALPINE 12KV | 3155 | 1803 | 0.4376
91 | KIRKLAND | 3545 | 39 | 0.4359
92 | SA WALNUT ST | 3910 | 486 | 0.4321
93 | SA SOUTHLND HILLS | 5055 | 563 | 0.42806
94 | SA SOUTH 138/12KV | 3990 | 318 | 0.42453
95 | AB MAPLE ST | 5750 | 103 | 0.41748
96 | AB HARTFORD ST | 3685 | 245 | 0.41633
97 | SA JACKSON ST | 4695 | 245 | 0.41224
98 | ROBERT LEE | 4125 | 684 | 0.40205
99 | SA AVENUE N | 1695 | 1187 | 0.38416
100 | SARAGOSA | 1590 | 16 | 0.375
101 | MATHIS FIELD | 5100 | 237 | 0.36709
102 | COLLEGE HILLS E.12.5KV | 4840 | 490 | 0.34898
103 | HAMLIN | 3270 | 1063 | 0.33396
104 | TEXON | 4345 | 150 | 0.33333
105 | VALENTINE | 5590 | 708 | 0.32486
106 | AB RAINEY CRK | 4220 | 132 | 0.31818
107 | CLYDE | 3635 | 1537 | 0.31165
108 | HIGHLAND | 6385 | 731 | 0.30917
109 | SA JACKSON ST | 4690 | 406 | 0.29803
110 | COLLEGE HILLS W.12.5KV | 6145 | 459 | 0.2963
111 | SA WALNUT ST | 3925 | 659 | 0.28376
112 | SA GRAPE CREEK | 5220 | 702 | 0.28205
113 | MCCAMEY 12..5KV | 2855 | 110 | 0.28182
114 | SA SOUTHLND HILLS | 5050 | 789 | 0.27757
115 | CHILDRESS 69 SUB 12.5KV | 1480 | 426 | 0.277
116 | AB WALNUT ST | 3110 | 607 | 0.27183
117 | POWELL FIELD (SWTEC) | 2528 | 26 | 0.26923
118 | SA WALNUT ST | 4635 | 1417 | 0.26535
119 | TWILIGHT TRAIL | 5855 | 605 | 0.26116
120 | AB COUNTRY CLUB | 4855 | 303 | 0.25743
121 | ABILENE PLANT NORTH 12KV BUS | 1575 | 298 | 0.25503
122 | SA AVENUE N | 1730 | 739 | 0.25169
123 | PUTNAM | 2129 | 223 | 0.25112
124 | PECOS VALLEY | 4080 | 57 | 0.24561
125 | MUNDAY | 6715 | 256 | 0.23047
126 | COLLEGE HILLS E.12.5KV | 4845 | 322 | 0.22981
127 | CROSS PLAINS | 1795 | 608 | 0.22862
128 | AB VOGEL ST. | 4410 | 328 | 0.22256
129 | HAMLIN | 3775 | 354 | 0.21751
130 | PLASTERCO(MWEC) | 2720 | 205 | 0.21463
131 | EDEN | 3195 | 513 | 0.21053
132 | FT. DAVIS | 4515 | 825 | 0.20606
133 | HIGHLAND | 6370 | 554 | 0.20217
134 | CHRISTOVAL #2 | 6620 | 441 | 0.19955
135 | TALPA ATL. | 5180 | 81 | 0.19753
136 | ROBY 12.5KV | 2276 | 352 | 0.19318
137 | THROCKMORTON | 3190 | 711 | 0.19128
138 | AB OVER STREET 12KV | 1840 | 827 | 0.19105
139 | ANSON 12KV BUS | 6630 | 419 | 0.19093
140 | GRAYBACK | 3315 | 100 | 0.19
141 | PAULANN | 6285 | 58 | 0.18966
142 | AB REBECCA LANE | 5550 | 651 | 0.1874
143 | WAGGONER | 5900 | 27 | 0.18519
144 | SA SOUTH (69/12.5KV) | 3995 | 551 | 0.1833
145 | CHERRY CREEK TAP | 5245 | 11 | 0.18182
146 | WINTERS | 3765 | 1046 | 0.18164
147 | TRENT | 4245 | 348 | 0.18103
148 | SA LAKE DRIVE | 6030 | 957 | 0.18077
149 | ASPR CONTINENTAL | 4800 | 28 | 0.17857
150 | AB RAINEY CRK | 4550 | 379 | 0.17678
151 | SARAGOSA | 1552 | 788 | 0.17513
152 | ABILENE PLANT NORTH 12KV BUS | 1570 | 280 | 0.175
153 | AB OIL MILL | 2780 | 455 | 0.17143
154 | AB MCMURRY | 3235 | 357 | 0.17087
155 | ANSON REA (SEC) | 5215 | 494 | 0.17004
156 | AB REBECCA LANE | 2710 | 303 | 0.16832
157 | MASTERSON FIELD | 2101 | 167 | 0.16766
158 | CHRISTOVAL #1 | 6615 | 802 | 0.16708
159 | AB HARTFORD ST | 3815 | 678 | 0.16667
160 | ROUNDTOP | 4490 | 54 | 0.16667
161 | AB VOGEL ST. | 4405 | 709 | 0.16643
162 | NORTH ANGELO 12KV BUS | 3120 | 1034 | 0.16634
163 | SA EMERSON ST | 4625 | 211 | 0.16588
164 | WEINERT | 6490 | 139 | 0.16547
165 | ESTELLINE | 3535 | 121 | 0.16529
166 | WINTERS | 2113 | 811 | 0.16523
167 | SHAMROCK | 148 | 1100 | 0.16455
168 | AB MCMURRY | 3245 | 886 | 0.16366
169 | AB EAST 12KV | 4820 | 479 | 0.15866
170 | HIGHLAND | 6380 | 2127 | 0.15515
171 | PAINT CREEK (Stamford Pump) | 3930 | 39 | 0.15385
172 | MUNDAY 12.5KV | 3365 | 450 | 0.14667
173 | SA JACKSON ST | 4260 | 693 | 0.14574
174 | MILES | 4670 | 474 | 0.14557
175 | EDITH HUMBLE | 6170 | 111 | 0.14414
176 | CLYDE | 1760 | 542 | 0.14391
177 | QUANAH | 3975 | 153 | 0.14379
178 | SWENSON | 136 | 35 | 0.14286
179 | RISING STAR | 5080 | 712 | 0.14045
180 | CONCHO | 1700 | 194 | 0.13918
181 | BEN FICKLIN | 6175 | 408 | 0.13725
182 | VERN CITY PLANT | 5840 | 67 | 0.13433
183 | ELM CREEK SOUTH 12KV BUS | 4745 | 725 | 0.13241
184 | ASPERMONT 12KV BUS | 3380 | 728 | 0.13049
185 | CEDAR GAP -TEC | 5445 | 108 | 0.12963
186 | MATHIS FIELD | 4790 | 31 | 0.12903
187 | WYLIE | 2675 | 891 | 0.12458
188 | AB CANYON ROCK | 5035 | 685 | 0.12263
189 | BALLINGER 12KV | 4375 | 1199 | 0.1226
190 | SA AVENUE N | 1975 | 436 | 0.11927
191 | ALBANY | 3640 | 312 | 0.11859
192 | MENARD 12.5KV | 3760 | 87 | 0.11494
193 | AB COUNTRY CLUB | 4730 | 201 | 0.11443
194 | KNOX CITY | 3300 | 632 | 0.11392
195 | AFTON | 2225 | 62 | 0.1129
196 | BIG LAKE 4KV BUS | 4665 | 231 | 0.11255
197 | PERKINS PROTHO | 5846 | 18 | 0.11111
198 | SA WALNUT ST | 3915 | 525 | 0.11048
199 | NORTH ANGELO 12KV BUS | 3125 | 1513 | 0.10773
200 | CLARENDON | 5005 | 764 | 0.10733
201 | AB EAST 12KV | 4825 | 558 | 0.10394
202 | THROCKMORTON | 2090 | 58 | 0.10345
203 | SA WALNUT ST | 3920 | 268 | 0.10075
204 | INDIAN MESA | 2690 | 70 | 0.1
205 | CONCHO | 1705 | 283 | 0.09894
206 | ROBERT LEE | 4120 | 286 | 0.097902
207 | BRONTE | 3560 | 124 | 0.096774
208 | ALBANY | 3655 | 669 | 0.092676
209 | JUNCTION | 4335 | 608 | 0.090461
210 | PADUCAH | 1930 | 557 | 0.089767
211 | OZONA 12.5 KV | 3810 | 807 | 0.085502
212 | BEN FICKLIN | 6180 | 1210 | 0.084298
213 | CHILDRESS 20TH STREET | 5720 | 124 | 0.080645
214 | AB MCMURRY | 4350 | 1145 | 0.080349
215 | AB MCMURRY | 4510 | 747 | 0.080321
216 | MENARD 12.5KV | 3755 | 885 | 0.080226
217 | SA JACKSON ST | 4250 | 214 | 0.079439
218 | MORAN | 2107 | 426 | 0.077465
219 | VERNON 12.5KV EAST | 5000 | 511 | 0.076321
220 | AB MCMURRY | 4355 | 1175 | 0.075745
221 | VERNON 12.5KV EAST | 1520 | 825 | 0.075152
222 | SHELTON NORTH 12KV | 3660 | 600 | 0.075
223 | COLLEGE HILLS E.12.5KV | 4835 | 295 | 0.074576
224 | HASKELL 12KV | 5240 | 203 | 0.073892
225 | CROWELL | 3980 | 761 | 0.070959
226 | SA AVENUE N | 1655 | 544 | 0.068015
227 | BALLINGER 12KV | 4370 | 860 | 0.067442
228 | AB ELMDALE | 4520 | 75 | 0.066667
229 | SA SOUTHLND HILLS | 5455 | 624 | 0.065705
230 | SA EMERSON ST | 4620 | 919 | 0.065288
231 | STERLING CITY 12.5KV | 1445 | 711 | 0.064698
232 | AB OVER STREET 12KV | 3140 | 583 | 0.063465
233 | SAND ROAD | 5655 | 737 | 0.061058
234 | HAWLEY | 4455 | 613 | 0.060359
235 | HUMBLE KEMPER | 1490 | 17 | 0.058824
236 | CISCO | 1675 | 901 | 0.058824
237 | RANKIN | 5735 | 17 | 0.058824
238 | ALBANY | 3540 | 580 | 0.058621
239 | WELLINGTON | 1770 | 234 | 0.055556
240 | MUNDAY 12.5KV | 2080 | 515 | 0.054369
241 | SPUR | 417 | 281 | 0.053381
242 | BIG LAKE 12KV BUS | 4655 | 1087 | 0.050598
243 | ALBANY | 2029 | 223 | 0.049327
244 | TUSCOLA | 3305 | 1076 | 0.049257
245 | SA JACKSON ST | 4265 | 1149 | 0.048738
246 | AB OVER STREET 12KV | 1645 | 504 | 0.047619
247 | FT. DAVIS | 3345 | 189 | 0.047619
248 | COLLEGE HILLS W.12.5KV | 5520 | 211 | 0.047393
249 | BAIRD | 5125 | 682 | 0.046921
250 | JAYTON 4.0KV | 6125 | 384 | 0.046875
251 | AB HARTFORD ST | 3690 | 171 | 0.046784
252 | BRADSHAW (CLIMAX) | 11301 | 43 | 0.046512
253 | PUTNAM | 2131 | 195 | 0.046154
254 | ABILENE DYESS 2 | 6335 | 608 | 0.044408
255 | ANSON 12KV BUS | 6635 | 589 | 0.044143
256 | BUSH KNOB | 5200 | 287 | 0.041812
257 | STAMFORD | 6255 | 503 | 0.04175
258 | VERN CITY PLANT | 5780 | 727 | 0.041265
259 | SHELTON SOUTH 12 KV | 4640 | 778 | 0.041131
260 | PRESIDIO | 4540 | 823 | 0.040097
261 | PADUCAH | 1935 | 424 | 0.037736
262 | MCCAMEY 12..5KV | 2420 | 133 | 0.037594
263 | SANTA ANNA 12KV | 3420 | 266 | 0.037594
264 | WYLIE | 2665 | 902 | 0.036585
265 | SHELTON NORTH 12KV | 3050 | 1272 | 0.036164
266 | VERNON 12.5KV WEST | 3340 | 388 | 0.036082
267 | STAMFORD | 2835 | 293 | 0.03413
268 | ABILENE DYESS 1 | 1775 | 300 | 0.033333
269 | TRENT | 2850 | 30 | 0.033333
270 | CAREY | 6115 | 122 | 0.032787
271 | CHILDRESS 20TH STREET | 5725 | 694 | 0.0317
272 | ELM CREEK NORTH 12KV BUS | 1810 | 1451 | 0.031013
273 | VERNON 12.5KV WEST | 1750 | 97 | 0.030928
274 | FT. DAVIS | 6570 | 134 | 0.029851
275 | MERKEL | 1895 | 968 | 0.028926
276 | TWILIGHT TRAIL | 3150 | 484 | 0.028926
277 | TUSCOLA | 3730 | 835 | 0.028743
278 | SPUR | 414 | 280 | 0.028571
279 | BENJAMIN BEPC | 5680 | 178 | 0.02809
280 | RIO PECOS 12KV | 3835 | 144 | 0.027778
281 | WYLIE | 6340 | 1284 | 0.027259
282 | MELVIN | 4955 | 148 | 0.027027
283 | WEST YATES | 5595 | 150 | 0.026667
284 | TURKEY | 2980 | 381 | 0.026247
285 | MEMPHIS | 3335 | 980 | 0.02551
286 | MEMPHIS | 11 | 168 | 0.02381
287 | PAULANN | 6280 | 678 | 0.023599
288 | MIDWAY LANE | 3440 | 86 | 0.023256
289 | SUN VALLEY | 4300 | 93 | 0.021505
290 | ELM CREEK SOUTH 12KV BUS | 4780 | 586 | 0.020478
291 | WELLINGTON | 3700 | 644 | 0.020186
292 | AILEEN | 6435 | 496 | 0.020161
293 | TWILIGHT TRAIL | 4285 | 1401 | 0.019986
294 | ONYX REA | 3255 | 103 | 0.019417
295 | TURKEY | 3825 | 361 | 0.019391
296 | BARNHART | 3725 | 111 | 0.018018
297 | ELM CREEK NORTH 12KV BUS | 1815 | 505 | 0.017822
298 | RANKIN | 1542 | 284 | 0.017606
299 | SPUR | 5170 | 1155 | 0.015584
300 | ROCHESTER | 3290 | 65 | 0.015385
301 | AB RAINEY CRK | 4270 | 790 | 0.01519
302 | BRONTE | 4160 | 369 | 0.01355
303 | AB WALNUT ST | 3785 | 1847 | 0.013535
304 | AB COUNTRY CLUB | 4725 | 151 | 0.013245
305 | MENARD 4.0KV | 3750 | 400 | 0.0125
306 | ROBY 12.5KV | 3795 | 89 | 0.011236
307 | JUNCTION | 4340 | 892 | 0.011211
308 | ABILENE PLANT SOUTH 12KV | 1915 | 93 | 0.010753
309 | PAINT ROCK | 5235 | 186 | 0.010753
310 | ROCHESTER | 3295 | 283 | 0.010601
311 | AB HARTFORD ST | 3820 | 1435 | 0.010453
312 | CISCO | 1685 | 193 | 0.010363
313 | CHILLICOTHE | 4530 | 583 | 0.010292
314 | ELM CREEK SOUTH 12KV BUS | 4775 | 597 | 0.01005
315 | BRONTE | 3590 | 100 | 0.01
316 | ONYX REA | 3260 | 103 | 0.0097087
317 | AILEEN | 4605 | 416 | 0.0096154
318 | SHELTON NORTH 12KV | 3060 | 1712 | 0.0093458
319 | MCCAMEY 4 KV | 3670 | 458 | 0.0087336
320 | SHEFFIELD (SWTEC) | 71300 | 248 | 0.0080645
321 | BALLINGER 4KV | 4395 | 389 | 0.0077121
322 | ALPINE 12KV | 3875 | 520 | 0.0076923
323 | SA EMERSON ST | 4860 | 394 | 0.0076142
324 | SA SOUTHLND HILLS | 5860 | 142 | 0.0070423
325 | AB REBECCA LANE | 5555 | 1953 | 0.0066564
326 | ABILENE PLANT SOUTH 12KV | 1735 | 151 | 0.0066225
327 | ELM CREEK NORTH 12KV BUS | 5045 | 606 | 0.0066007
328 | MERTZON (SWEC) | 1530 | 632 | 0.0063291
329 | SONORA 12.5KV | 2045 | 797 | 0.0062735
330 | RANKIN | 1543 | 320 | 0.00625
331 | AB COUNTRY CLUB | 4735 | 504 | 0.0059524
332 | SHELTON SOUTH 12 KV | 3435 | 338 | 0.0059172
333 | ROWENA | 7041 | 193 | 0.0051813
334 | PAULANN | 6310 | 580 | 0.0051724
335 | MCCAMEY 12..5KV | 2830 | 974 | 0.0051335
336 | BEN FICKLIN | 6185 | 586 | 0.0051195
337 | SA COKE ST | 4915 | 197 | 0.0050761
338 | IRAAN | 2050 | 430 | 0.0046512
339 | SANTA ANNA 12KV | 3415 | 479 | 0.0041754
340 | ABILENE PLANT SOUTH 12KV | 3175 | 296 | 0.0033784
341 | ELM CREEK SOUTH 12KV BUS | 1825 | 774 | 0.002584
342 | VERN CITY PLANT | 5770 | 388 | 0.0025773
343 | AB EAST 12KV | 4830 | 793 | 0.0025221
344 | BAIRD | 5120 | 431 | 0.0023202
345 | CHILDRESS 69 SUB 12.5KV | 4865 | 893 | 0.0022396
346 | FT.CHADBOURNE | 6520 | 706 | 0.0014164
347 | AB WALNUT ST | 3445 | 793 | 0.001261
348 | VERNON 12.5KV WEST | 1525 | 10 | 0
349 | ASPR CONTINENTAL | 3830 | 13 | 0
350 | KNOX CITY | 3985 | 17 | 0
351 | HAMLIN SHELL | 152 | 22 | 0
352 | HAMLIN SHELL | 6330 | 23 | 0
353 | HAROLD | 1495 | 27 | 0
354 | HAROLD | 3055 | 27 | 0
355 | CORINTH | 2590 | 28 | 0
356 | BRONTE AMBASSADOR | 6650 | 29 | 0
357 | GIRARD | 1547 | 34 | 0
358 | CEDAR GAP -TEC | 4115 | 40 | 0
359 | AB CANYON ROCK | 5025 | 40 | 0
360 | TRUSCOTT | 3845 | 43 | 0
361 | IRAAN | 4305 | 43 | 0
362 | VERN CITY PLANT | 5830 | 49 | 0
363 | PEACOCK | 43 | 50 | 0
364 | SHAFTER | 5110 | 50 | 0
365 | AFTON | 2355 | 52 | 0
366 | FREISS RANCH | 4870 | 56 | 0
367 | ELDORADO | 2880 | 61 | 0
368 | VERN CITY PLANT | 5835 | 67 | 0
369 | ASPERMONT 4KV BUS | 312 | 85 | 0
370 | VALERA HUMBLE | 7015 | 87 | 0
371 | ABILENE PLANT SOUTH 12KV | 1580 | 88 | 0
372 | PADUCAH REA-GBEC | 13 | 99 | 0
373 | MEMPHIS | 12 | 119 | 0
374 | FT.CHADBOURNE | 6515 | 125 | 0
375 | ABILENE PLANT NORTH 12KV BUS | 1740 | 184 | 0
376 | COLLEGE HILLS W.12.5KV | 5515 | 184 | 0
377 | VERN CITY PLANT | 5785 | 194 | 0
378 | BIG LAKE 12KV BUS | 4660 | 231 | 0
379 | AB RAINEY CRK | 4225 | 244 | 0
380 | EDEN | 1780 | 278 | 0
381 | AFTON | 2310 | 288 | 0
382 | AB OIL MILL | 3895 | 308 | 0
383 | CONCHO 37.5 MVA 12KV | 1725 | 345 | 0
384 | MEMPHIS | 3025 | 385 | 0
385 | AILEEN | 4600 | 545 | 0
386 | SONORA 12.5KV | 4805 | 559 | 0
387 | QUANAH | 3530 | 584 | 0
388 | CHILLICOTHE | 4525 | 621 | 0
389 | CONCHO 37.5 MVA 12KV | 1405 | 662 | 0
390 | CONCHO 12.5 MVA 12KV | 1710 | 701 | 0
391 | CHILDRESS 69 SUB 12.5KV | 2800 | 713 | 0
392 | SONORA 12.5KV | 4810 | 826 | 0
393 | SA SOUTH (69/12.5KV) | 3500 | 888 | 0
394 | ELDORADO | 1845 | 1066 | 0
395 | AB EAST 12KV | 5760 | 1091 | 0
396 | TWILIGHT TRAIL | 4290 | 1747 | 0

## WTU--Feeder-SAIDI
Distribution Feeders on Texas System (10 or more customers) |  |  |  | Total Number of Feeders
396
CSW - West Texas Utilities
1999 SAIDI Ranking | Substation Identification | Feeder Identification | # Of Customers | 1999 SAIDI Value
1 | HEDLEY | 5870 | 88 | 868.2386
2 | ROTAN | 1865 | 362 | 459.8398
3 | SA GRAPE CREEK | 5365 | 132 | 371.8864
4 | ROTAN | 1860 | 706 | 347.6048
5 | SA SOUTH 138/12KV | 2595 | 337 | 340.7745
6 | OZONA 12.5 KV | 3555 | 32 | 338.2812
7 | NORTH ANGELO 12KV BUS | 3115 | 213 | 304.6854
8 | SA SOUTH 138/12KV | 4255 | 172 | 224.9186
9 | MCELROY | 5165 | 164 | 209.2439
10 | RIO PECOS 12KV | 513 | 40 | 208.625
11 | SA WALNUT ST | 3910 | 486 | 199.5679
12 | RULE | 3396 | 525 | 183.8171
13 | SA LAKE DRIVE | 5865 | 1129 | 182.1107
14 | DUNE FIELD (NO. CRANE) | 3885 | 52 | 170.2308
15 | MCCAMEY 12..5KV | 2415 | 446 | 158.7623
16 | OZONA 12.5 KV | 4185 | 1075 | 157.8865
17 | SHAMROCK | 1835 | 75 | 149
18 | SA COKE ST | 3905 | 115 | 147.0696
19 | SA COKE ST | 4910 | 946 | 145.8446
20 | GRAYBACK | 3320 | 27 | 127.7778
21 | ALPINE 12KV | 3160 | 1792 | 124.005
22 | NORTH ANGELO 12KV BUS | 3130 | 376 | 113.0053
23 | FLOMOT | 4089 | 83 | 108.7952
24 | PRESIDIO | 6135 | 1017 | 103.2468
25 | CISCO | 1690 | 1021 | 101.1548
26 | WELLINGTON | 1765 | 856 | 99.1414
27 | SA LAKE DRIVE | 5880 | 1570 | 96.4268
28 | MERTZON | 2905 | 209 | 92.2823
29 | CHILDRESS 69 SUB 12.5KV | 1800 | 449 | 88.196
30 | SA SOUTHLND HILLS | 5055 | 563 | 78.8774
31 | TANKERSLY (CVEC) | 5260 | 688 | 76.9317
32 | RULE | 3378 | 105 | 75.1619
33 | BRADY | 5015 | 201 | 73.5821
34 | HASKELL 12KV | 3770 | 722 | 72.8906
35 | SPUDDER FLAT | 4175 | 60 | 71.9667
36 | ROWENA | 4480 | 25 | 70.8
37 | PECOS VALLEY | 4075 | 19 | 70.5263
38 | CLYDE | 3630 | 840 | 69.9917
39 | CROSS PLAINS | 2915 | 552 | 66.3913
40 | RISING STAR | 5075 | 455 | 63.7275
41 | VERHALEN | 4465 | 22 | 63.5
42 | ABILENE PLANT SOUTH 12KV | 1565 | 284 | 63.3732
43 | INDIAN MESA | 2695 | 15 | 60.0667
44 | MERKEL | 1890 | 465 | 59.8452
45 | TEXON | 4345 | 150 | 59.2867
46 | CLARENDON | 4040 | 757 | 57.317
47 | SPUDDER FLAT | 4180 | 65 | 55.9385
48 | AB VOGEL ST. | 4560 | 455 | 53.0637
49 | CONCHO 37.5 MVA 12KV | 1715 | 285 | 52.8246
50 | SA EMERSON ST | 4630 | 371 | 50.3396
51 | SAND ROAD | 5290 | 753 | 49.7477
52 | HASKELL 12KV | 3495 | 1220 | 49.441
53 | CROSS PLAINS | 2920 | 541 | 48.7652
54 | MATHIS FIELD | 5100 | 237 | 48.6582
55 | MORAN | 2108 | 202 | 48.396
56 | VALENTINE | 5590 | 708 | 48.3277
57 | SHAMROCK | 144 | 525 | 48.2095
58 | AB VOGEL ST. | 4650 | 1013 | 47.4176
59 | MATADOR 12.5KV | 3090 | 268 | 46.3806
60 | SHELTON SOUTH 12 KV | 3045 | 470 | 46.2681
61 | MARFA AIRPORT | 50100 | 18 | 45
62 | AB CANYON ROCK | 5030 | 431 | 44.3643
63 | STAMFORD | 4565 | 937 | 43.6841
64 | ROBERT LEE | 4125 | 684 | 43.2266
65 | COLLEGE HILLS W.12.5KV | 6145 | 459 | 42.0414
66 | ALPINE 12KV | 3155 | 1803 | 41.2008
67 | EOLA | 4950 | 235 | 39.8213
68 | SAND ROAD | 5295 | 427 | 39.8126
69 | ABILENE PLANT NORTH 12KV BUS | 1910 | 775 | 39.7897
70 | CLYDE | 1755 | 955 | 39.3885
71 | AB HARTFORD ST | 3685 | 245 | 39.0163
72 | WOODSON OIL FIELD | 30 | 40 | 38.85
73 | MCCAMEY 12..5KV | 2855 | 110 | 38.3091
74 | CROWELL | 3490 | 52 | 37.8846
75 | SHELTON NORTH 12KV | 3145 | 930 | 37.5978
76 | MATADOR 12.5KV | 3030 | 545 | 36.2092
77 | SA JACKSON ST | 4685 | 2737 | 35.5451
78 | BEN FICKLIN | 6175 | 408 | 34.0466
79 | SWENSON | 136 | 35 | 33.7143
80 | AB OVER STREET 12KV | 1635 | 357 | 32.4258
81 | KIRKLAND | 3545 | 39 | 32.3077
82 | QUANAH | 100 | 52 | 32.1154
83 | CISCO | 1680 | 573 | 31.4154
84 | MUNDAY 12.5KV | 2015 | 56 | 31.3393
85 | SHELTON SOUTH 12 KV | 3040 | 406 | 31.2956
86 | VERNON 12.5KV EAST | 4275 | 707 | 31.2504
87 | SA GRAPE CREEK | 5220 | 702 | 31.0427
88 | SA JACKSON ST | 4695 | 245 | 30.6163
89 | SA EMERSON ST | 4625 | 211 | 29.09
90 | SARAGOSA | 1590 | 16 | 29.0625
91 | HIGHLAND | 6375 | 188 | 28.5638
92 | AB REBECCA LANE | 5550 | 651 | 27.7788
93 | IRAAN | 2055 | 348 | 27.4828
94 | AB WALNUT ST | 3110 | 607 | 26.8353
95 | SA AVENUE N | 1695 | 1187 | 26.0725
96 | POWELL FIELD (SWTEC) | 2528 | 26 | 25.6154
97 | TRENT | 4245 | 348 | 25.3276
98 | SA AVENUE N | 1730 | 739 | 24.8417
99 | HIGHLAND | 6385 | 731 | 24.6977
100 | EDITH HUMBLE | 6170 | 111 | 24.4595
101 | HEDLEY | 5845 | 322 | 24.0217
102 | QUANAH | 1830 | 594 | 24.0067
103 | EDEN | 3195 | 513 | 23.4016
104 | PECOS VALLEY | 4080 | 57 | 23.3333
105 | MASTERSON FIELD | 2101 | 167 | 23.2874
106 | MARFA | 1905 | 1034 | 22.852
107 | AB MAPLE ST | 5750 | 103 | 22.6505
108 | STAMFORD | 2815 | 729 | 22.6118
109 | SA JACKSON ST | 4690 | 406 | 21.8424
110 | COLLEGE HILLS E.12.5KV | 4845 | 322 | 21.7236
111 | AB MCMURRY | 3240 | 318 | 21.566
112 | SA SOUTH (69/12.5KV) | 4795 | 207 | 21.5121
113 | BIG LAKE 4KV BUS | 4665 | 231 | 20.5368
114 | HIGHLAND | 6370 | 554 | 20.1877
115 | TWILIGHT TRAIL | 5855 | 605 | 20.1851
116 | AB MAPLE ST | 5755 | 734 | 20.015
117 | SA SOUTHLND HILLS | 5050 | 789 | 19.9049
118 | AB OIL MILL | 3900 | 651 | 19.8418
119 | CONCHO | 1700 | 194 | 19.6134
120 | COLLEGE HILLS E.12.5KV | 4840 | 490 | 19.0184
121 | ANSON 12KV BUS | 6630 | 419 | 18.7876
122 | SA GRAPE CREEK | 4700 | 994 | 18.6117
123 | PUTNAM | 2129 | 223 | 18.278
124 | WINTERS | 3765 | 1046 | 18.0793
125 | GRAYBACK | 3315 | 100 | 17.45
126 | PLASTERCO(MWEC) | 2720 | 205 | 17.2927
127 | SA WALNUT ST | 4635 | 1417 | 17.2611
128 | WAGGONER | 5900 | 27 | 16.6667
129 | ESTELLINE | 3535 | 121 | 16.3223
130 | WYLIE | 2675 | 891 | 16.2065
131 | AB MCMURRY | 4360 | 1263 | 15.692
132 | AB RAINEY CRK | 4550 | 379 | 15.591
133 | AFTON | 2225 | 62 | 15.2419
134 | AB RAINEY CRK | 4220 | 132 | 15.2273
135 | PAULANN | 6285 | 58 | 14.8276
136 | HASKELL 12KV | 5240 | 203 | 14.8128
137 | CHERRY CREEK TAP | 5245 | 11 | 14.4545
138 | SA SOUTH 138/12KV | 3990 | 318 | 14.3805
139 | MARFA | 1900 | 566 | 14.0194
140 | SA WALNUT ST | 3925 | 659 | 13.9514
141 | ABILENE PLANT NORTH 12KV BUS | 1575 | 298 | 13.6107
142 | MATHIS FIELD | 4790 | 31 | 13.1935
143 | HAMLIN | 3270 | 1063 | 12.9135
144 | SA AVENUE N | 1975 | 436 | 12.7431
145 | ROBY 12.5KV | 2276 | 352 | 12.3778
146 | CHRISTOVAL #2 | 6620 | 441 | 12.3673
147 | VERN CITY PLANT | 5840 | 67 | 12.2388
148 | CROWELL | 3980 | 761 | 12.2208
149 | WINTERS | 2113 | 811 | 12.2022
150 | AB CANYON ROCK | 5035 | 685 | 11.9971
151 | KNOX CITY | 3390 | 240 | 11.9583
152 | SA WALNUT ST | 3915 | 525 | 11.9486
153 | AB MCMURRY | 3245 | 886 | 11.8837
154 | CLYDE | 3635 | 1537 | 11.6428
155 | CROSS PLAINS | 1795 | 608 | 11.5609
156 | MUNDAY | 6715 | 256 | 11.5078
157 | SARAGOSA | 1552 | 788 | 11.4099
158 | CLYDE | 1760 | 542 | 11.4004
159 | PAINT CREEK (Stamford Pump) | 3930 | 39 | 11.0256
160 | RISING STAR | 5080 | 712 | 10.9803
161 | AB OIL MILL | 2780 | 455 | 10.9011
162 | CHRISTOVAL #1 | 6615 | 802 | 10.8791
163 | HAMLIN | 3775 | 354 | 10.5932
164 | MENARD 12.5KV | 3760 | 87 | 10.5747
165 | AB COUNTRY CLUB | 4855 | 303 | 10.3234
166 | AB OVER STREET 12KV | 1840 | 827 | 10.3035
167 | INDIAN MESA | 2690 | 70 | 10.2143
168 | AB MCMURRY | 3235 | 357 | 10.0448
169 | ROUNDTOP | 4490 | 54 | 10
170 | ASPERMONT 12KV BUS | 3380 | 728 | 9.9313
171 | AB EAST 12KV | 4820 | 479 | 9.8873
172 | AB VOGEL ST. | 4410 | 328 | 9.8171
173 | WEINERT | 6490 | 139 | 9.7554
174 | MENARD 12.5KV | 3755 | 885 | 9.2226
175 | BEN FICKLIN | 6180 | 1210 | 8.9678
176 | FT. DAVIS | 4515 | 825 | 8.6509
177 | CHILDRESS 69 SUB 12.5KV | 1480 | 426 | 8.27
178 | SA SOUTH (69/12.5KV) | 3995 | 551 | 8.2686
179 | MILES | 4670 | 474 | 8.2068
180 | TALPA ATL. | 5180 | 81 | 8.1481
181 | ROBERT LEE | 4120 | 286 | 7.9301
182 | SA LAKE DRIVE | 6030 | 957 | 7.6876
183 | AB HARTFORD ST | 3815 | 678 | 7.6755
184 | SA WALNUT ST | 3920 | 268 | 7.5187
185 | QUANAH | 3100 | 808 | 7.4691
186 | NORTH ANGELO 12KV BUS | 3120 | 1034 | 7.4449
187 | SA EMERSON ST | 4620 | 919 | 7.2437
188 | AB ELMDALE | 4520 | 75 | 7.1733
189 | ASPR CONTINENTAL | 4800 | 28 | 7.1429
190 | ALBANY | 3640 | 312 | 7.1282
191 | CAREY | 6115 | 122 | 6.8852
192 | ELM CREEK SOUTH 12KV BUS | 4745 | 725 | 6.5959
193 | ABILENE DYESS 2 | 6335 | 608 | 6.5822
194 | AB COUNTRY CLUB | 4730 | 201 | 6.4776
195 | SA JACKSON ST | 4260 | 693 | 6.4661
196 | THROCKMORTON | 3190 | 711 | 6.4487
197 | CEDAR GAP -TEC | 5445 | 108 | 6.3981
198 | MORAN | 2107 | 426 | 6.3897
199 | SAND ROAD | 5195 | 646 | 6.339
200 | MEMPHIS | 3335 | 980 | 6.1224
201 | MUNDAY 12.5KV | 3365 | 450 | 6.0733
202 | SA SOUTHLND HILLS | 5455 | 624 | 6.0433
203 | STERLING CITY 12.5KV | 1445 | 711 | 5.8692
204 | PERKINS PROTHO | 5846 | 18 | 5.8333
205 | NORTH ANGELO 12KV BUS | 3125 | 1513 | 5.7938
206 | KNOX CITY | 3300 | 632 | 5.7737
207 | AB VOGEL ST. | 4405 | 709 | 5.6714
208 | TUSCOLA | 3305 | 1076 | 5.5158
209 | HUMBLE KEMPER | 1490 | 17 | 5.2941
210 | OZONA 12.5 KV | 3810 | 807 | 5.1611
211 | COLLEGE HILLS E.12.5KV | 4835 | 295 | 5.0441
212 | STAMFORD | 6255 | 503 | 5.008
213 | AB REBECCA LANE | 2710 | 303 | 4.934
214 | AB MCMURRY | 4510 | 747 | 4.8728
215 | PADUCAH | 1930 | 557 | 4.8474
216 | QUANAH | 3975 | 153 | 4.8366
217 | AB EAST 12KV | 4825 | 558 | 4.8118
218 | ABILENE PLANT NORTH 12KV BUS | 1570 | 280 | 4.7786
219 | CLARENDON | 5005 | 764 | 4.6558
220 | SA JACKSON ST | 4250 | 214 | 4.6308
221 | BAIRD | 5125 | 682 | 4.4194
222 | VERNON 12.5KV EAST | 5000 | 511 | 4.3014
223 | PADUCAH | 1935 | 424 | 4.2453
224 | SHELTON NORTH 12KV | 3660 | 600 | 4.235
225 | AB OVER STREET 12KV | 1645 | 504 | 4.1984
226 | BALLINGER 12KV | 4375 | 1199 | 4.1418
227 | SHAMROCK | 148 | 1100 | 4.0909
228 | HAWLEY | 4455 | 613 | 3.9592
229 | BRONTE | 3560 | 124 | 3.871
230 | AB MCMURRY | 4355 | 1175 | 3.8604
231 | TURKEY | 2980 | 381 | 3.8583
232 | ANSON REA (SEC) | 5215 | 494 | 3.7753
233 | SA AVENUE N | 1655 | 544 | 3.6691
234 | WELLINGTON | 1770 | 234 | 3.5897
235 | FT. DAVIS | 6570 | 134 | 3.5821
236 | BIG LAKE 12KV BUS | 4655 | 1087 | 3.5501
237 | AB HARTFORD ST | 3690 | 171 | 3.3977
238 | CONCHO | 1705 | 283 | 3.3498
239 | BARNHART | 3725 | 111 | 3.2432
240 | VERNON 12.5KV WEST | 3340 | 388 | 3.2216
241 | VERNON 12.5KV EAST | 1520 | 825 | 3.2085
242 | TUSCOLA | 3730 | 835 | 3.1641
243 | SPUR | 417 | 281 | 3.1495
244 | ALBANY | 2029 | 223 | 3.0987
245 | FT. DAVIS | 3345 | 189 | 3.0794
246 | PAULANN | 6280 | 678 | 3.0324
247 | VERN CITY PLANT | 5780 | 727 | 3.0055
248 | SHELTON SOUTH 12 KV | 4640 | 778 | 2.8753
249 | ALBANY | 3655 | 669 | 2.7937
250 | AB MCMURRY | 4350 | 1145 | 2.7747
251 | ONYX REA | 3255 | 103 | 2.7282
252 | JAYTON 4.0KV | 6125 | 384 | 2.6693
253 | AB OVER STREET 12KV | 3140 | 583 | 2.669
254 | COLLEGE HILLS W.12.5KV | 5520 | 211 | 2.6256
255 | SA JACKSON ST | 4265 | 1149 | 2.624
256 | PUTNAM | 2131 | 195 | 2.6051
257 | CISCO | 1675 | 901 | 2.4761
258 | CHILDRESS 20TH STREET | 5720 | 124 | 2.4677
259 | JUNCTION | 4335 | 608 | 2.4539
260 | HIGHLAND | 6380 | 2127 | 2.4495
261 | BRADSHAW (CLIMAX) | 11301 | 43 | 2.3953
262 | BENJAMIN BEPC | 5680 | 178 | 2.382
263 | WYLIE | 2665 | 902 | 2.1353
264 | SAND ROAD | 5655 | 737 | 2.0353
265 | MELVIN | 4955 | 148 | 2.027
266 | TRENT | 2850 | 30 | 2
267 | WYLIE | 6340 | 1284 | 1.9198
268 | BALLINGER 12KV | 4370 | 860 | 1.85
269 | MERKEL | 1895 | 968 | 1.8347
270 | ALBANY | 3540 | 580 | 1.7448
271 | THROCKMORTON | 2090 | 58 | 1.7414
272 | MUNDAY 12.5KV | 2080 | 515 | 1.732
273 | RANKIN | 5735 | 17 | 1.7059
274 | BUSH KNOB | 5200 | 287 | 1.6829
275 | ELM CREEK NORTH 12KV BUS | 1810 | 1451 | 1.6802
276 | SUN VALLEY | 4300 | 93 | 1.6344
277 | VERNON 12.5KV WEST | 1750 | 97 | 1.6082
278 | RANKIN | 1542 | 284 | 1.5282
279 | ELM CREEK NORTH 12KV BUS | 1815 | 505 | 1.4792
280 | MIDWAY LANE | 3440 | 86 | 1.4535
281 | MCCAMEY 12..5KV | 2420 | 133 | 1.4286
282 | AB WALNUT ST | 3785 | 1847 | 1.4191
283 | SHELTON NORTH 12KV | 3050 | 1272 | 1.3931
284 | ANSON 12KV BUS | 6635 | 589 | 1.3667
285 | TWILIGHT TRAIL | 3150 | 484 | 1.3636
286 | PAINT ROCK | 5235 | 186 | 1.2634
287 | ABILENE PLANT SOUTH 12KV | 1915 | 93 | 1.2366
288 | STAMFORD | 2835 | 293 | 1.1672
289 | RIO PECOS 12KV | 3835 | 144 | 1.0903
290 | ELM CREEK SOUTH 12KV BUS | 4780 | 586 | 1.0717
291 | WEST YATES | 5595 | 150 | 1.0667
292 | CHILDRESS 20TH STREET | 5725 | 694 | 1.0634
293 | WELLINGTON | 3700 | 644 | 1.0481
294 | ELM CREEK SOUTH 12KV BUS | 4775 | 597 | 1.0285
295 | TWILIGHT TRAIL | 4285 | 1401 | 1.01
296 | AB RAINEY CRK | 4270 | 790 | 0.99747
297 | AILEEN | 4605 | 416 | 0.96394
298 | AB REBECCA LANE | 5555 | 1953 | 0.88274
299 | PRESIDIO | 4540 | 823 | 0.86148
300 | BRONTE | 4160 | 369 | 0.81301
301 | AILEEN | 6435 | 496 | 0.77823
302 | ROBY 12.5KV | 3795 | 89 | 0.76404
303 | SPUR | 5170 | 1155 | 0.74892
304 | SHELTON NORTH 12KV | 3060 | 1712 | 0.7354
305 | ABILENE DYESS 1 | 1775 | 300 | 0.61667
306 | SHEFFIELD (SWTEC) | 71300 | 248 | 0.60484
307 | MEMPHIS | 11 | 168 | 0.59524
308 | SANTA ANNA 12KV | 3420 | 266 | 0.56391
309 | AB COUNTRY CLUB | 4725 | 151 | 0.55629
310 | ELM CREEK NORTH 12KV BUS | 5045 | 606 | 0.5198
311 | SPUR | 414 | 280 | 0.46429
312 | MERTZON (SWEC) | 1530 | 632 | 0.45253
313 | TURKEY | 3825 | 361 | 0.44598
314 | MCCAMEY 4 KV | 3670 | 458 | 0.44105
315 | ONYX REA | 3260 | 103 | 0.43689
316 | ROCHESTER | 3290 | 65 | 0.43077
317 | IRAAN | 2050 | 430 | 0.4186
318 | ABILENE PLANT SOUTH 12KV | 1735 | 151 | 0.4106
319 | AB WALNUT ST | 3445 | 793 | 0.40984
320 | AB HARTFORD ST | 3820 | 1435 | 0.40557
321 | BRONTE | 3590 | 100 | 0.4
322 | MCCAMEY 12..5KV | 2830 | 974 | 0.39117
323 | JUNCTION | 4340 | 892 | 0.36099
324 | ALPINE 12KV | 3875 | 520 | 0.34615
325 | PAULANN | 6310 | 580 | 0.3431
326 | SONORA 12.5KV | 2045 | 797 | 0.33877
327 | RANKIN | 1543 | 320 | 0.3375
328 | ROCHESTER | 3295 | 283 | 0.33569
329 | AB COUNTRY CLUB | 4735 | 504 | 0.32738
330 | SA EMERSON ST | 4860 | 394 | 0.32487
331 | SA SOUTHLND HILLS | 5860 | 142 | 0.3169
332 | CISCO | 1685 | 193 | 0.28497
333 | SHELTON SOUTH 12 KV | 3435 | 338 | 0.27515
334 | SA COKE ST | 4915 | 197 | 0.26904
335 | MENARD 4.0KV | 3750 | 400 | 0.25
336 | CHILLICOTHE | 4530 | 583 | 0.21441
337 | BEN FICKLIN | 6185 | 586 | 0.2099
338 | ELM CREEK SOUTH 12KV BUS | 1825 | 774 | 0.1938
339 | ROWENA | 7041 | 193 | 0.18135
340 | BALLINGER 4KV | 4395 | 389 | 0.1671
341 | SANTA ANNA 12KV | 3415 | 479 | 0.16701
342 | ABILENE PLANT SOUTH 12KV | 3175 | 296 | 0.16216
343 | AB EAST 12KV | 4830 | 793 | 0.14502
344 | BAIRD | 5120 | 431 | 0.13921
345 | FT.CHADBOURNE | 6520 | 706 | 0.084986
346 | CHILDRESS 69 SUB 12.5KV | 4865 | 893 | 0.057111
347 | VERN CITY PLANT | 5770 | 388 | 0.025773
348 | VERNON 12.5KV WEST | 1525 | 10 | 0
349 | ASPR CONTINENTAL | 3830 | 13 | 0
350 | KNOX CITY | 3985 | 17 | 0
351 | HAMLIN SHELL | 152 | 22 | 0
352 | HAMLIN SHELL | 6330 | 23 | 0
353 | HAROLD | 3055 | 27 | 0
354 | HAROLD | 1495 | 27 | 0
355 | CORINTH | 2590 | 28 | 0
356 | BRONTE AMBASSADOR | 6650 | 29 | 0
357 | GIRARD | 1547 | 34 | 0
358 | AB CANYON ROCK | 5025 | 40 | 0
359 | CEDAR GAP -TEC | 4115 | 40 | 0
360 | TRUSCOTT | 3845 | 43 | 0
361 | IRAAN | 4305 | 43 | 0
362 | VERN CITY PLANT | 5830 | 49 | 0
363 | PEACOCK | 43 | 50 | 0
364 | SHAFTER | 5110 | 50 | 0
365 | AFTON | 2355 | 52 | 0
366 | FREISS RANCH | 4870 | 56 | 0
367 | ELDORADO | 2880 | 61 | 0
368 | VERN CITY PLANT | 5835 | 67 | 0
369 | ASPERMONT 4KV BUS | 312 | 85 | 0
370 | VALERA HUMBLE | 7015 | 87 | 0
371 | ABILENE PLANT SOUTH 12KV | 1580 | 88 | 0
372 | PADUCAH REA-GBEC | 13 | 99 | 0
373 | MEMPHIS | 12 | 119 | 0
374 | FT.CHADBOURNE | 6515 | 125 | 0
375 | ABILENE PLANT NORTH 12KV BUS | 1740 | 184 | 0
376 | COLLEGE HILLS W.12.5KV | 5515 | 184 | 0
377 | VERN CITY PLANT | 5785 | 194 | 0
378 | BIG LAKE 12KV BUS | 4660 | 231 | 0
379 | AB RAINEY CRK | 4225 | 244 | 0
380 | EDEN | 1780 | 278 | 0
381 | AFTON | 2310 | 288 | 0
382 | AB OIL MILL | 3895 | 308 | 0
383 | CONCHO 37.5 MVA 12KV | 1725 | 345 | 0
384 | MEMPHIS | 3025 | 385 | 0
385 | AILEEN | 4600 | 545 | 0
386 | SONORA 12.5KV | 4805 | 559 | 0
387 | QUANAH | 3530 | 584 | 0
388 | CHILLICOTHE | 4525 | 621 | 0
389 | CONCHO 37.5 MVA 12KV | 1405 | 662 | 0
390 | CONCHO 12.5 MVA 12KV | 1710 | 701 | 0
391 | CHILDRESS 69 SUB 12.5KV | 2800 | 713 | 0
392 | SONORA 12.5KV | 4810 | 826 | 0
393 | SA SOUTH (69/12.5KV) | 3500 | 888 | 0
394 | ELDORADO | 1845 | 1066 | 0
395 | AB EAST 12KV | 5760 | 1091 | 0
396 | TWILIGHT TRAIL | 4290 | 1747 | 0

## WTU--Causes
CSW - West Texas Utilities
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
| Causes of Forced Interruptions 1999 |  | Percentage
|  | Weather (Including Lightning) | 38.7%
|  | Vegetation | 12.2%
|  | Animals and Birds | 10.8%
|  | People (Including cars and farm equip) | 1.9%
|  | Utility-owned Equipment | 6.7%
|  | Other | 19.3%
|  | Unknown | 10.4%
100%
24 Month Interim System-wide
Standards (01/01/1998 - 12/31/1999)
Interim System-wide SAIFI Standard
|  | WTU | 0.457
Interim System-wide SAIDI Standard
|  | WTU | 28.123