## Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | El Paso Electric Company
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 228
Due: |  | February 15, 2000
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 21972
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Industry Analysis Division
Office of Regulatory Affairs
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mel.eckhoff@puc.state.tx.us

## Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
1998 And 1999
El Paso Electric Company
Project 21972

## System-SAIFI
El Paso Electric Company
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 0.45112 | 0.014296 | 0.03688 | 0.069258 | 0.054045 | 0.012383 | 0.022489 | 0.12536 | 0.049224 | 0.008435 | 0.0091236 | 0.033603 | 0.020188
1999 | 0.2131 | 0.011848 | 0.0025891 | 0.013201 | 0.0056755 | 0.022169 | 0.031305 | 0.027494 | 0.03108 | 0.023143 | 0.01879 | 0.0039599 | 0.023532
Scheduled
1998 | 0.0083 | 0.0009 | 0.0005 | 0.0013 | 0.001 | 0.0011 | 0.0006 | 0.0005 | 0.0007 | 0.0009 | 0 | 0.0005 | 0.0003
1999 | 0.0072 | 0.0007 | 0.0004 | 0.0007 | 0.0009 | 0.001 | 0.0008 | 0.0007 | 0.0007 | 0.0003 | 0.0003 | 0.0004 | 0.0003
Outside Causes
1998 | 0.0781 | 0 | 0 | 0 | 0 | 0.0072 | 0.0182 | 0.0176 | 0 | 0.0356 | 0 | 0 | 0
1999 | 0.011489 | 0.013787 | 0.0095871 | 0.016505 | 0.0013114 | 0.0075106 | 0.011348 | 0 | 0.068312 | 0 | 0.0096503 | 0 | 0
Major Events
1998 | 0.4261 | 0 | 0.0015 | 0 | 0 | 0.4274 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## System-SAIDI
El Paso Electric Company
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 35.1321 | 1.4994 | 1.223 | 3.5022 | 2.3322 | 1.6564 | 3.09 | 11.8659 | 4.7779 | 1.2922 | 1.4304 | 1.6492 | 1.1034
1999 | 23.36 | 1.0903 | 0.31357 | 0.63973 | 0.74509 | 1.6189 | 3.3243 | 3.1286 | 5.2911 | 2.4899 | 1.6302 | 0.37065 | 2.8896
Scheduled
1998 | 0.34 | 0.02 | 0.02 | 0.08 | 0.05 | 0.03 | 0.03 | 0.01 | 0.03 | 0.03 | 0 | 0.01 | 0.01
1999 | 0.45 | 0.03 | 0.02 | 0.03 | 0.04 | 0.09 | 0.04 | 0.04 | 0.06 | 0.02 | 0.01 | 0.02 | 0.05
Outside Causes
1998 | 5.59 | 0 | 0 | 0 | 0 | 3.85 | 0.71 | 0.71 | 0 | 0.36 | 0 | 0 | 0
1999 | 0.82103 | 0.55282 | 0.99706 | 5.2157 | 0.24917 | 0.66731 | 0.43881 | 0 | 1.2219 | 0 | 0.55972 | 0 | 0
Major Events
1998 | 6.34 | 0 | 0.22 | 0 | 0 | 6.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Feeder-SAIFI
List all Distribution Feeders on Texas System |  |  | Total Number of Feeders
Add or Delete Rows as Necessary |  |  | 228
El Paso Electric Company
1999 SAIFI Ranking | Substation Identification | Feeder Identification | 1999 SAIFI Value
1 | BUTTERFIELD | 11 | 2.63
2 | SIERRA BLANCA | 20 | 2.13
3 | SUMMIT | 01 | 2.12
4 | SOCORRO | 10 | 2.11
5 | BUTTERFIELD | 12 | 2.03
6 | ALAMO | 21 | 1.67
7 | CALIENTE | 10 | 1.62
8 | AMERICAS | 10 | 1.46
9 | LOMALAND | 02 | 1.41
10 | CIELO | 01 | 1.36
11 | VAN HORN | 02 | 1.3
12 | ASCARATE | 03 | 1.22
13 | RANCHLAND | 02 | 1.22
14 | MONTOYA | 20 | 1.14
15 | WRANGLER | 14 | 1.12
16 | MESA | 16 | 1.11
17 | ASCARATE | 13 | 1.08
18 | ASCARATE | 11 | 1.06
19 | LA TUNA | 01 | 1.06
20 | DALLAS | 01 | 1.05
21 | FT. HANCOCK | 01 | 1.05
22 | MANN | 14 | 1.05
23 | PARKDALE | 02 | 1.05
24 | SUNSET | 13 | 1.05
25 | SANTA FE | 04 | 1.04
26 | VISTA | 15 | 1.04
27 | RADFORD | 01 | 1
28 | DALLAS | 04 | 0.99
29 | FARMER | 21 | 0.96
30 | HORIZON | 10 | 0.95
31 | CLARDY | 02 | 0.92
32 | MILAGRO | 11 | 0.84
33 | CANUTILLO | 01 | 0.78
34 | AUSTIN | 04 | 0.75
35 | AUSTIN | 01 | 0.63
36 | DIANA | 01 | 0.63
37 | LANE | 11 | 0.58
38 | MISSION | 01 | 0.58
39 | FRESNO | 01 | 0.51
40 | FIVE POINTS | 02 | 0.49
41 | FRONTERA | 01 | 0.48
42 | SUNSET | 05 | 0.45
43 | CIELO | 02 | 0.44
44 | ALAMO | 20 | 0.43
45 | AUSTIN | 15 | 0.42
46 | ALTURA | 04 | 0.41
47 | HORIZON | 11 | 0.38
48 | MILAGRO | 17 | 0.38
49 | ASCARATE | 10 | 0.37
50 | EAST | 01 | 0.37
51 | NEWTEX | 02 | 0.35
52 | VALLEY | 10 | 0.35
53 | MESA | 14 | 0.34
54 | RIO GRANDE | 13 | 0.34
55 | WHITE | 01 | 0.33
56 | ANTHONY | 20 | 0.32
57 | MULBERRY | 01 | 0.32
58 | DIANA | 02 | 0.3
59 | COYOTE | 10 | 0.29
60 | LOMALAND | 01 | 0.29
61 | CLINT | 11 | 0.28
62 | MORNINGSIDE | 02 | 0.28
63 | SUMMIT | 02 | 0.28
64 | SOL | 10 | 0.28
65 | GRACE | 01 | 0.27
66 | VAN HORN | 01 | 0.27
67 | SUNSET | 02 | 0.26
68 | CINECUE | 01 | 0.25
69 | SANTA TERESA | 20 | 0.25
70 | THORN | 12 | 0.25
71 | AUSTIN | 03 | 0.24
72 | CROMO | 15 | 0.24
73 | SHEARMAN | 11 | 0.23
74 | FABENS | 01 | 0.21
75 | MANN | 13 | 0.21
76 | VISTA | 10 | 0.21
77 | CORONADO | 01 | 0.2
78 | CLARDY | 01 | 0.19
79 | HACIENDA | 01 | 0.19
80 | FIVE POINTS | 01 | 0.18
81 | THORN | 11 | 0.18
82 | TORNILLO | 01 | 0.18
83 | VISTA | 14 | 0.18
84 | CALIENTE | 11 | 0.17
85 | DYER | 11 | 0.17
86 | RANCHLAND | 01 | 0.17
87 | VISTA | 13 | 0.17
88 | CROMO | 12 | 0.16
89 | DIANA | 03 | 0.16
90 | ASCARATE | 04 | 0.15
91 | KEMP | 01 | 0.15
92 | MANN | 10 | 0.15
93 | PARKDALE | 01 | 0.15
94 | SCOTSDALE | 15 | 0.15
95 | VISTA | 11 | 0.15
96 | MANN | 12 | 0.14
97 | MILAGRO | 12 | 0.14
98 | MONTOYA | 21 | 0.14
99 | SOL | 14 | 0.14
100 | MANN | 11 | 0.13
101 | MILAGRO | 13 | 0.13
102 | SHEARMAN | 12 | 0.13
103 | SIERRA BLANCA | 01 | 0.13
104 | YSLETA | 02 | 0.13
105 | LEO | 02 | 0.12
106 | MULBERRY | 02 | 0.12
107 | SCOTSDALE | 12 | 0.12
108 | SANTA TERESA | 21 | 0.12
109 | ZARAGOSA | 01 | 0.12
110 | FELIPE | 20 | 0.11
111 | SCOTSDALE | 16 | 0.11
112 | THORN | 13 | 0.11
113 | ALTURA | 03 | 0.1
114 | RIO GRANDE | 15 | 0.1
115 | SCOTSDALE | 11 | 0.1
116 | THORN | 14 | 0.1
117 | TOBIN | 02 | 0.1
118 | LEO | 01 | 0.09
119 | MILAGRO | 15 | 0.09
120 | DYER | 13 | 0.08
121 | MILAGRO | 14 | 0.08
122 | MISSION | 02 | 0.08
123 | THORN | 15 | 0.08
124 | VISTA | 12 | 0.08
125 | ALTURA | 02 | 0.07
126 | ALTURA | 06 | 0.07
127 | ASCARATE | 02 | 0.07
128 | LEO | 11 | 0.07
129 | ZARAGOSA | 11 | 0.07
130 | ASCARATE | 01 | 0.06
131 | AUSTIN | 02 | 0.06
132 | COTTON | 01 | 0.06
133 | CROMO | 11 | 0.06
134 | FIVE POINTS | 03 | 0.06
135 | HACIENDA | 02 | 0.06
136 | WRANGLER | 13 | 0.06
137 | ALTURA | 05 | 0.05
138 | AMERICAS | 11 | 0.05
139 | BUTTERFIELD | 10 | 0.05
140 | CLINT | 01 | 0.05
141 | MIDWAY | 01 | 0.05
142 | VISCOUNT | 11 | 0.05
143 | ANTHONY | 22 | 0.04
144 | BEAUMONT | 01 | 0.04
145 | DALLAS | 16 | 0.04
146 | SANTA FE | 01 | 0.04
147 | DALLAS | 13 | 0.03
148 | LEO | 12 | 0.03
149 | NEWTEX | 01 | 0.03
150 | SOL | 15 | 0.03
151 | SUNSET | 04 | 0.03
152 | THORN | 10 | 0.03
153 | YSLETA | 01 | 0.03
154 | ZARAGOSA | 10 | 0.03
155 | AUSTIN | 10 | 0.02
156 | AUSTIN | 12 | 0.02
157 | FABENS | 02 | 0.02
158 | MESA | 17 | 0.02
159 | MESA | 18 | 0.02
160 | OCTAVIA | 01 | 0.02
161 | SCOTSDALE | 13 | 0.02
162 | SANTA FE | 11 | 0.02
163 | SUNSET | 07 | 0.02
164 | TOBIN | 01 | 0.02
165 | ALTURA | 01 | 0.01
166 | COTTON | 02 | 0.01
167 | DALLAS | 11 | 0.01
168 | DYER | 12 | 0.01
169 | DYER | 14 | 0.01
170 | FIVE POINTS | 04 | 0.01
171 | LATTA | 01 | 0.01
172 | MIDWAY | 02 | 0.01
173 | SUNSET NORTH | 11 | 0.01
174 | SOL | 13 | 0.01
175 | SUNSET | 08 | 0.01
176 | SUNSET | 15 | 0.01
177 | VISCOUNT | 10 | 0.01
178 | WRANGLER | 10 | 0.01
179 | AUSTIN | 16 | 0
180 | AUSTIN | 17 | 0
181 | COPPER | 10 | 0
182 | CROMO | 13 | 0
183 | DALLAS | 12 | 0
184 | DALLAS | 17 | 0
185 | LANE | 13 | 0
186 | MANN | 15 | 0
187 | MESA | 12 | 0
188 | MESA | 13 | 0
189 | SANTA FE | 02 | 0
190 | SANTA FE | 10 | 0
191 | SHEARMAN | 10 | 0
192 | SUNSET NORTH | 10 | 0
193 | SUNSET NORTH | 12 | 0
194 | SOCORRO | 11 | 0
195 | SOL | 11 | 0
196 | SUNSET | 14 | 0
197 | AMERICAS | 12 | 0
198 | ASCARATE | 12 | 0
199 | ASCARATE | 14 | 0
200 | AUSTIN | 11 | 0
201 | AUSTIN | 13 | 0
202 | AUSTIN | 14 | 0
203 | BUTTERFIELD | 14 | 0
204 | COPPER | 11 | 0
205 | COPPER | 12 | 0
206 | CROMO | 10 | 0
207 | CROMO | 14 | 0
208 | DALLAS | 02 | 0
209 | EAST | 02 | 0
210 | FARAH | 11 | 0
211 | LANE | 12 | 0
212 | LEO | 13 | 0
213 | MORNINGSIDE | 01 | 0
214 | RIO GRANDE | 11 | 0
215 | RIVER | 01 | 0
216 | MONTOYA | 22 | 0
217 | MONTOYA | 23 | 0
218 | SCOTSDALE | 14 | 0
219 | SANTA FE | 03 | 0
220 | SANTA FE | 05 | 0
221 | SANTA FE | 12 | 0
222 | SANTA FE | 50 | 0
223 | SOL | 12 | 0
224 | SUNSET | 01 | 0
225 | VISCOUNT | 12 | 0
226 | WHITE | 02 | 0
227 | WRANGLER | 11 | 0
228 | WRANGLER | 12 | 0

## Feeder-SAIDI
List all Distribution Feeders on Texas System |  |  | Total Number of Feeders
Add or Delete Rows as Necessary |  |  | 228
El Paso Electric Company
1999 SAIDI Ranking | Substation Identification | Feeder Identification | 1999 SAIDI Value
1 | VAN HORN | 02 | 424.3778
2 | LOMALAND | 02 | 280.6791
3 | BUTTERFIELD | 11 | 245.375
4 | BUTTERFIELD | 12 | 244.25
5 | SIERRA BLANCA | 20 | 216.8141
6 | FT. HANCOCK | 01 | 214.4278
7 | AUSTIN | 04 | 212.5349
8 | CLARDY | 02 | 209.9282
9 | HORIZON | 10 | 181
10 | DALLAS | 01 | 163.1769
11 | ALAMO | 21 | 159.9104
12 | AMERICAS | 10 | 156.019
13 | ASCARATE | 03 | 151.4033
14 | LA TUNA | 01 | 147.4583
15 | AUSTIN | 15 | 134.4193
16 | CALIENTE | 10 | 121.2422
17 | MONTOYA | 20 | 115.7738
18 | CIELO | 01 | 107.8566
19 | SOCORRO | 10 | 102.698
20 | CANUTILLO | 01 | 100.5641
21 | DIANA | 01 | 87.9577
22 | DALLAS | 04 | 87.8289
23 | MILAGRO | 11 | 83.842
24 | LANE | 11 | 81.2231
25 | SUNSET | 05 | 79.14
26 | MISSION | 01 | 75.6849
27 | THORN | 12 | 73.5736
28 | WRANGLER | 14 | 71.9684
29 | SUMMIT | 02 | 71.048
30 | ANTHONY | 20 | 70.5175
31 | ASCARATE | 11 | 68.8424
32 | MORNINGSIDE | 02 | 68.3987
33 | FIVE POINTS | 02 | 67.3253
34 | ASCARATE | 10 | 66.2475
35 | MILAGRO | 17 | 64.1292
36 | MESA | 16 | 63.2055
37 | VISTA | 15 | 62.3301
38 | RANCHLAND | 02 | 60.7532
39 | HORIZON | 11 | 60.432
40 | RADFORD | 01 | 57.8344
41 | FRESNO | 01 | 54.9912
42 | SHEARMAN | 11 | 53.865
43 | SANTA TERESA | 20 | 51.0311
44 | CLINT | 11 | 49.1329
45 | FRONTERA | 01 | 44.9036
46 | THORN | 11 | 44.6772
47 | EAST | 01 | 43.1408
48 | RIO GRANDE | 13 | 42.1193
49 | FARMER | 21 | 41.8749
50 | WHITE | 01 | 41.6943
51 | VISTA | 11 | 41.3993
52 | VISTA | 13 | 41.3154
53 | CROMO | 15 | 40.2201
54 | SUNSET | 02 | 40.0205
55 | CORONADO | 01 | 39.9046
56 | AUSTIN | 01 | 39.4689
57 | AUSTIN | 03 | 38.0372
58 | ALAMO | 20 | 37.6855
59 | VALLEY | 10 | 36.3725
60 | SOL | 10 | 35.6113
61 | MANN | 13 | 34.7672
62 | SANTA FE | 04 | 33.6601
63 | VISTA | 14 | 32.5047
64 | LOMALAND | 01 | 32.4254
65 | MULBERRY | 01 | 32.3196
66 | DIANA | 02 | 29.2216
67 | COYOTE | 10 | 28.551
68 | SOL | 14 | 26.3158
69 | MILAGRO | 13 | 26.108
70 | TOBIN | 02 | 26.0241
71 | NEWTEX | 02 | 24.0364
72 | ALTURA | 04 | 23.7478
73 | THORN | 14 | 23.7094
74 | CINECUE | 01 | 22.4254
75 | BUTTERFIELD | 10 | 22.15
76 | CIELO | 02 | 22.0672
77 | ASCARATE | 02 | 21.9964
78 | FELIPE | 20 | 21.7413
79 | SANTA TERESA | 21 | 20.8953
80 | YSLETA | 02 | 20.0892
81 | PARKDALE | 01 | 20.0267
82 | LEO | 11 | 19.8758
83 | CROMO | 12 | 19.8458
84 | MESA | 14 | 19.507
85 | MANN | 12 | 19.1195
86 | FIVE POINTS | 01 | 18.7844
87 | MILAGRO | 12 | 18.4254
88 | MONTOYA | 21 | 18.1752
89 | THORN | 15 | 18.0499
90 | ASCARATE | 13 | 17.561
91 | DIANA | 03 | 17.4977
92 | CALIENTE | 11 | 17.2106
93 | DYER | 11 | 17.0321
94 | RIO GRANDE | 15 | 16.9167
95 | VISTA | 10 | 16.6176
96 | VAN HORN | 01 | 16.4786
97 | DYER | 13 | 16.265
98 | GRACE | 01 | 16.1984
99 | SUNSET | 13 | 16.1882
100 | MANN | 10 | 16.0521
101 | FABENS | 01 | 15.9261
102 | RANCHLAND | 01 | 15.702
103 | THORN | 13 | 15.5248
104 | SCOTSDALE | 16 | 15.1899
105 | SCOTSDALE | 12 | 14.3545
106 | LEO | 01 | 14.2897
107 | MANN | 14 | 14.0957
108 | KEMP | 01 | 13.3406
109 | WRANGLER | 13 | 12.9789
110 | LEO | 02 | 12.7343
111 | SCOTSDALE | 11 | 11.8579
112 | MANN | 11 | 11.3462
113 | MISSION | 02 | 11.1423
114 | SCOTSDALE | 15 | 10.1406
115 | HACIENDA | 01 | 10.1353
116 | VISTA | 12 | 9.6857
117 | SIERRA BLANCA | 01 | 9.6415
118 | SOL | 15 | 8.946
119 | ASCARATE | 04 | 8.7151
120 | ALTURA | 06 | 8.5574
121 | CLARDY | 01 | 8.5528
122 | MILAGRO | 14 | 8.482
123 | PARKDALE | 02 | 8.4242
124 | TORNILLO | 01 | 8.3562
125 | SHEARMAN | 12 | 8.3346
126 | CLINT | 01 | 8.0138
127 | DALLAS | 16 | 7.9649
128 | MULBERRY | 02 | 7.7795
129 | ZARAGOSA | 01 | 7.6556
130 | THORN | 10 | 7.3477
131 | ASCARATE | 01 | 6.9797
132 | COTTON | 01 | 6.7522
133 | AUSTIN | 02 | 6.7022
134 | MESA | 17 | 6.6224
135 | MILAGRO | 15 | 5.9242
136 | ALTURA | 05 | 5.6994
137 | FIVE POINTS | 03 | 5.3832
138 | ALTURA | 03 | 5.0188
139 | ALTURA | 02 | 5
140 | AMERICAS | 11 | 4.7943
141 | CROMO | 11 | 4.371
142 | MIDWAY | 01 | 4.3148
143 | ZARAGOSA | 11 | 4.2682
144 | NEWTEX | 01 | 4.1274
145 | HACIENDA | 02 | 3.8635
146 | MIDWAY | 02 | 3.2617
147 | LEO | 12 | 3.2386
148 | ZARAGOSA | 10 | 2.9056
149 | SCOTSDALE | 13 | 2.8821
150 | SUMMIT | 01 | 2.5169
151 | BEAUMONT | 01 | 2.4155
152 | YSLETA | 01 | 2.2928
153 | MANN | 15 | 2.0833
154 | VISCOUNT | 11 | 2.0477
155 | SUNSET | 08 | 1.991
156 | SUNSET | 15 | 1.9109
157 | DALLAS | 13 | 1.8859
158 | MESA | 18 | 1.8638
159 | AUSTIN | 12 | 1.8247
160 | SUNSET | 04 | 1.7619
161 | SOL | 13 | 1.6402
162 | AUSTIN | 10 | 1.4868
163 | ALTURA | 01 | 1.4792
164 | SUNSET NORTH | 11 | 1.4292
165 | TOBIN | 01 | 1.2483
166 | SOL | 11 | 1.2455
167 | OCTAVIA | 01 | 1.1206
168 | ANTHONY | 22 | 1.0321
169 | LATTA | 01 | 1.0179
170 | SUNSET | 07 | 0.9785
171 | DALLAS | 11 | 0.939
172 | FABENS | 02 | 0.8485
173 | COTTON | 02 | 0.7778
174 | SANTA FE | 11 | 0.7467
175 | FIVE POINTS | 04 | 0.652
176 | MESA | 12 | 0.5908
177 | DYER | 14 | 0.3948
178 | SANTA FE | 01 | 0.3922
179 | WRANGLER | 10 | 0.3714
180 | SANTA FE | 10 | 0.3416
181 | DALLAS | 17 | 0.3259
182 | DYER | 12 | 0.2973
183 | VISCOUNT | 10 | 0.2505
184 | SUNSET | 14 | 0.2439
185 | DALLAS | 12 | 0.2257
186 | MESA | 13 | 0.1652
187 | SOCORRO | 11 | 0.1479
188 | SHEARMAN | 10 | 0.129
189 | SUNSET NORTH | 12 | 0.1182
190 | SUNSET NORTH | 10 | 0.1045
191 | CROMO | 13 | 0.1002
192 | LANE | 13 | 0.0991
193 | SANTA FE | 02 | 0.0914
194 | AUSTIN | 16 | 0.058
195 | AUSTIN | 17 | 0.0385
196 | COPPER | 10 | 0.035
197 | AMERICAS | 12 | 0
198 | ASCARATE | 12 | 0
199 | ASCARATE | 14 | 0
200 | AUSTIN | 11 | 0
201 | AUSTIN | 13 | 0
202 | AUSTIN | 14 | 0
203 | BUTTERFIELD | 14 | 0
204 | COPPER | 11 | 0
205 | COPPER | 12 | 0
206 | CROMO | 10 | 0
207 | CROMO | 14 | 0
208 | DALLAS | 02 | 0
209 | EAST | 02 | 0
210 | FARAH | 11 | 0
211 | LANE | 12 | 0
212 | LEO | 13 | 0
213 | MORNINGSIDE | 01 | 0
214 | RIO GRANDE | 11 | 0
215 | RIVER | 01 | 0
216 | MONTOYA | 22 | 0
217 | MONTOYA | 23 | 0
218 | SCOTSDALE | 14 | 0
219 | SANTA FE | 03 | 0
220 | SANTA FE | 05 | 0
221 | SANTA FE | 12 | 0
222 | SANTA FE | 50 | 0
223 | SOL | 12 | 0
224 | SUNSET | 01 | 0
225 | VISCOUNT | 12 | 0
226 | WHITE | 02 | 0
227 | WRANGLER | 11 | 0
228 | WRANGLER | 12 | 0

## Causes
El Paso Electric Company
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 27.58%
|  | Utility-owned Equipment | 20.18%
|  | Unknown | 19.03%
|  | People (Including cars and farm equip) | 10.48%
|  | Vegetation | 10.48%
|  | Animals and Birds | 10.42%
|  | Other | 1.82%