## Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | TEXAS-NEW MEXICO POWER COMPANY
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 264
Due: |  | February 15, 2000
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 21972
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Industry Analysis Division
Office of Regulatory Affairs
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mel.eckhoff@puc.state.tx.us

## Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
1998 And 1999
TEXAS-NEW MEXICO POWER COMPANY
Project 21972

## System-SAIFI
TEXAS-NEW MEXICO POWER COMPANY
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 0.8989 | 0.0309 | 0.0699 | 0.0537 | 0.0178 | 0.1061 | 0.1232 | 0.1093 | 0.083 | 0.1367 | 0.0855 | 0.0438 | 0.0389
1999 | 0.6366 | 0.0168 | 0.0198 | 0.0543 | 0.0895 | 0.1463 | 0.075 | 0.046 | 0.0512 | 0.0191 | 0.0253 | 0.0312 | 0.0623
Scheduled
1998 | 0.0183 | 0.0011 | 0.0058 | 0.0003 | 0.0033 | 0.0005 | 0.0005 | 0.0045 | 0.0006 | 0.0002 | 0.0005 | 0.0002 | 0.0008
1999 | 0.0164 | 0.0001 | 0.0011 | 0.0057 | 0.0005 | 0.0002 | 0.0002 | 0.0024 | 0.0003 | 0.0004 | 0.0003 | 0.0051 | 0.0001
Outside Causes
1998 | 0.1695 | 0.0037 | 0.0017 | 0 | 0 | 0.0554 | 0.0403 | 0.0358 | 0 | 0 | 0.0195 | 0 | 0.0131
1999 | 0.0283 | 0 | 0 | 0.0036 | 0.0059 | 0.0185 | 0 | 0 | 0 | 0 | 0.0003 | 0 | 0
Major Events
1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## System-SAIDI
TEXAS-NEW MEXICO POWER COMPANY
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 65.5617 | 2.5813 | 4.5573 | 2.264 | 0.8317 | 6.4536 | 11.1914 | 7.7538 | 5.5742 | 12.1042 | 4.6669 | 2.938 | 4.6453
1999 | 41.6364 | 1.3055 | 1.588 | 3.087 | 3.5657 | 9.9073 | 5.502 | 2.7981 | 3.6245 | 1.1112 | 1.6338 | 3.2048 | 4.3083
Scheduled
1998 | 0.9335 | 0.0774 | 0.4665 | 0.039 | 0.0688 | 0.0511 | 0.0364 | 0.0252 | 0.0397 | 0.0114 | 0.0416 | 0.0428 | 0.0337
1999 | 0.4431 | 0.005 | 0.0483 | 0.0434 | 0.0616 | 0.0229 | 0.0143 | 0.0746 | 0.0151 | 0.0329 | 0.0314 | 0.0863 | 0.0071
Outside Causes
1998 | 12.6669 | 1.1407 | 0.0558 | 0 | 0 | 2.8698 | 3.9103 | 2.2498 | 0 | 0.0003 | 1.3058 | 0 | 1.1343
1999 | 1.334 | 0 | 0 | 0.1895 | 0.6365 | 0.5039 | 0 | 0 | 0 | 0 | 0.0041 | 0 | 0
Major Events
1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Feeder-SAIFI
List all Distribution Feeders on Texas System |  |  | Total Number of Feeders
Add or Delete Rows as Necessary |  |  | 264
TEXAS-NEW MEXICO POWER COMPANY
1999 SAIFI Ranking | Substation Identification | Feeder Identification | 1999 SAIFI Value
1 | SUBS-PC,FLAT TOP SUB | 26P02 25.0 KV | 5.0741
2 | SUBS-SN,SANDERSON SUB | 4S28 4.0 KV | 4.0226
3 | SUBS-SN,SANDERSON SUB | 4S26 4.0 KV | 4.0043
4 | SUBS-SN,SANDERSON SUB | 4S27 4.0 KV | 4
5 | SUBS-SN,C.C. MITCHELL SUB | SF2S102 12.5 KV | 4
6 | SUBS-PC,FLAT TOP SUB | 26P01 25.0 KV | 3.7652
7 | SUBS-PC,PYOTE SUB | 25P217 25.0 KV | 3.6173
8 | SUBS-DC,LEAGUE CITY SUB | 1281 12.5 KV | 3.5
9 | SUBS-WC,BRAZORIA SUB | 1270 12.5 KV | 3.2649
10 | SUBS-PC,COCHISE SUB | 25P47 25.0 KV | 2.9
11 | SUBS-WC,BRAZORIA SUB | 1271 12.5 KV | 2.8783
12 | SUBS-LW,SOUTH SUB | 1103 12.5 KV | 2.8244
13 | SUBS-WC,WEST COLUMBIA SUB | 1234 12.5 KV | 2.5484
14 | SUBS-BG,RED RIVER SUB | 2252 22.0 KV | 2.3967
15 | SUBS-PL,KRUGERVILLE SUB | 2604 22.0 KV | 2.329
16 | SUBS-PC,PYOTE SUB | 25P312 25.0 KV | 2.2955
17 | SUBS-PC,LONE STAR SUB | 25P171 25.0 KV | 2.2766
18 | SUBS-PC,STAFFORD SUB | 12P83 12.5 KV | 2.2551
19 | SUBS-BG,TALCO WEST SUB | 13909 12.5 KV | 2.2195
20 | SUBS-PC,LONE STAR SUB | 25P174 25.0 KV | 2.2143
21 | SUBS-FI,ALVIN SUB | 1230 12.5 KV | 2.1767
22 | SUBS-FR,PUCKETT SUB | 25F18 25.0 KV | 2.1667
23 | SUBS-BR,BRYSONS SUB | 1233 12.5 KV | 2.1417
24 | SUBS-TC,HEIGHTS SUB | 1132 12.5 KV | 2.103
25 | SUBS-PC,PECOS MAIN SUB | 12P01 12.5 KV | 2.0935
26 | SUBS-LW,WEST SUB | 1234 12.5 KV | 2.0525
27 | SUBS-LO,LEONARD SUB | 12678 12.5 KV | 2.0033
28 | SUBS-KR,KERMIT NO.1 SUB | 4K03 4.0 KV | 2
29 | SUBS-LW,LAKEPOINTE SUB | 2536 25.0 KV | 1.9
30 | SUBS-PC,WORSHAM FIELD SUB | 13P97 12.5 KV | 1.7031
31 | SUBS-HM,HAMILTON CITY #2 22 | 23820 25.0 KV | 1.5797
32 | SUBS-LW,WEST SUB | 1223 12.5 KV | 1.5627
33 | SUBS-HC,HICO CITY SUB | 390 4.0 KV | 1.5014
34 | SUBS-TC,LAMARQUE SUB | 1204 12.5 KV | 1.4494
35 | SUBS-TC,TEJAS SUB | 1215 12.5 KV | 1.4067
36 | SUBS-PC,REEVES CO. NO.4 SUB | 12P28 12.5 KV | 1.3803
37 | DEPORT | 22164 22.0 KV | 1.3792
38 | SUBS-TC,FREEWAY PARK SUB | 1297 12.5 KV | 1.3706
39 | SUBS-PI,CLIMAX SUB | 2270 22.0 KV | 1.3683
40 | SUBS-TC,NORTHSIDE SUB | 1293 12.5 KV | 1.3279
41 | SUBS-PC,REEVES CO. NO.4 SUB | 13P37 12.5 KV | 1.3232
42 | SUBS-LW,WEST SUB | 1235 12.5 KV | 1.3068
43 | SUBS-KR,CALIFORNIA SUB | 12K87 12.5 KV | 1.2885
44 | SUBS-GE,GLEN ROSE #1 SUB | 22295 22.0 KV | 1.2844
45 | SUBS-SR,THURBER 22KV SUB | 1490 22.0 KV | 1.2817
46 | SUBS-TC,LAMARQUE SUB | 1205 12.5 KV | 1.2686
47 | SUBS-FR,PUCKETT SUB | 25F14 25.0 KV | 1.25
48 | SUBS-WC,BRAZORIA SUB | 1290 12.5 KV | 1.2494
49 | SUBS-HM,HAMILTON CITY #1 22 | 22785 22.0 KV | 1.2151
50 | SUBS-DC,DICKINSON SUB | 1274 12.5 KV | 1.2065
51 | SUBS-LW,WEST SUB | 1221 12.5 KV | 1.2012
52 | SUBS-GT,CORYELL CO #2 SUB | 22365 22.0 KV | 1.1996
53 | SUBS-TC,NORTHSIDE SUB | 1228 12.5 KV | 1.1933
54 | SUBS-CL,CLIFTON #1 22 KV | 22480 22.0 KV | 1.1744
55 | SUBS-LW,JONES STREET SUB | 1412 12.5 KV | 1.1481
56 | SUBS-PC,WORSHAM FIELD SUB | 13P98 12.5 KV | 1.137
57 | SUBS-WC,BRAZORIA SUB | 1291 12.5 KV | 1.1343
58 | SUBS-PC,W.D. FAULKNER SUB | 12P259 12.5 KV | 1.1259
59 | SUBS-LW,SOUTH SUB | 1102 12.5 KV | 1.1181
60 | SUBS-SR,THURBER 12.5KV SUB | 1447 12.5 KV | 1.1047
61 | SUBS-KR,WICKETT SUB | 12K446 12.5 KV | 1.1
62 | SUBS-AG,ANGLETON SUB | 1242 12.5 KV | 1.0744
63 | SUBS-DC,DICKINSON SUB | 1272 12.5 KV | 1.0479
64 | SUBS-LW,SOUTH SUB | 1104 12.5 KV | 1.0462
65 | SUBS-LW,WEST SUB | 1233 12.5 KV | 1.0302
66 | SUBS-FR,DOWNTOWN SUB | 12F114 12.5 KV | 1.0275
67 | SUBS-MR,MERIDIAN 22KV SUB | 23205 22.0 KV | 1.0229
68 | SUBS-TC,LAMARQUE SUB | 1110 12.5 KV | 1.0128
69 | SUBS-LW,TI SUB | 1012 12.5 KV | 1.0081
70 | SUBS-KR,KERMIT NO.1 SUB | 4K02 4.0 KV | 1.0056
71 | SUBS-KR,WICKETT SUB | 12K449 12.5 KV | 1.0056
72 | SUBS-MR,MERIDIAN 22KV SUB | 23210 22.0 KV | 1.0014
73 | SUBS-GE,GLEN ROSE #2 SUB | 22305 22.0 KV | 1.0012
74 | SUBS-CL,CLIFTON #2 22KV | 23165 22.0 KV | 1
75 | SUBS-KR,KEYSTONE SUB | 12K437 12.5 KV | 1
76 | SUBS-KR,KERMIT NO.1 SUB | 4K05 4.0 KV | 1
77 | SUBS-KR,KERMIT NO.1 SUB | 4K04 4.0 KV | 1
78 | SUBS-MR,MERIDIAN 4KV SUB | 680 4.0 KV | 1
79 | SUBS-LW,LAKEPOINTE SUB | 2508 25.0 KV | 1
80 | SUBS-MR,MERIDIAN 4KV SUB | 690 4.0 KV | 1
81 | SUBS-KR,CALIFORNIA SUB | 12K86 12.5 KV | 1
82 | SUBS-LW,WEST SUB | 1222 12.5 KV | 1
83 | SUBS-HC,HICO CITY SUB | 395 4.0 KV | 0.9935
84 | SUBS-SR,THURBER 22KV SUB | 22890 22.0 KV | 0.9899
85 | SUBS-VL,VALLEY MILLS SUB | 22570 22.0 KV | 0.9227
86 | SUBS-NC,PETROLIA SUB | 12260 12.5 KV | 0.9214
87 | SUBS-PL,KRUGERVILLE SUB | 2608 25.0 KV | 0.8995
88 | SUBS-DC,DICKINSON SUB | 1267 12.5 KV | 0.8867
89 | SUBS-AG,ANGLETON SUB | 1240 12.5 KV | 0.8858
90 | SUBS-WC,OLD OCEAN SUB | 1260 12.5 KV | 0.8852
91 | SUBS-FI,ALVIN SUB | 1257 12.5 KV | 0.8061
92 | SUBS-GE,GLEN ROSE #2 SUB | 22300 22.0 KV | 0.771
93 | SUBS-HM,HAMILTON COUNTY SUB | 2340 2.4 KV | 0.7652
94 | SUBS-EO,LONE OAK SUB | 13384 12.5 KV | 0.7143
95 | SUBS-FI,FRIENDSWOOD SUB | 1251 12.5 KV | 0.7013
96 | SUBS-FR,GOMEZ SUB | 25F05 25.0 KV | 0.6957
97 | SUBS-MR,WALNUT SPRINGS 22KV | 2210 22.0 KV | 0.6923
98 | SUBS-NC,NOCONA SUB | 13374 12.5 KV | 0.6264
99 | SUBS-FI,MAGNOLIA SUB | 1145 12.5 KV | 0.6129
100 | SUBS-ON,GRAHAM SUB | 1245 12.5 KV | 0.6068
101 | SUBS-TC,FREEWAY PARK SUB | 1298 12.5 KV | 0.5922
102 | SUBS-WC,SWEENY SUB | 1128 12.5 KV | 0.5689
103 | SUBS-FI,FRIENDSWOOD SUB | 1253 12.5 KV | 0.5582
104 | SUBS-DC,LEAGUE CITY SUB | 1285 12.5 KV | 0.5471
105 | SUBS-DC,DICKINSON SUB | 1266 12.5 KV | 0.5363
106 | SUBS-AG,ANGLETON SUB | 1243 12.5 KV | 0.5168
107 | SUBS-WI,HILL CO SUB | 22125 22.0 KV | 0.5141
108 | SUBS-FI,FRIENDSWOOD SUB | 1107 12.5 KV | 0.4991
109 | SUBS-FI,ALVIN SUB | 1115 12.5 KV | 0.4949
110 | SUBS-DC,LEAGUE CITY SUB | 1282 12.5 KV | 0.4717
111 | SUBS-DC,DICKINSON SUB | 1277 12.5 KV | 0.4462
112 | SUBS-PI,CLIMAX SUB | 22110 22.0 KV | 0.4379
113 | SUBS-TC,NORTHSIDE SUB | 1294 12.5 KV | 0.4209
114 | SUBS-PI,CLIMAX SUB | 2267 22.0 KV | 0.4158
115 | SUBS-DC,LEAGUE CITY SUB | 1284 12.5 KV | 0.412
116 | SUBS-NC,NOCONA SUB | 13610 12.5 KV | 0.4113
117 | SUBS-AG,ANGLETON SUB | 1244 12.5 KV | 0.4034
118 | SUBS-DC,LEAGUE CITY SUB | 1280 12.5 KV | 0.3995
119 | SUBS-PC,PECOS MAIN SUB | 12P02 12.5 KV | 0.3956
120 | EMORY TU | TU-1201 12.5 KV | 0.3883
121 | SUBS-DC,DICKINSON SUB | 1279 12.5 KV | 0.3808
122 | SUBS-LW,JONES STREET SUB | 1411 12.5 KV | 0.3644
123 | SUBS-GE,GLEN ROSE #3 SUB | 23875 25.0 KV | 0.3587
124 | SUBS-WC,WEST COLUMBIA SUB | 1235 12.5 KV | 0.3452
125 | SUBS-FR,BELDING SUB | 12F161 12.5 KV | 0.3333
126 | SUBS-FI,ALVIN SUB | 1117 12.5 KV | 0.3323
127 | SUBS-FI,ALVIN SUB | 1254 12.5 KV | 0.3257
128 | SUBS-AG,ANGLETON SUB | 1155 12.5 KV | 0.3237
129 | SUBS-FR,16TH STREET SUB | 12F71 12.5 KV | 0.3229
130 | SUBS-FI,ALVIN SUB | 1116 12.5 KV | 0.3202
131 | SUBS-BG,RED RIVER SUB | 2262 22.0 KV | 0.3187
132 | SUBS-TC,NORTHSIDE SUB | 1295 12.5 KV | 0.3057
133 | SUBS-WC,WEST COLUMBIA SUB | 1233 12.5 KV | 0.3025
134 | SUBS-WC,WEST COLUMBIA SUB | 1237 12.5 KV | 0.298
135 | SUBS-NC,NOCONA SUB | 12490 12.5 KV | 0.2861
136 | SUBS-NC,NOCONA SUB | 12486 12.5 KV | 0.2821
137 | SUBS-GT,SYCAMORE SUB | 24105 25.0 KV | 0.2778
138 | SUBS-TC,LAMARQUE SUB | 1201 12.5 KV | 0.2757
139 | SUBS-FR,DOWNTOWN SUB | 12F130 12.5 KV | 0.2714
140 | SUBS-WC,SWEENY SUB | 1129 12.5 KV | 0.2696
141 | SUBS-AG,ANGLETON SUB | 1241 12.5 KV | 0.2642
142 | SUBS-WW,WHITEWRIGHT SUB | 12574 12.5 KV | 0.2573
143 | SUBS-TC,LAMARQUE SUB | 1202 12.5 KV | 0.253
144 | SUBS-ON,GRAHAM SUB | 12605 12.5 KV | 0.2388
145 | SUBS-FR,16TH STREET SUB | 13F14 12.5 KV | 0.2283
146 | SUBS-TC,NORTHSIDE SUB | 1292 12.5 KV | 0.222
147 | SUBS-DC,SOUTH SHORE SUB | 1192 12.5 KV | 0.2169
148 | SUBS-WC,SWEENY SUB | 1264 12.5 KV | 0.2092
149 | SUBS-FI,FRIENDSWOOD SUB | 1108 12.5 KV | 0.2018
150 | SUBS-FI,FRIENDSWOOD SUB | 1252 12.5 KV | 0.2017
151 | SUBS-FI,MAGNOLIA SUB | 1144 12.5 KV | 0.2
152 | SUBS-TC,TEJAS SUB | 1214 12.5 KV | 0.2
153 | SUBS-FI,ALVIN SUB | 1259 12.5 KV | 0.1917
154 | SUBS-DC,SOUTH SHORE SUB | 1190 12.5 KV | 0.1917
155 | SUBS-CL,HANDLEY 22KV SUB | 22825 22.0 KV | 0.1881
156 | SUBS-TC,LAMARQUE SUB | 1203 12.5 KV | 0.1865
157 | SUBS-FI,ALVIN SUB | 1231 12.5 KV | 0.1852
158 | SUBS-TC,FREEWAY PARK SUB | 1299 12.5 KV | 0.181
159 | SUBS-AG,ANGLETON SUB | 1153 12.5 KV | 0.1781
160 | SUBS-WC,OLD OCEAN SUB | 1261 12.5 KV | 0.1761
161 | SUBS-TC,FREEWAY PARK SUB | 1102 12.5 KV | 0.1729
162 | SUBS-FR,DOWNTOWN SUB | 4F52 4.0 KV | 0.1714
163 | SUBS-WI,HILL CO SUB | 23340 22.0 KV | 0.1471
164 | SUBS-NC,NOCONA SUB | 13370 12.5 KV | 0.1401
165 | SUBS-AG,ANGLETON SUB | 1154 12.5 KV | 0.1399
166 | SUBS-AG,ANGLETON SUB | 1245 12.5 KV | 0.1398
167 | SUBS-FI,MAGNOLIA SUB | 1149 12.5 KV | 0.1379
168 | SUBS-DC,LEAGUE CITY SUB | 1283 12.5 KV | 0.1372
169 | SUBS-FR,16TH STREET SUB | 12F72 12.5 KV | 0.1364
170 | SUBS-DC,SOUTH SHORE SUB | 1195 12.5 KV | 0.1282
171 | SUBS-TC,FREEWAY PARK SUB | 1103 12.5 KV | 0.1278
172 | SUBS-TC,TEJAS SUB | 1212 12.5 KV | 0.1247
173 | SUBS-FI,MAGNOLIA SUB | 1150 12.5 KV | 0.1245
174 | ELIASVILLE POD | 1300 12.5 KV | 0.1227
175 | SUBS-NC,SAINT JO SUB | 408 4.0 KV | 0.1171
176 | SUBS-LW,WEST SUB | 1201 12.5 KV | 0.1143
177 | SUBS-FI,ALVIN SUB | 1232 12.5 KV | 0.1126
178 | SUBS-LO,LEONARD SUB | 12682 12.5 KV | 0.1057
179 | SUBS-HM,HAMILTON COUNTY SUB | 2345 2.4 KV | 0.1034
180 | SUBS-TC,HEIGHTS SUB | 1222 12.5 KV | 0.1003
181 | SUBS-HM,HAMILTON CITY #1 22 | 22780 22.0 KV | 0.0982
182 | SUBS-PC,PECOS MAIN SUB | 12P362 12.5 KV | 0.0962
183 | SUBS-WI,WHITNEY #2 SUB | 22460 22.0 KV | 0.0932
184 | SUBS-PC,STAFFORD SUB | 13P50 12.5 KV | 0.092
185 | SUBS-ON,OLNEY SWCH STA | 1685 12.5 KV | 0.0861
186 | SUBS-TC,HEIGHTS SUB | 1224 12.5 KV | 0.0849
187 | SUBS-CL,LAKE WHITNEY SUB | 12355 12.5 KV | 0.082
188 | SUBS-TC,HEIGHTS SUB | 1134 12.5 KV | 0.0817
189 | SUBS-HM,HAMILTON COUNTY SUB | 24015 25.0 KV | 0.0769
190 | SUBS-NC,SAINT JO SUB | 401 4.0 KV | 0.0759
191 | SUBS-LW,SOUTH SUB | 1109 12.5 KV | 0.0757
192 | SUBS-TC,FREEWAY PARK SUB | 1101 12.5 KV | 0.0744
193 | SUBS-PC,COCHISE SUB | 25P48 25.0 KV | 0.0736
194 | SUBS-VL,VALLEY MILLS SUB | 22575 22.0 KV | 0.0708
195 | SUBS-GT,GATESVILLE #2 SUB | 22725 22.0 KV | 0.0657
196 | SUBS-BR,BRYSONS SUB | 1230 12.5 KV | 0.0632
197 | SUBS-FR,AIRPORT SUB | 12F271 12.5 KV | 0.0588
198 | SUBS-WC,SWEENY SUB | 1263 12.5 KV | 0.0494
199 | SUBS-KR,KERMIT NO. 2 SUB | 12K48 12.5 KV | 0.0493
200 | SUBS-GT,GATESVILLE #2 SUB | 23065 22.0 KV | 0.0455
201 | SUBS-WW,BLUE RIDGE SUB | 22700 22.0 KV | 0.0389
202 | SUBS-LW,LAKEPOINTE SUB | 2516 25.0 KV | 0.0375
203 | SUBS-TC,TEJAS SUB | 1217 12.5 KV | 0.0371
204 | SUBS-LW,SOUTH SUB | 1107 12.5 KV | 0.0364
205 | SUBS-LW,JONES STREET SUB | 1413 12.5 KV | 0.0354
206 | SUBS-LW,TI SUB | 1032 12.5 KV | 0.0345
207 | SUBS-ON,OLNEY SWCH STA | 1431 12.5 KV | 0.0344
208 | SUBS-LW,TI SUB | 1033 12.5 | 0.0324
209 | SUBS-MR,WALNUT SPRINGS 12.5 | 1270 12.5 KV | 0.0303
210 | SUBS-FR,AIRPORT SUB | 12F44 12.5 KV | 0.0273
211 | SUBS-PC,STAFFORD SUB | 12P82 12.5 KV | 0.0271
212 | SUBS-PC,PECOS MAIN SUB | 2P03 2.4 KV | 0.0257
213 | SUBS-HM,HAMILTON CITY #2 22 | 23825 25.0 KV | 0.024
214 | SUBS-PC,PECOS MAIN SUB | 12P03 12.5 KV | 0.0219
215 | SUBS-GT,GATESVILLE #1 4KV | 422 4.0 KV | 0.0209
216 | SUBS-WI,WHITNEY #1 SUB | 22450 22.0 KV | 0.0169
217 | SUBS-BG,RED RIVER SUB | 2229 22.0 KV | 0.0155
218 | SUBS-GT,CORYELL CO #1 SUB | 22160 22.0 KV | 0.0149
219 | SUBS-MR,WALNUT SPRINGS 22KV | 2200 22.0 KV | 0.0147
220 | SUBS-LW,WEST SUB | 1203 12.5 KV | 0.0134
221 | SUBS-KR,KERMIT NO. 2 SUB | 4K06 4.0 KV | 0.0125
222 | SUBS-GT,GATESVILLE #1 4KV | 419 4.0 KV | 0.0121
223 | SUBS-LW,SOUTH SUB | 1108 12.5 KV | 0.0118
224 | SUBS-WI,WHITNEY #1 SUB | 22455 22.0 KV | 0.0117
225 | SUBS-LO,LEONARD SUB | 14631 12.5 KV | 0.011
226 | SUBS-WW,WHITEWRIGHT SUB | 12698 12.5 KV | 0.0099
227 | SUBS-CL,LAKE WHITNEY SUB | 1230 12.5 KV | 0.0093
228 | SUBS-ON,OLNEY SWCH STA | 1690 12.5 KV | 0.0092
229 | SUBS-MR,WALNUT SPRINGS 22KV | 2215 22.0 KV | 0.0044
230 | SUBS-CL,CLIFTON #1 4KV SUB | 407 4.0 KV | 0.0041
231 | SUBS-LO,LEONARD SUB | 14635 12.5 KV | 0.0036
232 | SUBS-GT,CORYELL #1 SUB | 22155 22.0 KV | 0.0034
233 | SUBS-WW,WHITEWRIGHT SUB | 12575 12.5 KV | 0.0032
234 | SUBS-KR,KERMIT NO. 2 SUB | 12K98 12.5 KV | 0.0025
235 | SUBS-CL,CLIFTON #2 4KV | 4160 4.0 KV | 0
236 | SUBS-CL,CLIFTON #2 4KV | 4165 4.0 KV | 0
237 | SUBS-CL,CLIFTON #1 22 KV | 22485 22.0 KV | 0
238 | SUBS-CL,CLIFTON #1 22 KV | 22495 22.0 KV | 0
239 | SUBS-CL,CLIFTON #1 4KV SUB | 405 4.0 KV | 0
240 | SUBS-CL,CLIFTON #1 4KV SUB | 490 4.0 KV | 0
241 | SUBS-CL,HANDLEY 22KV SUB | 22820 22.0 KV | 0
242 | SUBS-GT,GATESVILLE #1 4KV | 413 4.0 KV | 0
243 | SUBS-GT,GATESVILLE #2 4KV | 426 4.0 KV | 0
244 | SUBS-GT,GATESVILLE #2 4KV | 429 4.0 KV | 0
245 | SUBS-GT,SYCAMORE SUB | 24100 25.0 KV | 0
246 | SUBS-VL,VALLEY MILLS SUB | 22565 22.0 KV | 0
247 | SUBS-WI,WHITNEY #2 SUB | 22469 22.0 KV | 0
248 | SUBS-LW,LAKEPOINTE SUB | 2512 25.0 KV | 0
249 | SUBS-LW,LAKEPOINTE SUB | 2532 25.0 KV | 0
250 | SUBS-LW,WEST SUB | 1202 12.5 KV | 0
251 | SUBS-EO,LONE OAK SUB | 13388 12.5 KV | 0
252 | SUBS-LO,FRONTIER SUB | 4236 4.0 KV | 0
253 | SUBS-LO,TRENTON SUB | 4120 4.0 KV | 0
254 | SUBS-WW,WHITEWRIGHT SUB | 12753 12.5 KV | 0
255 | SUBS-WW,WHITEWRIGHT SUB | 13563 12.5 KV | 0
256 | SUBS-KR,KERMIT NO. 2 SUB | 4K07 4.0 KV | 0
257 | SUBS-KR,WINKLER CO. NO.6 SUB | 25K11 25.0 KV | 0
258 | SUBS-PC,PECOS MAIN SUB | 2P04 2.4 KV | 0
259 | SUBS-PC,PECOS MAIN SUB | 2P05 2.5 KV | 0
260 | SUBS-PC,PECOS MAIN SUB | 2P06 2.4 KV | 0
261 | SUBS-PC,STAFFORD SUB | 12P50 12.5 KV | 0
262 | SUBS-PC,STAFFORD SUB | 12P99 12.5 KV | 0
263 | SUBS-FR,GOMEZ SUB | 25F61 25.0 KV | 0
264 | SUBS-CL,CLIFTON#2 22KV | 24370 22.0 | 0

## Feeder-SAIDI
List all Distribution Feeders on Texas System |  |  | Total Number of Feeders
Add or Delete Rows as Necessary |  |  | 264
TEXAS-NEW MEXICO POWER COMPANY
1999 SAIDI Ranking | Substation Identification | Feeder Identification | 1999 SAIDI Value
1 | SUBS-SN,SANDERSON SUB | 4S28 4.0 KV | 998.8452
2 | SUBS-SN,SANDERSON SUB | 4S26 4.0 KV | 996.1745
3 | SUBS-SN,SANDERSON SUB | 4S27 4.0 KV | 996
4 | SUBS-SN,C.C. MITCHELL SUB | SF2S102 12.5 KV | 996
5 | SUBS-PC,FLAT TOP SUB | 26P02 25.0 KV | 695.8148
6 | SUBS-PC,FLAT TOP SUB | 26P01 25.0 KV | 464
7 | SUBS-DC,LEAGUE CITY SUB | 1281 12.5 KV | 375.3594
8 | SUBS-KR,KERMIT NO.1 SUB | 4K03 4.0 KV | 351.05
9 | SUBS-FR,PUCKETT SUB | 25F18 25.0 KV | 345.8333
10 | SUBS-PC,PYOTE SUB | 25P217 25.0 KV | 327.5432
11 | SUBS-PC,COCHISE SUB | 25P47 25.0 KV | 290.45
12 | SUBS-WC,BRAZORIA SUB | 1270 12.5 KV | 268.3057
13 | SUBS-CL,CLIFTON #1 22 KV | 22480 22.0 KV | 251.8605
14 | SUBS-PC,PYOTE SUB | 25P312 25.0 KV | 234.3182
15 | SUBS-BG,TALCO WEST SUB | 13909 12.5 KV | 201.4967
16 | SUBS-TC,HEIGHTS SUB | 1132 12.5 KV | 172.5571
17 | SUBS-PC,PECOS MAIN SUB | 12P01 12.5 KV | 171.7477
18 | SUBS-WC,WEST COLUMBIA SUB | 1234 12.5 KV | 170.6949
19 | SUBS-FR,GOMEZ SUB | 25F05 25.0 KV | 167.8696
20 | SUBS-HC,HICO CITY SUB | 390 4.0 KV | 159.8093
21 | SUBS-TC,FREEWAY PARK SUB | 1297 12.5 KV | 155.8311
22 | SUBS-LW,WEST SUB | 1223 12.5 KV | 152.3393
23 | SUBS-LW,SOUTH SUB | 1103 12.5 KV | 141.6588
24 | SUBS-WC,BRAZORIA SUB | 1271 12.5 KV | 139.2062
25 | SUBS-PL,KRUGERVILLE SUB | 2604 22.0 KV | 131.0237
26 | SUBS-TC,LAMARQUE SUB | 1204 12.5 KV | 126.4268
27 | SUBS-FI,ALVIN SUB | 1230 12.5 KV | 123.1775
28 | SUBS-LW,WEST SUB | 1234 12.5 KV | 117.1253
29 | SUBS-LW,WEST SUB | 1221 12.5 KV | 115.2098
30 | SUBS-KR,KERMIT NO.1 SUB | 4K02 4.0 KV | 112.5278
31 | SUBS-KR,KERMIT NO.1 SUB | 4K04 4.0 KV | 112
32 | SUBS-KR,KERMIT NO.1 SUB | 4K05 4.0 KV | 112
33 | DEPORT | 22164 22.0 KV | 108.2338
34 | SUBS-PC,WORSHAM FIELD SUB | 13P97 12.5 KV | 105.5781
35 | SUBS-KR,CALIFORNIA SUB | 12K87 12.5 KV | 105.2885
36 | SUBS-PC,LONE STAR SUB | 25P174 25.0 KV | 104.2857
37 | SUBS-HC,HICO CITY SUB | 395 4.0 KV | 102.7528
38 | SUBS-PC,REEVES CO. NO.4 SUB | 12P28 12.5 KV | 102.7394
39 | SUBS-WC,OLD OCEAN SUB | 1260 12.5 KV | 101.1967
40 | SUBS-LW,JONES STREET SUB | 1412 12.5 KV | 100.3299
41 | SUBS-NC,PETROLIA SUB | 12260 12.5 KV | 100.2264
42 | SUBS-PC,REEVES CO. NO.4 SUB | 13P37 12.5 KV | 98.0404
43 | SUBS-LW,TI SUB | 1012 12.5 KV | 97.3695
44 | SUBS-HM,HAMILTON CITY #1 22 | 22785 22.0 KV | 96.753
45 | SUBS-BR,BRYSONS SUB | 1233 12.5 KV | 96.1024
46 | SUBS-LW,WEST SUB | 1222 12.5 KV | 94
47 | SUBS-PC,STAFFORD SUB | 12P83 12.5 KV | 87.8588
48 | SUBS-LW,SOUTH SUB | 1102 12.5 KV | 87.257
49 | SUBS-PI,CLIMAX SUB | 2270 22.0 KV | 84.7754
50 | SUBS-LW,LAKEPOINTE SUB | 2508 25.0 KV | 84.6508
51 | SUBS-WC,BRAZORIA SUB | 1291 12.5 KV | 83.9187
52 | SUBS-PC,W.D. FAULKNER SUB | 12P259 12.5 KV | 82.2
53 | SUBS-LW,SOUTH SUB | 1104 12.5 KV | 80.558
54 | SUBS-GT,CORYELL CO #2 SUB | 22365 22.0 KV | 80.2781
55 | SUBS-KR,WICKETT SUB | 12K446 12.5 KV | 78
56 | SUBS-HM,HAMILTON CITY #2 22 | 23820 25.0 KV | 70.7967
57 | SUBS-BG,RED RIVER SUB | 2262 22.0 KV | 69.3407
58 | SUBS-PC,LONE STAR SUB | 25P171 25.0 KV | 64.9362
59 | SUBS-LO,LEONARD SUB | 12678 12.5 KV | 61.6427
60 | SUBS-GE,GLEN ROSE #2 SUB | 22300 22.0 KV | 60.1697
61 | SUBS-LW,LAKEPOINTE SUB | 2536 25.0 KV | 59.76
62 | SUBS-PC,PECOS MAIN SUB | 12P02 12.5 KV | 59.2601
63 | SUBS-GE,GLEN ROSE #1 SUB | 22295 22.0 KV | 56.8956
64 | SUBS-WI,HILL CO SUB | 22125 22.0 KV | 56.081
65 | SUBS-KR,KEYSTONE SUB | 12K437 12.5 KV | 56
66 | SUBS-FR,PUCKETT SUB | 25F14 25.0 KV | 55.5833
67 | SUBS-TC,NORTHSIDE SUB | 1293 12.5 KV | 53.2776
68 | SUBS-PC,WORSHAM FIELD SUB | 13P98 12.5 KV | 52.9863
69 | SUBS-BG,RED RIVER SUB | 2252 22.0 KV | 52.2256
70 | SUBS-VL,VALLEY MILLS SUB | 22570 22.0 KV | 52.0918
71 | SUBS-FI,ALVIN SUB | 1257 12.5 KV | 49.9459
72 | SUBS-TC,FREEWAY PARK SUB | 1298 12.5 KV | 48.8496
73 | SUBS-FI,FRIENDSWOOD SUB | 1107 12.5 KV | 48.6172
74 | SUBS-AG,ANGLETON SUB | 1240 12.5 KV | 48.0525
75 | SUBS-DC,DICKINSON SUB | 1274 12.5 KV | 45.7563
76 | SUBS-KR,WICKETT SUB | 12K449 12.5 KV | 45.3444
77 | SUBS-GE,GLEN ROSE #2 SUB | 22305 22.0 KV | 45.0301
78 | SUBS-KR,CALIFORNIA SUB | 12K86 12.5 KV | 45
79 | SUBS-HM,HAMILTON COUNTY SUB | 2340 2.4 KV | 44.9394
80 | SUBS-EO,LONE OAK SUB | 13384 12.5 KV | 43.4935
81 | SUBS-TC,LAMARQUE SUB | 1205 12.5 KV | 42.6415
82 | SUBS-MR,MERIDIAN 22KV SUB | 23205 22.0 KV | 42.1374
83 | SUBS-FI,FRIENDSWOOD SUB | 1251 12.5 KV | 41.9942
84 | SUBS-FR,DOWNTOWN SUB | 12F114 12.5 KV | 41.1838
85 | SUBS-LW,WEST SUB | 1235 12.5 KV | 40.4057
86 | SUBS-MR,MERIDIAN 22KV SUB | 23210 22.0 KV | 40.1288
87 | SUBS-MR,MERIDIAN 4KV SUB | 690 4.0 KV | 40
88 | SUBS-MR,MERIDIAN 4KV SUB | 680 4.0 KV | 40
89 | SUBS-TC,TEJAS SUB | 1215 12.5 KV | 38.836
90 | SUBS-AG,ANGLETON SUB | 1242 12.5 KV | 36.873
91 | SUBS-DC,DICKINSON SUB | 1267 12.5 KV | 36.5285
92 | SUBS-TC,LAMARQUE SUB | 1110 12.5 KV | 36.3282
93 | SUBS-AG,ANGLETON SUB | 1243 12.5 KV | 36.0681
94 | SUBS-MR,WALNUT SPRINGS 22KV | 2210 22.0 KV | 35.799
95 | SUBS-TC,NORTHSIDE SUB | 1228 12.5 KV | 35.4382
96 | SUBS-FI,ALVIN SUB | 1115 12.5 KV | 35.2043
97 | SUBS-FI,FRIENDSWOOD SUB | 1253 12.5 KV | 33.7282
98 | SUBS-TC,NORTHSIDE SUB | 1294 12.5 KV | 31.2687
99 | SUBS-GE,GLEN ROSE #3 SUB | 23875 25.0 KV | 30.7671
100 | SUBS-WC,BRAZORIA SUB | 1290 12.5 KV | 30.4448
101 | SUBS-FI,MAGNOLIA SUB | 1145 12.5 KV | 30.1534
102 | SUBS-DC,LEAGUE CITY SUB | 1284 12.5 KV | 29.8276
103 | SUBS-PI,CLIMAX SUB | 2267 22.0 KV | 29.2111
104 | SUBS-NC,NOCONA SUB | 13374 12.5 KV | 29.0128
105 | SUBS-ON,GRAHAM SUB | 1245 12.5 KV | 28.3981
106 | SUBS-DC,DICKINSON SUB | 1266 12.5 KV | 27.7591
107 | SUBS-DC,LEAGUE CITY SUB | 1282 12.5 KV | 26.9567
108 | SUBS-FR,BELDING SUB | 12F161 12.5 KV | 25.2292
109 | SUBS-DC,LEAGUE CITY SUB | 1280 12.5 KV | 24.9364
110 | SUBS-TC,NORTHSIDE SUB | 1295 12.5 KV | 24.7839
111 | SUBS-WC,SWEENY SUB | 1128 12.5 KV | 24.4556
112 | SUBS-CL,HANDLEY 22KV SUB | 22825 22.0 KV | 24.4059
113 | SUBS-WC,SWEENY SUB | 1264 12.5 KV | 24.2655
114 | SUBS-DC,DICKINSON SUB | 1279 12.5 KV | 23.3176
115 | SUBS-DC,DICKINSON SUB | 1272 12.5 KV | 23.2325
116 | SUBS-AG,ANGLETON SUB | 1244 12.5 KV | 22.9551
117 | SUBS-DC,DICKINSON SUB | 1277 12.5 KV | 22.2742
118 | SUBS-SR,THURBER 12.5KV SUB | 1447 12.5 KV | 22.1637
119 | SUBS-SR,THURBER 22KV SUB | 1490 22.0 KV | 21.8054
120 | SUBS-TC,FREEWAY PARK SUB | 1299 12.5 KV | 21.5858
121 | SUBS-NC,NOCONA SUB | 12490 12.5 KV | 21.5249
122 | SUBS-FR,16TH STREET SUB | 12F71 12.5 KV | 21.441
123 | SUBS-TC,LAMARQUE SUB | 1202 12.5 KV | 21.2298
124 | SUBS-DC,LEAGUE CITY SUB | 1285 12.5 KV | 20.7241
125 | SUBS-LW,JONES STREET SUB | 1411 12.5 KV | 20.5476
126 | EMORY TU | TU-1201 12.5 KV | 19.7633
127 | SUBS-FI,ALVIN SUB | 1117 12.5 KV | 19.3523
128 | SUBS-AG,ANGLETON SUB | 1155 12.5 KV | 18.8693
129 | SUBS-PI,CLIMAX SUB | 22110 22.0 KV | 18.6343
130 | SUBS-FI,ALVIN SUB | 1116 12.5 KV | 17.0153
131 | SUBS-CL,CLIFTON #2 22KV | 23165 22.0 KV | 17
132 | SUBS-FI,FRIENDSWOOD SUB | 1252 12.5 KV | 15.8995
133 | SUBS-WC,WEST COLUMBIA SUB | 1235 12.5 KV | 15.4881
134 | SUBS-NC,NOCONA SUB | 13610 12.5 KV | 15.4444
135 | SUBS-AG,ANGLETON SUB | 1153 12.5 KV | 15.2252
136 | SUBS-TC,LAMARQUE SUB | 1201 12.5 KV | 15.192
137 | SUBS-DC,SOUTH SHORE SUB | 1195 12.5 KV | 15.0985
138 | SUBS-FI,ALVIN SUB | 1231 12.5 KV | 14.8719
139 | SUBS-TC,NORTHSIDE SUB | 1292 12.5 KV | 14.5986
140 | SUBS-FR,16TH STREET SUB | 13F14 12.5 KV | 14.5772
141 | SUBS-FR,DOWNTOWN SUB | 12F130 12.5 KV | 14.3786
142 | SUBS-FI,MAGNOLIA SUB | 1150 12.5 KV | 14.1479
143 | SUBS-WC,WEST COLUMBIA SUB | 1237 12.5 KV | 14.0662
144 | SUBS-FI,ALVIN SUB | 1254 12.5 KV | 14.0266
145 | SUBS-SR,THURBER 22KV SUB | 22890 22.0 KV | 13.8593
146 | SUBS-PL,KRUGERVILLE SUB | 2608 25.0 KV | 13.7589
147 | SUBS-AG,ANGLETON SUB | 1245 12.5 KV | 13.7529
148 | SUBS-AG,ANGLETON SUB | 1154 12.5 KV | 13.6287
149 | SUBS-LW,WEST SUB | 1233 12.5 KV | 12.8712
150 | SUBS-WW,WHITEWRIGHT SUB | 12574 12.5 KV | 12.6316
151 | SUBS-FI,MAGNOLIA SUB | 1144 12.5 KV | 12.5483
152 | SUBS-TC,FREEWAY PARK SUB | 1102 12.5 KV | 12.2632
153 | SUBS-WC,WEST COLUMBIA SUB | 1233 12.5 KV | 12.1134
154 | SUBS-WC,SWEENY SUB | 1129 12.5 KV | 11.6539
155 | SUBS-FI,FRIENDSWOOD SUB | 1108 12.5 KV | 11.6131
156 | SUBS-TC,TEJAS SUB | 1214 12.5 KV | 11.5686
157 | SUBS-DC,SOUTH SHORE SUB | 1192 12.5 KV | 11.1983
158 | SUBS-WC,OLD OCEAN SUB | 1261 12.5 KV | 10.7673
159 | SUBS-DC,SOUTH SHORE SUB | 1190 12.5 KV | 10.5612
160 | SUBS-AG,ANGLETON SUB | 1241 12.5 KV | 10.4837
161 | SUBS-DC,LEAGUE CITY SUB | 1283 12.5 KV | 10.4484
162 | SUBS-NC,NOCONA SUB | 12486 12.5 KV | 9.8718
163 | SUBS-PC,STAFFORD SUB | 13P50 12.5 KV | 9.756
164 | SUBS-NC,SAINT JO SUB | 408 4.0 KV | 9.6537
165 | SUBS-FI,MAGNOLIA SUB | 1149 12.5 KV | 8.9799
166 | SUBS-FI,ALVIN SUB | 1259 12.5 KV | 8.7613
167 | SUBS-TC,LAMARQUE SUB | 1203 12.5 KV | 8.6382
168 | SUBS-NC,NOCONA SUB | 13370 12.5 KV | 8.5827
169 | SUBS-VL,VALLEY MILLS SUB | 22575 22.0 KV | 8.515
170 | SUBS-TC,TEJAS SUB | 1212 12.5 KV | 7.8153
171 | SUBS-GT,SYCAMORE SUB | 24105 25.0 KV | 7.7315
172 | SUBS-ON,GRAHAM SUB | 12605 12.5 KV | 7.3881
173 | SUBS-MR,WALNUT SPRINGS 12.5 | 1270 12.5 KV | 7.2727
174 | SUBS-FR,16TH STREET SUB | 12F72 12.5 KV | 7.1364
175 | SUBS-WW,BLUE RIDGE SUB | 22700 22.0 KV | 7.006
176 | SUBS-FI,ALVIN SUB | 1232 12.5 KV | 6.9721
177 | SUBS-WI,HILL CO SUB | 23340 22.0 KV | 6.9565
178 | SUBS-LW,SOUTH SUB | 1109 12.5 KV | 6.6151
179 | SUBS-TC,FREEWAY PARK SUB | 1103 12.5 KV | 6.5546
180 | SUBS-LW,WEST SUB | 1201 12.5 KV | 6.0878
181 | ELIASVILLE POD | 1300 12.5 KV | 6.0123
182 | SUBS-HM,HAMILTON COUNTY SUB | 2345 2.4 KV | 5.3879
183 | SUBS-PC,COCHISE SUB | 25P48 25.0 KV | 5.2403
184 | SUBS-TC,HEIGHTS SUB | 1222 12.5 KV | 4.6429
185 | SUBS-PC,PECOS MAIN SUB | 12P362 12.5 KV | 4.6192
186 | SUBS-HM,HAMILTON COUNTY SUB | 24015 25.0 KV | 4.4615
187 | SUBS-TC,FREEWAY PARK SUB | 1101 12.5 KV | 4.0475
188 | SUBS-GT,GATESVILLE #1 4KV | 422 4.0 KV | 4
189 | SUBS-HM,HAMILTON CITY #1 22 | 22780 22.0 KV | 3.9707
190 | SUBS-TC,HEIGHTS SUB | 1224 12.5 KV | 3.9405
191 | SUBS-ON,OLNEY SWCH STA | 1685 12.5 KV | 3.6678
192 | SUBS-LW,TI SUB | 1032 12.5 KV | 3.3111
193 | SUBS-TC,HEIGHTS SUB | 1134 12.5 KV | 3.1998
194 | SUBS-LO,LEONARD SUB | 12682 12.5 KV | 3.1698
195 | SUBS-NC,SAINT JO SUB | 401 4.0 KV | 2.9805
196 | SUBS-CL,LAKE WHITNEY SUB | 12355 12.5 KV | 2.9258
197 | SUBS-PC,PECOS MAIN SUB | 12P03 12.5 KV | 2.7031
198 | SUBS-FR,AIRPORT SUB | 12F271 12.5 KV | 2.6265
199 | SUBS-KR,KERMIT NO. 2 SUB | 12K48 12.5 KV | 2.5975
200 | SUBS-TC,TEJAS SUB | 1217 12.5 KV | 2.5668
201 | SUBS-GT,GATESVILLE #2 SUB | 22725 22.0 KV | 2.5229
202 | SUBS-LW,WEST SUB | 1203 12.5 KV | 2.4967
203 | SUBS-WI,WHITNEY #2 SUB | 22460 22.0 KV | 2.4373
204 | SUBS-FR,AIRPORT SUB | 12F44 12.5 KV | 2.3814
205 | SUBS-LW,SOUTH SUB | 1107 12.5 KV | 2.1784
206 | SUBS-BR,BRYSONS SUB | 1230 12.5 KV | 2.1599
207 | SUBS-LW,JONES STREET SUB | 1413 12.5 KV | 2.147
208 | SUBS-LW,LAKEPOINTE SUB | 2516 25.0 KV | 2.0638
209 | SUBS-PC,PECOS MAIN SUB | 2P03 2.4 KV | 2.0571
210 | SUBS-WC,SWEENY SUB | 1263 12.5 KV | 2.0311
211 | SUBS-GT,GATESVILLE #2 SUB | 23065 22.0 KV | 1.8182
212 | SUBS-LW,TI SUB | 1033 12.5 | 1.6341
213 | SUBS-FR,DOWNTOWN SUB | 4F52 4.0 KV | 1.5657
214 | SUBS-MR,WALNUT SPRINGS 22KV | 2200 22.0 KV | 1.3268
215 | SUBS-ON,OLNEY SWCH STA | 1431 12.5 KV | 1.2372
216 | SUBS-HM,HAMILTON CITY #2 22 | 23825 25.0 KV | 1.2
217 | SUBS-BG,RED RIVER SUB | 2229 22.0 KV | 1.0976
218 | SUBS-WW,WHITEWRIGHT SUB | 12698 12.5 KV | 0.9967
219 | SUBS-LW,SOUTH SUB | 1108 12.5 KV | 0.9905
220 | SUBS-PC,STAFFORD SUB | 12P82 12.5 KV | 0.9496
221 | SUBS-GT,CORYELL CO #1 SUB | 22160 22.0 KV | 0.597
222 | SUBS-WI,WHITNEY #1 SUB | 22450 22.0 KV | 0.5189
223 | SUBS-LO,LEONARD SUB | 14631 12.5 KV | 0.5128
224 | SUBS-GT,GATESVILLE #1 4KV | 419 4.0 KV | 0.4858
225 | SUBS-CL,CLIFTON #1 4KV SUB | 407 4.0 KV | 0.4149
226 | SUBS-ON,OLNEY SWCH STA | 1690 12.5 KV | 0.4144
227 | SUBS-CL,LAKE WHITNEY SUB | 1230 12.5 KV | 0.3631
228 | SUBS-LO,LEONARD SUB | 14635 12.5 KV | 0.2151
229 | SUBS-MR,WALNUT SPRINGS 22KV | 2215 22.0 KV | 0.1982
230 | SUBS-KR,KERMIT NO. 2 SUB | 12K98 12.5 KV | 0.1919
231 | SUBS-KR,KERMIT NO. 2 SUB | 4K06 4.0 KV | 0.1875
232 | SUBS-WI,WHITNEY #1 SUB | 22455 22.0 KV | 0.185
233 | SUBS-WW,WHITEWRIGHT SUB | 12575 12.5 KV | 0.0965
234 | SUBS-GT,CORYELL #1 SUB | 22155 22.0 KV | 0.0507
235 | SUBS-CL,CLIFTON #2 4KV | 4160 4.0 KV | 0
236 | SUBS-CL,CLIFTON #2 4KV | 4165 4.0 KV | 0
237 | SUBS-CL,CLIFTON #1 22 KV | 22485 22.0 KV | 0
238 | SUBS-CL,CLIFTON #1 22 KV | 22495 22.0 KV | 0
239 | SUBS-CL,CLIFTON #1 4KV SUB | 405 4.0 KV | 0
240 | SUBS-CL,CLIFTON #1 4KV SUB | 490 4.0 KV | 0
241 | SUBS-CL,HANDLEY 22KV SUB | 22820 22.0 KV | 0
242 | SUBS-GT,GATESVILLE #1 4KV | 413 4.0 KV | 0
243 | SUBS-GT,GATESVILLE #2 4KV | 426 4.0 KV | 0
244 | SUBS-GT,GATESVILLE #2 4KV | 429 4.0 KV | 0
245 | SUBS-GT,SYCAMORE SUB | 24100 25.0 KV | 0
246 | SUBS-VL,VALLEY MILLS SUB | 22565 22.0 KV | 0
247 | SUBS-WI,WHITNEY #2 SUB | 22469 22.0 KV | 0
248 | SUBS-LW,LAKEPOINTE SUB | 2512 25.0 KV | 0
249 | SUBS-LW,LAKEPOINTE SUB | 2532 25.0 KV | 0
250 | SUBS-LW,WEST SUB | 1202 12.5 KV | 0
251 | SUBS-EO,LONE OAK SUB | 13388 12.5 KV | 0
252 | SUBS-LO,FRONTIER SUB | 4236 4.0 KV | 0
253 | SUBS-LO,TRENTON SUB | 4120 4.0 KV | 0
254 | SUBS-WW,WHITEWRIGHT SUB | 12753 12.5 KV | 0
255 | SUBS-WW,WHITEWRIGHT SUB | 13563 12.5 KV | 0
256 | SUBS-KR,KERMIT NO. 2 SUB | 4K07 4.0 KV | 0
257 | SUBS-KR,WINKLER CO. NO.6 SUB | 25K11 25.0 KV | 0
258 | SUBS-PC,PECOS MAIN SUB | 2P04 2.4 KV | 0
259 | SUBS-PC,PECOS MAIN SUB | 2P05 2.5 KV | 0
260 | SUBS-PC,PECOS MAIN SUB | 2P06 2.4 KV | 0
261 | SUBS-PC,STAFFORD SUB | 12P50 12.5 KV | 0
262 | SUBS-PC,STAFFORD SUB | 12P99 12.5 KV | 0
263 | SUBS-FR,GOMEZ SUB | 25F61 25.0 KV | 0
264 | SUBS-CL,CLIFTON#2 22KV | 24370 22.0 | 0

## Causes
TEXAS-NEW MEXICO POWER COMPANY
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 28.47%
|  | Vegetation | 11.49%
|  | Animals and Birds | 19.47%
|  | People (Including cars and farm equip) | 5.98%
|  | Utility-owned Equipment | 27.42%
|  | Other | 1.63%
|  | Unknown | 5.6%