## Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | Austin Energy - corrected version 2/18/2000
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 222
Due: |  | February 15, 2000
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 21972
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Industry Analysis Division
Office of Regulatory Affairs
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mel.eckhoff@puc.state.tx.us

## Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
1998 And 1999
Austin Energy - corrected version 2/18/2000
Project 21972

## System-SAIFI
Austin Energy - corrected version 2/18/2000
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 0.86185 | 0.043483 | 0.051547 | 0.10769 | 0.051982 | 0.044016 | 0.066308 | 0.080917 | 0.14499 | 0.073561 | 0.080702 | 0.032204 | 0.084454
1999 | 0.77077 | 0.020024 | 0.027356 | 0.079857 | 0.04592 | 0.15259 | 0.050614 | 0.087922 | 0.059285 | 0.049784 | 0.046953 | 0.078768 | 0.071693
Scheduled
1998 | 0.018008 | 0.0022122 | 0.0021121 | 0.0016313 | 0.0018464 | 0.00081863 | 0.0013719 | 0.0013622 | 0.0021584 | 0.00077249 | 0.00058537 | 0.0026592 | 0.00047787
1999 | 0.0096189 | 0.00071483 | 0.00056685 | 0.0014072 | 0.0012013 | 0.00035784 | 0.00071632 | 0.0009764 | 0.00043242 | 0.00062226 | 0.00050146 | 0.00032845 | 0.0017935
Outside Causes
1998 | 0.25569 | 0.0086189 | 0.0083923 | 0.027114 | 0.023911 | 0.035643 | 0.029799 | 0.049259 | 0.0083938 | 0.022027 | 0.037913 | 0.0046229 | 0
1999 | 0.1418 | 0 | 0.01203 | 0.067959 | 0 | 0.04906 | 0.0023081 | 0 | 0 | 0 | 0 | 0.010443 | 0
Major Events
1998
1999

## System-SAIDI
Austin Energy - corrected version 2/18/2000
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
1998 | 62.4794 | 2.613 | 2.2756 | 6.8437 | 3.0392 | 3.8466 | 3.8693 | 6.2913 | 15.4472 | 4.2853 | 5.1109 | 2.5021 | 6.3552
1999 | 54.8998 | 1.1457 | 1.4092 | 5.8689 | 3.3734 | 15.6571 | 3.4154 | 5.6664 | 4.0795 | 2.8235 | 4.1681 | 3.5147 | 3.7779
Scheduled
1998 | 1.5256 | 0.24398 | 0.20711 | 0.096334 | 0.161 | 0.089418 | 0.14154 | 0.10844 | 0.1417 | 0.063744 | 0.037547 | 0.16251 | 0.072303
1999 | 0.8381 | 0.068912 | 0.053638 | 0.14562 | 0.17571 | 0.028102 | 0.048966 | 0.035809 | 0.043753 | 0.044379 | 0.044012 | 0.021997 | 0.1272
Outside Causes
1998 | 10.2885 | 0.25857 | 0.075531 | 1.0323 | 1.2718 | 2.4159 | 0.96412 | 2.7025 | 0.36224 | 0.83867 | 0.18957 | 0.17732 | 0
1999 | 3.4509 | 0 | 0.45005 | 0.40775 | 0 | 1.5044 | 0.37055 | 0 | 0 | 0 | 0 | 0.71813 | 0
Major Events
1998
1999

## Feeder-SAIFI
List all Distribution Feeders on Texas System |  |  | Total Number of Feeders
Add or Delete Rows as Necessary |  |  | 222
Austin Energy - corrected version 2/18/2000
1999 SAIFI Ranking | Substation Identification | Feeder Identification | 1999 SAIFI Value
1 | Seaholm Plant | SP05 | 5.1159
2 | Cameron | CM01 | 4.1277
3 | Koenig Lane | KL03 | 3.2527
4 | Northland | NL14 | 3.2391
5 | Pedernales | PE02 | 3.2244
6 | Seaholm Plant | SP06 | 3.1391
7 | Cardinal Lane | CL08 | 3.0956
8 | Riverplace | RP05 | 3.0435
9 | Bergstrom | BE04 | 3
10 | Salem Walk | SW02 | 2.6247
11 | Northland | NL11 | 2.6086
12 | Lakeway | LW04 | 2.5054
13 | Oak Hill | OH03 | 2.4267
14 | Koenig Lane | KL01 | 2.3986
15 | North | NO01 | 2.3923
16 | Kingsbery | KB03 | 2.3652
17 | Bee Creek | BC06 | 2.3063
18 | Burleson | BU09 | 2.2826
19 | Pedernales | PE01 | 2.2163
20 | Jollyville | JV04 | 2.1885
21 | Pedernales | PE04 | 2.1313
22 | Commons Ford | CF02 | 2.1312
23 | Howard Lane | HL03 | 2.0952
24 | Summit | SU05 | 2.0873
25 | Commons Ford | CF05 | 2.07
26 | Williamson | WI11 | 2.0319
27 | Seaholm Plant | SP04 | 1.8462
28 | Northland | NL01 | 1.7022
29 | Commons Ford | CF04 | 1.6729
30 | Wheless Lane | WL01 | 1.6472
31 | Patton Lane | PL02 | 1.6399
32 | Bergstrom | BE02 | 1.638
33 | Cameron | CM05 | 1.6304
34 | Bee Creek | BC05 | 1.5978
35 | Hi-Cross | HC06 | 1.502
36 | Slaughter Lane | SL05 | 1.4532
37 | Brodie Lane | BL04 | 1.4485
38 | Cardinal Lane | CL11 | 1.4307
39 | Williamson | WI09 | 1.4255
40 | Warren | WA01 | 1.4052
41 | Pedernales | PE05 | 1.4027
42 | Salem Walk | SW07 | 1.3739
43 | Austin Dam | AD02 | 1.3398
44 | Brodie Lane | BL01 | 1.3346
45 | Austin Dam | AD01 | 1.3296
46 | North | NO02 | 1.2962
47 | Slaughter Lane | SL04 | 1.281
48 | Slaughter Lane | SL01 | 1.2701
49 | Brodie Lane | BL05 | 1.2334
50 | Jett | JE06 | 1.2323
51 | Cardinal Lane | CL09 | 1.227
52 | Northland | NL08 | 1.2244
53 | Oak Hill | OH02 | 1.2122
54 | Magnesium Plant | MP06 | 1.2095
55 | Fiskville | FV03 | 1.2048
56 | Commons Ford | CF01 | 1.1832
57 | Zilker | ZL02 | 1.1798
58 | Magnesium Plant | MP03 | 1.1589
59 | Warren | WA05 | 1.1532
60 | Jollyville | JV03 | 1.1333
61 | Magnesium Plant | MP02 | 1.1298
62 | Steck | ST04 | 1.1224
63 | McNeil | MC07 | 1.1103
64 | Cardinal Lane | CL03 | 1.1019
65 | Slaughter Lane | SL02 | 1.1005
66 | Koenig Lane | KL12 | 1.0884
67 | Howard Lane | HL04 | 1.0824
68 | Koenig Lane | KL08 | 1.0753
69 | Carson Creek | CC06 | 1.0612
70 | Jett | JE03 | 1.0565
71 | Magnesium Plant | MP05 | 1.046
72 | Williamson | WI05 | 1.0098
73 | Oak Hill | OH05 | 1.0091
74 | Brodie Lane | BL03 | 1.0086
75 | Williamson | WI10 | 1
76 | Walnut Creek | WC07 | 0.9582
77 | Steck | ST05 | 0.80109
78 | Warren | WA04 | 0.78481
79 | Pedernales | PE09 | 0.75636
80 | Seaholm Plant | SP09 | 0.69059
81 | Bee Creek | BC02 | 0.64089
82 | Bergstrom | BE06 | 0.63742
83 | Summit | SU02 | 0.63497
84 | Northland | NL02 | 0.63109
85 | Northland | NL15 | 0.61284
86 | Patton Lane | PL01 | 0.60225
87 | Walnut Creek | WC08 | 0.54915
88 | Burleson | BU07 | 0.54516
89 | Howard Lane | HL01 | 0.52998
90 | Koenig Lane | KL06 | 0.52878
91 | Warren | WA02 | 0.52392
92 | Hi-Cross | HC09 | 0.5015
93 | Hi-Cross | HC01 | 0.49263
94 | Salem Walk | SW08 | 0.4824
95 | Wheless Lane | WL04 | 0.48096
96 | Koenig Lane | KL14 | 0.47856
97 | Fiskville | FV05 | 0.47731
98 | North | NO04 | 0.46836
99 | Cardinal Lane | CL01 | 0.44922
100 | Koenig Lane | KL10 | 0.43842
101 | Wheless Lane | WL02 | 0.42317
102 | Steck | ST06 | 0.421
103 | Onion Creek | OC02 | 0.41587
104 | Steck | ST02 | 0.39692
105 | Salem Walk | SW06 | 0.38848
106 | Sprinkle | SK02 | 0.38542
107 | Magnesium Plant | MP09 | 0.37157
108 | Fiskville | FV06 | 0.36227
109 | Carson Creek | CC05 | 0.34715
110 | Magnesium Plant | MP07 | 0.32749
111 | Salem Walk | SW05 | 0.32718
112 | Cardinal Lane | CL12 | 0.3143
113 | Lakeshore | LS01 | 0.3086
114 | Seaholm Plant | SP07 | 0.30769
115 | Zilker | ZL03 | 0.30725
116 | Salem Walk | SW04 | 0.29806
117 | Warren | WA06 | 0.29705
118 | Jollyville | JV02 | 0.2969
119 | Dessau | DE01 | 0.28167
120 | Jollyville | JV05 | 0.27995
121 | Kingsbery | KB05 | 0.27913
122 | Salem Walk | SW01 | 0.27849
123 | Lakeway | LW03 | 0.2753
124 | Steck | ST01 | 0.27438
125 | Lakeway | LW02 | 0.26791
126 | Sprinkle | SK03 | 0.26562
127 | Bergstrom | BE05 | 0.26135
128 | Northland | NL12 | 0.25974
129 | Fiskville | FV01 | 0.25795
130 | Bee Creek | BC03 | 0.25681
131 | Bergstrom | BE03 | 0.25144
132 | Burleson | BU01 | 0.24837
133 | Warren | WA03 | 0.23733
134 | Seaholm Plant | SP02 | 0.23558
135 | Onion Creek | OC04 | 0.2296
136 | Burleson | BU02 | 0.22951
137 | North | NO08 | 0.22844
138 | Jett | JE04 | 0.22684
139 | Austin Dam | AD05 | 0.21704
140 | Daffin Gin | DG01 | 0.21286
141 | McNeil | MC02 | 0.21252
142 | Angus Valley | AG02 | 0.207
143 | Cardinal Lane | CL07 | 0.19738
144 | Barton | BA03 | 0.19693
145 | Carson Creek | CC02 | 0.19333
146 | Howard Lane | HL02 | 0.19281
147 | Cameron | CM04 | 0.18213
148 | Walnut Creek | WC10 | 0.1743
149 | Kingsbery | KB04 | 0.17
150 | Barton | BA01 | 0.16667
151 | Hamilton | HM11 | 0.16667
152 | Koenig Lane | KL13 | 0.16292
153 | McNeil | MC08 | 0.16261
154 | Cardinal Lane | CL04 | 0.15942
155 | Cameron | CM06 | 0.15636
156 | Hi-Cross | HC03 | 0.15579
157 | Burleson | BU05 | 0.15385
158 | Seaholm Plant | SP01 | 0.14899
159 | Cardinal Lane | CL06 | 0.14648
160 | McNeil | MC05 | 0.14551
161 | Pedernales | PE07 | 0.14089
162 | Barton | BA07 | 0.13606
163 | Barton | BA04 | 0.13451
164 | North | NO07 | 0.13343
165 | Burleson | BU04 | 0.13333
166 | Wheless Lane | WL06 | 0.13125
167 | Koenig Lane | KL07 | 0.12881
168 | North | NO06 | 0.12731
169 | Barton | BA02 | 0.12716
170 | McNeil | MC06 | 0.127
171 | Riverplace | RP04 | 0.12698
172 | Angus Valley | AG03 | 0.12682
173 | Kingsbery | KB06 | 0.12635
174 | Lakeshore | LS06 | 0.11976
175 | Barton | BA05 | 0.11848
176 | Summit | SU06 | 0.11792
177 | Lakeshore | LS04 | 0.11268
178 | Burleson | BU06 | 0.11127
179 | Hamilton | HM03 | 0.11
180 | Sprinkle | SK01 | 0.10535
181 | Hi-Cross | HC08 | 0.10508
182 | Burleson | BU08 | 0.10179
183 | Hamilton | HM10 | 0.096154
184 | Cameron | CM02 | 0.096005
185 | Williamson | WI04 | 0.090137
186 | Williamson | WI02 | 0.089269
187 | Summit | SU03 | 0.083595
188 | Steck | ST03 | 0.083216
189 | Williamson | WI01 | 0.080371
190 | Kingsbery | KB01 | 0.077197
191 | McNeil | MC01 | 0.075743
192 | Howard Lane | HL05 | 0.074935
193 | Daffin Gin | DG02 | 0.073171
194 | Wheless Lane | WL03 | 0.071902
195 | Hi-Cross | HC05 | 0.068421
196 | Jollyville | JV07 | 0.06768
197 | Burleson | BU03 | 0.066667
198 | Wheless Lane | WL05 | 0.066406
199 | Commons Ford | CF03 | 0.064286
200 | Barton | BA09 | 0.061073
201 | Cameron | CM03 | 0.056243
202 | Hamilton | HM09 | 0.053103
203 | Oak Hill | OH04 | 0.051256
204 | Brodie Lane | BL02 | 0.045921
205 | Jett | JE02 | 0.041012
206 | Hamilton | HM01 | 0.040736
207 | Oak Hill | OH06 | 0.040433
208 | North | NO05 | 0.038298
209 | Hamilton | HM05 | 0.033631
210 | Northland | NL13 | 0.033423
211 | Jollyville | JV08 | 0.032457
212 | Williamson | WI06 | 0.027515
213 | Williamson | WI08 | 0.023942
214 | Howard Lane | HL06 | 0.02024
215 | Fiskville | FV02 | 0.018443
216 | Williamson | WI07 | 0.015544
217 | Barton | BA08 | 0.012397
218 | Summit | SU01 | 0.011161
219 | Hamilton | HM04 | 0.0073099
220 | Hamilton | HM08 | 0.0044944
221 | North | NO09 | 0.0030211
222 | Summit | SU04 | 0.0013167

## Feeder-SAIDI
List all Distribution Feeders on Texas System |  |  | Total Number of Feeders
Add or Delete Rows as Necessary |  |  | 222
Austin Energy - corrected version 2/18/2000
1999 SAIDI Ranking | Substation Identification | Feeder Identification | 1999 SAIDI Value
1 | Northland | NL14 | 316.9861
2 | Bergstrom | BE04 | 304
3 | Cameron | CM01 | 271.5195
4 | Riverplace | RP05 | 245.2757
5 | Oak Hill | OH03 | 240.6817
6 | Koenig Lane | KL03 | 204.8707
7 | Lakeway | LW04 | 203.0496
8 | Commons Ford | CF02 | 197.8768
9 | McNeil | MC07 | 188.3316
10 | Seaholm Plant | SP05 | 185.9592
11 | Warren | WA04 | 175.5949
12 | Bergstrom | BE02 | 170.8235
13 | Salem Walk | SW02 | 165.0874
14 | Pedernales | PE04 | 162.3173
15 | Pedernales | PE02 | 160.1673
16 | Koenig Lane | KL01 | 158.3719
17 | Warren | WA05 | 153.7548
18 | Northland | NL01 | 152.6121
19 | Bergstrom | BE06 | 149.5577
20 | Cardinal Lane | CL08 | 149.2222
21 | Patton Lane | PL02 | 145.9349
22 | Oak Hill | OH02 | 136.2002
23 | Bee Creek | BC06 | 128.2505
24 | Cardinal Lane | CL11 | 126.9507
25 | Northland | NL11 | 125.49
26 | Cardinal Lane | CL03 | 124.1604
27 | Slaughter Lane | SL05 | 124.1408
28 | Wheless Lane | WL01 | 123.6328
29 | Jollyville | JV04 | 122.2573
30 | Walnut Creek | WC07 | 122.0482
31 | Jett | JE03 | 120.9073
32 | Walnut Creek | WC08 | 120.8974
33 | Bee Creek | BC05 | 119.5093
34 | Williamson | WI09 | 118.0671
35 | North | NO01 | 117.3844
36 | Burleson | BU09 | 109.4305
37 | Cameron | CM05 | 107.7063
38 | Summit | SU05 | 105.8891
39 | Northland | NL15 | 101.9963
40 | Pedernales | PE05 | 101.2003
41 | Pedernales | PE01 | 100.9813
42 | Seaholm Plant | SP09 | 100.8094
43 | Magnesium Plant | MP05 | 99.3685
44 | Brodie Lane | BL01 | 95.9769
45 | Brodie Lane | BL04 | 93.5556
46 | Commons Ford | CF01 | 91.4503
47 | Williamson | WI11 | 86.9962
48 | Commons Ford | CF04 | 86.6275
49 | Salem Walk | SW08 | 86.2302
50 | North | NO04 | 83.669
51 | Howard Lane | HL03 | 83.0107
52 | Hi-Cross | HC01 | 82.5521
53 | Jollyville | JV03 | 81.7954
54 | Northland | NL02 | 81.1171
55 | Slaughter Lane | SL04 | 78.7018
56 | Jett | JE06 | 78.6263
57 | Commons Ford | CF05 | 74.9365
58 | Hi-Cross | HC09 | 70.4252
59 | Austin Dam | AD02 | 69.7424
60 | Warren | WA01 | 68.5183
61 | Steck | ST05 | 67.168
62 | Cardinal Lane | CL09 | 66.6026
63 | Northland | NL08 | 66.0997
64 | Steck | ST06 | 64.9385
65 | Seaholm Plant | SP04 | 64.6923
66 | Kingsbery | KB03 | 62.8208
67 | Koenig Lane | KL14 | 62.7897
68 | Koenig Lane | KL10 | 62.7855
69 | Hi-Cross | HC06 | 61.7464
70 | Barton | BA03 | 61.255
71 | Steck | ST02 | 59.4208
72 | Salem Walk | SW01 | 58.615
73 | Slaughter Lane | SL01 | 58.3382
74 | North | NO02 | 56.21
75 | Pedernales | PE09 | 55.4345
76 | Austin Dam | AD01 | 55.0342
77 | Salem Walk | SW05 | 54.6096
78 | Slaughter Lane | SL02 | 53.6141
79 | Bee Creek | BC02 | 53.5241
80 | Carson Creek | CC06 | 52.3863
81 | Wheless Lane | WL02 | 52.0688
82 | Zilker | ZL03 | 51.5989
83 | Howard Lane | HL01 | 49.518
84 | Seaholm Plant | SP06 | 47.4047
85 | Summit | SU02 | 47.1825
86 | Koenig Lane | KL06 | 46.1405
87 | Warren | WA02 | 45.8182
88 | Howard Lane | HL04 | 44.1898
89 | Fiskville | FV03 | 43.881
90 | McNeil | MC02 | 43.1387
91 | Williamson | WI05 | 42.9412
92 | Fiskville | FV05 | 42.6453
93 | Seaholm Plant | SP02 | 42.2949
94 | Seaholm Plant | SP07 | 41.9115
95 | Salem Walk | SW07 | 41.8967
96 | Cardinal Lane | CL12 | 40.4926
97 | Sprinkle | SK02 | 40.3021
98 | Magnesium Plant | MP02 | 40.2981
99 | Carson Creek | CC05 | 39.4145
100 | Fiskville | FV06 | 38.7741
101 | Riverplace | RP04 | 38.3942
102 | Koenig Lane | KL08 | 38.2831
103 | Sprinkle | SK03 | 37.6052
104 | Salem Walk | SW06 | 35.7511
105 | Lakeshore | LS01 | 35.5665
106 | Cardinal Lane | CL07 | 35.3152
107 | Magnesium Plant | MP03 | 35.288
108 | Patton Lane | PL01 | 35.0668
109 | Burleson | BU07 | 34.9658
110 | Salem Walk | SW04 | 34.8735
111 | Bee Creek | BC03 | 33.9495
112 | Williamson | WI10 | 33
113 | Onion Creek | OC02 | 32.3834
114 | Wheless Lane | WL04 | 31.7024
115 | Lakeway | LW02 | 31.1429
116 | Jollyville | JV05 | 31.1131
117 | Daffin Gin | DG01 | 30.5633
118 | Cameron | CM06 | 30.3911
119 | Jollyville | JV02 | 30.0685
120 | Lakeway | LW03 | 29.6445
121 | Steck | ST01 | 29.4322
122 | Warren | WA06 | 29.3143
123 | Bergstrom | BE05 | 27.7095
124 | McNeil | MC08 | 27.5334
125 | Zilker | ZL02 | 27.2551
126 | Magnesium Plant | MP07 | 27.2419
127 | Howard Lane | HL05 | 26.2196
128 | Walnut Creek | WC10 | 25.8368
129 | Cardinal Lane | CL01 | 25.4554
130 | Northland | NL12 | 23.8979
131 | Onion Creek | OC04 | 23.6028
132 | Barton | BA04 | 23.163
133 | Magnesium Plant | MP06 | 23.0637
134 | Jett | JE04 | 22.7869
135 | Kingsbery | KB05 | 22.0898
136 | Kingsbery | KB04 | 21.905
137 | Brodie Lane | BL03 | 21.5161
138 | Carson Creek | CC02 | 21.0733
139 | Burleson | BU01 | 20.2672
140 | North | NO08 | 20.2313
141 | Bergstrom | BE03 | 20.0029
142 | Warren | WA03 | 20.0023
143 | Hi-Cross | HC03 | 19.9855
144 | McNeil | MC05 | 19.7137
145 | Steck | ST04 | 19.0495
146 | Magnesium Plant | MP09 | 19.049
147 | Cameron | CM04 | 19.0234
148 | Howard Lane | HL02 | 18.4679
149 | Brodie Lane | BL05 | 18.2912
150 | Burleson | BU06 | 17.9803
151 | Oak Hill | OH05 | 17.98
152 | Burleson | BU08 | 17.1361
153 | Dessau | DE01 | 17.0683
154 | Austin Dam | AD05 | 16.8022
155 | Angus Valley | AG03 | 16.6298
156 | Koenig Lane | KL13 | 16.5955
157 | Hamilton | HM03 | 15.473
158 | Pedernales | PE07 | 15.1025
159 | Fiskville | FV01 | 14.5027
160 | Barton | BA01 | 13.7843
161 | Seaholm Plant | SP01 | 12.6944
162 | North | NO07 | 12.4249
163 | Burleson | BU04 | 12.2833
164 | Williamson | WI04 | 12.2442
165 | Koenig Lane | KL12 | 12.068
166 | Barton | BA02 | 12.0493
167 | Steck | ST03 | 12.0085
168 | Lakeshore | LS04 | 11.8028
169 | Angus Valley | AG02 | 11.4607
170 | Barton | BA05 | 11.0576
171 | Cameron | CM03 | 11.0045
172 | Sprinkle | SK01 | 10.5361
173 | Lakeshore | LS06 | 9.8084
174 | Burleson | BU02 | 9.7705
175 | Koenig Lane | KL07 | 9.4506
176 | Hamilton | HM11 | 9.4086
177 | Burleson | BU05 | 9.3846
178 | Cardinal Lane | CL04 | 9.311
179 | Kingsbery | KB06 | 9.2499
180 | North | NO06 | 9.1355
181 | McNeil | MC01 | 9.0964
182 | Barton | BA07 | 8.4629
183 | Hamilton | HM10 | 8.4375
184 | Summit | SU06 | 8.2028
185 | Commons Ford | CF03 | 8.0286
186 | Cardinal Lane | CL06 | 8.0092
187 | Wheless Lane | WL06 | 8
188 | Hi-Cross | HC08 | 7.9635
189 | Jollyville | JV07 | 7.5304
190 | McNeil | MC06 | 6.7703
191 | Cameron | CM02 | 6.5754
192 | Burleson | BU03 | 6.2583
193 | Williamson | WI02 | 5.9921
194 | Daffin Gin | DG02 | 5.8049
195 | Hi-Cross | HC05 | 5.6662
196 | Williamson | WI01 | 5.6207
197 | Kingsbery | KB01 | 5.5428
198 | Wheless Lane | WL05 | 5.3945
199 | Williamson | WI06 | 5.1423
200 | Hamilton | HM09 | 5.111
201 | Summit | SU03 | 5.0679
202 | Hamilton | HM05 | 4.779
203 | Oak Hill | OH04 | 4.4587
204 | Wheless Lane | WL03 | 4.3442
205 | Northland | NL13 | 4.1356
206 | Barton | BA09 | 4.0439
207 | Williamson | WI08 | 3.6849
208 | North | NO05 | 3.5702
209 | Brodie Lane | BL02 | 3.4931
210 | Jett | JE02 | 3.1606
211 | Hamilton | HM01 | 2.6813
212 | Jollyville | JV08 | 2.476
213 | Fiskville | FV02 | 2.4559
214 | Williamson | WI07 | 2.2228
215 | Oak Hill | OH06 | 1.5653
216 | Howard Lane | HL06 | 1.2789
217 | Barton | BA08 | 0.89256
218 | Summit | SU01 | 0.72321
219 | Hamilton | HM04 | 0.60234
220 | Hamilton | HM08 | 0.3236
221 | Summit | SU04 | 0.11389
222 | North | NO09 | 0.096677

## Causes
Austin Energy - corrected version 2/18/2000
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 18.8%
|  | Vegetation | 12.22%
|  | Animals and Birds | 24.7%
|  | People (Including cars and farm equip) | 4.41%
|  | Utility-owned Equipment | 18.92%
Other
|  | Unknown | 20.95%