## Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | El Paso Electric Company
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 226
Due: |  | February 14, 2001
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 23436
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Division
Commission Staff
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mailto:mel.eckhoff@puc.state.tx.us

## Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
2000 Reporting Year
El Paso Electric Company
Project 23436

## System-SAIFI
El Paso Electric Company
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2000 | 0.37728 | 0.01667 | 0.015081 | 0.039152 | 0.01516 | 0.030295 | 0.045359 | 0.10501 | 0.05125 | 0.018492 | 0.022548 | 0.014749 | 0.0062656
Scheduled
2000 | 0.040757 | 0.0070213 | 0.0011436 | 0.0010308 | 0.0010573 | 0.0012518 | 0.0015156 | 0.0055576 | 0.001295 | 0.0064452 | 0.013329 | 0.00082948 | 0.00053293
Outside Causes
2000 | 0.68576 | 4.3774e-05 | 4.3665e-06 | 0.58493 | 0 | 0 | 0.012919 | 0.0030967 | 0.042414 | 2.5836e-05 | 0.048017 | 0.0022907 | 0
Major Events
2000 | 0.010994 | 0 | 0 | 0 | 0 | 0.011091 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## System-SAIDI
El Paso Electric Company
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2000 | 41.2495 | 1.6138 | 0.94675 | 2.5284 | 1.7913 | 2.6067 | 6.9015 | 12.3159 | 5.479 | 1.7715 | 3.2789 | 1.2142 | 1.0799
Scheduled
2000 | 1.6754 | 0.53601 | 0.057082 | 0.048839 | 0.074208 | 0.062684 | 0.1002 | 0.080903 | 0.060054 | 0.17571 | 0.39236 | 0.063795 | 0.038169
Outside Causes
2000 | 26.5844 | 0.001751 | 0.00048905 | 17.8398 | 0 | 0 | 1.2118 | 0.093604 | 3.6681 | 0.0062006 | 3.9536 | 0.071013 | 0
Major Events
2000 | 2.1896 | 0 | 0 | 0 | 0 | 2.2091 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Feeder-SAIFI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System |  |  |  |  | Total Number of Feeders
With More Than 10 Customers |  |  |  |  | 226
Add or Delete Rows as Necessary
El Paso Electric Company
2000 SAIFI Ranking | 1999 SAIFI Ranking* | Substation Identification | Feeder Identification | Number of Customers | 2000 SAIFI Value
1 | 9 | SIERRA BLANCA | 20 | 418 | 3.0646
2 | 37 | FRESNO | 01 | 236.1826 | 2.2991
3 | 226 | VISCOUNT | 12 | 2242.6993 | 2.1813
4 | 7 | MILAGRO | 11 | 1114.6164 | 2.12
5 | 53 | CINECUE | 01 | 472.3653 | 2.0408
6 | 111 | SHEARMAN | 12 | 2649.8036 | 1.9813
7 | 88 | SIERRA BLANCA | 01 | 109.8042 | 1.9307
8 | 57 | ASCARATE | 10 | 1435.7419 | 1.8994
9 | 44 | MULBERRY | 01 | 100.4812 | 1.5824
10 | 91 | SCOTSDALE | 16 | 1129.1188 | 1.5729
11 | 49 | COYOTE | 10 | 1564.1921 | 1.441
12 | 34 | LANE | 11 | 1244.1025 | 1.409
13 | 40 | HORIZON | 11 | 1728.8984 | 1.3922
14 | 42 | ALTURA | 04 | 357.3816 | 1.3459
15 | 41 | MISSION | 01 | 322.1614 | 1.3347
16 | 28 | SUNSET | 13 | 25 | 1.32
17 | 13 | MONTOYA | 20 | 1923.6455 | 1.3007
18 | 141 | CLINT | 01 | 828.711 | 1.2827
19 | 79 | LA TUNA | 01 | 74.584 | 1.2067
20 | 115 | MILAGRO | 13 | 2753.3924 | 1.168
21 | 94 | RANCHLAND | 01 | 264.1516 | 1.1546
22 | 97 | THORN | 14 | 2391.8672 | 1.1539
23 | 54 | VALLEY | 10 | 2166.0435 | 1.1533
24 | 43 | FRONTERA | 01 | 257.9363 | 1.1514
25 | 216 | MONTOYA | 22 | 11.3948 | 1.1409
26 | 81 | VISTA | 10 | 2250.9864 | 1.1373
27 | 30 | WRANGLER | 14 | 458.8987 | 1.1288
28 | 48 | LOMALAND | 01 | 416.4273 | 1.1262
29 | 128 | DYER | 13 | 2122.5362 | 1.1227
30 | 143 | VISTA | 12 | 2046.9163 | 1.1158
31 | 10 | CIELO | 01 | 252.7569 | 1.1157
32 | 137 | COTTON | 01 | 234.1109 | 1.0935
33 | 1 | CANUTILLO | 01 | 1235.8153 | 1.0827
34 | 213 | DYER | 15 | 150 | 1.0733
35 | 125 | MILAGRO | 15 | 1107.3651 | 1.0584
36 | 203 | ANTHONY | 22 | 97 | 1.0515
37 | 51 | AMERICAS | 10 | 1201.631 | 1.0511
38 | 185 | SCOTSDALE | 14 | 2030.3421 | 1.0451
39 | 191 | COPPER | 11 | 1171.5902 | 1.0285
40 | 65 | THORN | 12 | 2147.3975 | 1.0054
41 | 178 | SOL | 11 | 2143.2539 | 0.99988
42 | 190 | SANTA FE | 02 | 362.5611 | 0.99569
43 | 217 | MONTOYA | 23 | 11.3948 | 0.96535
44 | 156 | SOL | 13 | 2737.8541 | 0.9102
45 | 119 | FELIPE | 20 | 744.804 | 0.87808
46 | 142 | ASCARATE | 01 | 204.0701 | 0.84285
47 | 38 | AUSTIN | 01 | 249.6492 | 0.75706
48 | 25 | HORIZON | 10 | 634.9998 | 0.72126
49 | 63 | CORONADO | 01 | 521.0521 | 0.66404
50 | 14 | CLARDY | 02 | 216.5008 | 0.64203
51 | 86 | VISTA | 11 | 2695.3827 | 0.63479
52 | 58 | RIO GRANDE | 13 | 1006.8839 | 0.61576
53 | 18 | ASCARATE | 04 | 356.3457 | 0.54161
54 | 20 | PARKDALE | 02 | 170.9217 | 0.51486
55 | 11 | CLINT | 11 | 1433.6701 | 0.49384
56 | 84 | MILAGRO | 12 | 2084.2083 | 0.49323
57 | 62 | GRACE | 01 | 266.2234 | 0.47704
58 | 60 | DIANA | 02 | 200.9624 | 0.4578
59 | 138 | AUSTIN | 02 | 476.5088 | 0.4491
60 | 106 | ANTHONY | 20 | 2954 | 0.43331
61 | 70 | MORNINGSIDE | 02 | 322.1614 | 0.41904
62 | 56 | SOL | 10 | 1945.3992 | 0.41534
63 | 101 | VISTA | 13 | 1871.8511 | 0.38999
64 | 100 | PARKDALE | 01 | 271.4029 | 0.38319
65 | 82 | ASCARATE | 03 | 498.2625 | 0.37932
66 | 109 | SOL | 14 | 1453.352 | 0.37775
67 | 153 | SUNSET | 04 | 326.305 | 0.37695
68 | 113 | CLARDY | 01 | 579.0618 | 0.35057
69 | 31 | YSLETA | 02 | 278.6541 | 0.3481
70 | 154 | YSLETA | 01 | 332.5203 | 0.34584
71 | 71 | WHITE | 01 | 237.2185 | 0.33724
72 | 50 | ALAMO | 20 | 1116.6881 | 0.32955
73 | 47 | VISTA | 14 | 2108.0337 | 0.32732
74 | 87 | THORN | 11 | 2220.9456 | 0.32689
75 | 80 | HACIENDA | 01 | 275.5464 | 0.31937
76 | 3 | SOCORRO | 10 | 1831 | 0.31458
77 | 17 | RADFORD | 01 | 168.8499 | 0.30204
78 | #N/A | CHAPARRAL | 10 | 3452 | 0.29838
79 | 55 | CROMO | 15 | 1134.2982 | 0.29534
80 | 93 | DIANA | 03 | 459.9346 | 0.29135
81 | 114 | BUTTERFIELD | 10 | 40 | 0.275
82 | 173 | FABENS | 02 | 581.1336 | 0.26328
83 | 12 | MANN | 10 | 895.0079 | 0.26033
84 | 74 | MANN | 13 | 1868.7434 | 0.26007
85 | 23 | LEO | 01 | 807.9933 | 0.25867
86 | 69 | SUMMIT | 02 | 237.2185 | 0.25715
87 | 131 | THORN | 15 | 1928.825 | 0.25663
88 | 172 | MIDWAY | 02 | 554.2005 | 0.25622
89 | 89 | MISSION | 02 | 487.9036 | 0.2562
90 | 150 | THORN | 10 | 1781.7287 | 0.25369
91 | 76 | FABENS | 01 | 210.2854 | 0.25204
92 | 116 | MULBERRY | 02 | 201.9983 | 0.21782
93 | 66 | VAN HORN | 02 | 186.46 | 0.21452
94 | 98 | TOBIN | 01 | 613.2462 | 0.21036
95 | 96 | ZARAGOSA | 01 | 436.1092 | 0.20637
96 | 2 | ALAMO | 21 | 427.8221 | 0.19868
97 | 112 | MANN | 12 | 1222.3488 | 0.18816
98 | 45 | MILAGRO | 17 | 1483.3928 | 0.18269
99 | 139 | DALLAS | 17 | 1074.2167 | 0.17873
100 | 120 | TOBIN | 02 | 601.8514 | 0.17778
101 | 188 | WRANGLER | 10 | 1732.0061 | 0.17552
102 | 146 | LEO | 12 | 1910.179 | 0.17276
103 | 32 | DALLAS | 04 | 157.4551 | 0.17148
104 | 59 | MESA | 14 | 1691.6064 | 0.17084
105 | 35 | AUSTIN | 04 | 623.6051 | 0.16677
106 | 85 | THORN | 13 | 2735.7823 | 0.16631
107 | 16 | EAST | 01 | 147.0962 | 0.15636
108 | 6 | BUTTERFIELD | 12 | 40 | 0.15
109 | 29 | AMERICAS | 11 | 1677.104 | 0.13893
110 | 222 | SANTA FE | 05 | 439.2169 | 0.13661
111 | 24 | ASCARATE | 13 | 2293.4578 | 0.13648
112 | 110 | MANN | 11 | 1909.1431 | 0.13357
113 | 83 | SCOTSDALE | 15 | 2246.8428 | 0.12907
114 | 107 | MONTOYA | 21 | 3629.7544 | 0.12756
115 | 135 | ALTURA | 06 | 252.7569 | 0.1266
116 | 166 | MESA | 17 | 1075.2526 | 0.12648
117 | 61 | VISTA | 15 | 2316.2474 | 0.12348
118 | 182 | COTTON | 02 | 130.522 | 0.12258
119 | 197 | LANE | 13 | 2059.3469 | 0.12237
120 | 148 | MIDWAY | 01 | 579.0618 | 0.12089
121 | 168 | CROMO | 13 | 620.4974 | 0.12087
122 | 15 | RANCHLAND | 02 | 243.4339 | 0.11502
123 | 149 | MORNINGSIDE | 01 | 298.336 | 0.11061
124 | 39 | FIVE POINTS | 02 | 171.9575 | 0.11049
125 | 151 | WHITE | 02 | 216.5008 | 0.10624
126 | 122 | ALTURA | 03 | 330.4485 | 0.10592
127 | 102 | CROMO | 12 | 1780.6929 | 0.10389
128 | 123 | RIO GRANDE | 15 | 2388.7596 | 0.09754
129 | 52 | CIELO | 02 | 123.2708 | 0.097347
130 | 121 | HACIENDA | 02 | 371.8841 | 0.096804
131 | 104 | WRANGLER | 13 | 3039.2977 | 0.093772
132 | 95 | DYER | 11 | 2288.2784 | 0.091772
133 | 130 | MILAGRO | 14 | 747.9117 | 0.089583
134 | 73 | SUNSET | 02 | 252.7569 | 0.08704
135 | 99 | SCOTSDALE | 12 | 1840.7744 | 0.08692
136 | 161 | SANTA TERESA | 21 | 1959.9016 | 0.085719
137 | 105 | FIVE POINTS | 03 | 221.6802 | 0.081198
138 | 127 | BEAUMONT | 01 | 533.4827 | 0.080602
139 | 126 | ZARAGOSA | 11 | 2131.8592 | 0.077397
140 | 129 | LEO | 11 | 1476.1415 | 0.076551
141 | 108 | CROMO | 11 | 871.1825 | 0.075759
142 | 155 | DALLAS | 13 | 1107.3651 | 0.072244
143 | 133 | ALTURA | 05 | 348.0586 | 0.071827
144 | 218 | NEWTEX | 01 | 1146 | 0.070681
145 | 78 | NEWTEX | 02 | 836.1731 | 0.068168
146 | 92 | TORNILLO | 01 | 75.6199 | 0.06612
147 | 36 | DIANA | 01 | 220.6443 | 0.063451
148 | 75 | LEO | 02 | 347.0227 | 0.063396
149 | 170 | SUNSET | 15 | 2022.0549 | 0.061324
150 | 72 | CALIENTE | 11 | 1136.37 | 0.05808
151 | 77 | AUSTIN | 03 | 278.6541 | 0.057419
152 | 33 | FARMER | 21 | 1068.0014 | 0.05618
153 | 158 | AUSTIN | 12 | 1293.8251 | 0.052557
154 | 8 | LOMALAND | 02 | 193.7112 | 0.051623
155 | 22 | ASCARATE | 11 | 1498.9311 | 0.050703
156 | 64 | VAN HORN | 01 | 242.398 | 0.049505
157 | 164 | AUSTIN | 10 | 2008.5884 | 0.044808
158 | 159 | ZARAGOSA | 10 | 1965.0811 | 0.043764
159 | 179 | DYER | 14 | 1353.9067 | 0.043578
160 | 184 | DYER | 12 | 1323.8659 | 0.0423
161 | 46 | SUNSET | 05 | 362.5611 | 0.041372
162 | 132 | MESA | 12 | 2030.3421 | 0.038417
163 | 163 | SANTA FE | 11 | 466.15 | 0.036469
164 | 160 | CALIENTE | 10 | 1701.9653 | 0.036428
165 | 187 | AUSTIN | 15 | 2406.3697 | 0.033661
166 | 152 | SCOTSDALE | 13 | 2346.2881 | 0.031539
167 | 157 | SOL | 15 | 2340.0728 | 0.029914
168 | 192 | SHEARMAN | 10 | 2867.3402 | 0.027552
169 | 167 | AUSTIN | 17 | 1668.8169 | 0.025767
170 | 196 | MESA | 13 | 1530.0078 | 0.022876
171 | 169 | OCTAVIA | 01 | 266.2234 | 0.022537
172 | 68 | SANTA FE | 01 | 316.982 | 0.022083
173 | 5 | SANTA FE | 04 | 420.5709 | 0.021399
174 | 124 | FIVE POINTS | 04 | 282.7976 | 0.021217
175 | 145 | DALLAS | 16 | 1269.9997 | 0.01811
176 | 134 | ASCARATE | 02 | 291.0848 | 0.017177
177 | 186 | AUSTIN | 16 | 1785.8723 | 0.016239
178 | 144 | FT. HANCOCK | 01 | 380.1712 | 0.015782
179 | 27 | DALLAS | 01 | 269.3311 | 0.014852
180 | 207 | AUSTIN | 13 | 1112.5446 | 0.012584
181 | 118 | SCOTSDALE | 11 | 2150.5052 | 0.012555
182 | 202 | AMERICAS | 12 | 1583.874 | 0.010102
183 | 174 | ALTURA | 01 | 198.8907 | 0.010056
184 | 26 | SUMMIT | 01 | 214.429 | 0.0093271
185 | 165 | VISCOUNT | 10 | 1687.4629 | 0.0088891
186 | 206 | AUSTIN | 11 | 1583.874 | 0.0088391
187 | 67 | SHEARMAN | 11 | 2355.6111 | 0.0084904
188 | 194 | SUNSET | 14 | 2637.3729 | 0.0060666
189 | 90 | FIVE POINTS | 01 | 225.8238 | 0.0044282
190 | 183 | DALLAS | 11 | 1308.3276 | 0.0030573
191 | 180 | SUNSET | 08 | 344.951 | 0.002899
192 | 162 | MESA | 18 | 691.9737 | 0.0028903
193 | 19 | MANN | 14 | 1840.7744 | 0.0016297
194 | 199 | DALLAS | 12 | 1482.3569 | 0.0013492
195 | 214 | LANE | 12 | 1944.3633 | 0.0010286
196 | 176 | FARAH | 11 | 1652.2426 | 0.00060524
197 | 200 | COPPER | 10 | 1715.4319 | 0.00058294
198 | 210 | CROMO | 10 | 1742.365 | 0.00057393
199 | 208 | AUSTIN | 14 | 2122.5362 | 0.00047113
200 | 136 | ALTURA | 02 | 290.0489 | 0
201 | 204 | ASCARATE | 12 | 839.0699 | 0
202 | 4 | BUTTERFIELD | 11 | 40 | 0
203 | 177 | COPPER | 12 | 1690.5705 | 0
204 | 211 | CROMO | 14 | 11.3948 | 0
205 | 212 | DALLAS | 02 | 306.6231 | 0
206 | 140 | EAST | 02 | 251.721 | 0
207 | 103 | KEMP | 01 | 237.2185 | 0
208 | 171 | LATTA | 01 | 462.0064 | 0
209 | 215 | LEO | 13 | 963.3766 | 0
210 | 189 | MANN | 15 | 1093.8986 | 0
211 | 21 | MESA | 16 | 1466.8185 | 0
212 | 219 | RIO GRANDE | 11 | 1577.6586 | 0
213 | 220 | RIVER | 01 | 125.3425 | 0
214 | 195 | SANTA FE | 10 | 1213.0258 | 0
215 | 181 | SANTA FE | 12 | 1868.7434 | 0
216 | 221 | SANTA FE | 03 | 11.3948 | 0
217 | 193 | SOCORRO | 11 | 2353.5394 | 0
218 | 223 | SOL | 12 | 1968.1887 | 0
219 | 224 | SUNSET | 01 | 328.3768 | 0
220 | 225 | SUNSET | 07 | 482.7242 | 0
221 | 201 | SUNSET NORTH | 10 | 2278.9554 | 0
222 | 175 | SUNSET NORTH | 11 | 1310.3993 | 0
223 | 198 | SUNSET NORTH | 12 | 2454.0206 | 0
224 | 147 | VISCOUNT | 11 | 1780.6929 | 0
225 | 227 | WRANGLER | 11 | 1073.1808 | 0
226 | 228 | WRANGLER | 12 | 11.3948 | 0
* Data reflects revised Service Quality Report for 1998/1999 as submitted to the Commission
concurrently with this filing.

## Feeder-SAIDI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System |  |  |  |  | Total Number of Feeders
With More Than 10 Customers |  |  |  |  | 226
Add or Delete Rows as Necessary
El Paso Electric Company
2000 SAIDI Ranking | 1999 SAIDI Ranking* | Substation Identification | Feeder Identification | Number of Customers | 2000 SAIDI Value
1 | 217 | MONTOYA | 23 | 11.3948 | 408.345
2 | 111 | SIERRA BLANCA | 01 | 109.8042 | 345.4877
3 | 70 | CINECUE | 01 | 472.3653 | 330.399
4 | 68 | FRONTERA | 01 | 257.9363 | 305.7732
5 | 14 | SIERRA BLANCA | 20 | 418 | 297.055
6 | 33 | AMERICAS | 10 | 1201.631 | 284.361
7 | 135 | ASCARATE | 01 | 204.0701 | 234.5616
8 | 91 | FELIPE | 20 | 744.804 | 209.8592
9 | 65 | AUSTIN | 01 | 249.6492 | 204.9876
10 | 44 | FRESNO | 01 | 236.1826 | 200.925
11 | 137 | AUSTIN | 02 | 476.5088 | 177.1552
12 | 36 | ASCARATE | 10 | 1435.7419 | 175.3532
13 | 19 | MULBERRY | 01 | 100.4812 | 168.6086
14 | 131 | SHEARMAN | 12 | 2649.8036 | 166.8143
15 | 13 | MONTOYA | 20 | 1923.6455 | 161.1362
16 | 54 | VISTA | 11 | 2695.3827 | 152.5505
17 | 15 | LANE | 11 | 1244.1025 | 148.7844
18 | 124 | CLINT | 01 | 828.711 | 144.7356
19 | 38 | COYOTE | 10 | 1564.1921 | 142.3968
20 | 226 | VISCOUNT | 12 | 2242.6993 | 136.8405
21 | 26 | HORIZON | 11 | 1728.8984 | 134.4058
22 | 12 | CLARDY | 02 | 216.5008 | 133.824
23 | 6 | HORIZON | 10 | 634.9998 | 127.7071
24 | 57 | ALTURA | 04 | 357.3816 | 126.4642
25 | 17 | MILAGRO | 11 | 1114.6164 | 121.937
26 | 109 | SUNSET | 13 | 25 | 120.24
27 | 138 | COTTON | 01 | 234.1109 | 117.7818
28 | 69 | MILAGRO | 12 | 2084.2083 | 115.0686
29 | 157 | MIDWAY | 02 | 554.2005 | 114.7978
30 | 1 | CANUTILLO | 01 | 1235.8153 | 109.1304
31 | 76 | SCOTSDALE | 16 | 1129.1188 | 105.438
32 | 122 | VISTA | 12 | 2046.9163 | 97.619
33 | 110 | DYER | 13 | 2122.5362 | 95.7034
34 | 141 | CLARDY | 01 | 579.0618 | 95.6564
35 | 47 | RIO GRANDE | 13 | 1006.8839 | 94.9077
36 | 213 | DYER | 15 | 150 | 92.3733
37 | 101 | ASCARATE | 03 | 498.2625 | 90.5988
38 | 46 | VISTA | 10 | 2250.9864 | 89.4794
39 | 112 | RANCHLAND | 01 | 264.1516 | 86.7116
40 | 216 | MONTOYA | 22 | 11.3948 | 85.5655
41 | 56 | CROMO | 15 | 1134.2982 | 84.7546
42 | 34 | SOL | 10 | 1945.3992 | 84.5323
43 | 59 | VISTA | 13 | 1871.8511 | 81.6427
44 | 55 | VALLEY | 10 | 2166.0435 | 81.3525
45 | 51 | THORN | 11 | 2220.9456 | 80.9597
46 | 16 | CIELO | 01 | 252.7569 | 77.8614
47 | 32 | VISTA | 14 | 2108.0337 | 77.1733
48 | 73 | SOL | 14 | 1453.352 | 75.0059
49 | 18 | CLINT | 11 | 1433.6701 | 73.0859
50 | 2 | ALAMO | 21 | 427.8221 | 70.2348
51 | 161 | YSLETA | 01 | 332.5203 | 70.1671
52 | 75 | ASCARATE | 04 | 356.3457 | 69.8395
53 | 143 | MILAGRO | 15 | 1107.3651 | 68.7443
54 | 83 | MILAGRO | 13 | 2753.3924 | 68.1283
55 | 29 | MISSION | 01 | 322.1614 | 67.6121
56 | 23 | THORN | 12 | 2147.3975 | 67.3448
57 | 74 | EAST | 01 | 147.0962 | 66.3715
58 | 52 | CORONADO | 01 | 521.0521 | 65.4848
59 | 96 | THORN | 15 | 1928.825 | 64.081
60 | 84 | GRACE | 01 | 266.2234 | 62.3311
61 | 104 | ANTHONY | 20 | 2954 | 61.542
62 | 203 | ANTHONY | 22 | 97 | 58.2062
63 | 20 | RADFORD | 01 | 168.8499 | 57.9627
64 | 48 | YSLETA | 02 | 278.6541 | 57.4404
65 | 120 | FIVE POINTS | 03 | 221.6802 | 57.001
66 | 50 | PARKDALE | 02 | 170.9217 | 56.7277
67 | 53 | BUTTERFIELD | 10 | 40 | 56.45
68 | 177 | SCOTSDALE | 14 | 2030.3421 | 54.9124
69 | 39 | RANCHLAND | 02 | 243.4339 | 52.6878
70 | 148 | SOL | 13 | 2737.8541 | 50.7664
71 | 77 | MORNINGSIDE | 02 | 322.1614 | 50.3288
72 | 42 | LA TUNA | 01 | 74.584 | 49.6889
73 | 107 | DYER | 11 | 2288.2784 | 48.9582
74 | 164 | SUNSET | 04 | 326.305 | 48.7427
75 | 155 | SOL | 11 | 2143.2539 | 47.9943
76 | 35 | WRANGLER | 14 | 458.8987 | 47.1128
77 | 64 | THORN | 14 | 2391.8672 | 46.5925
78 | 4 | BUTTERFIELD | 12 | 40 | 45.775
79 | 9 | SOCORRO | 10 | 1831 | 44.5866
80 | 71 | DIANA | 02 | 200.9624 | 44.5208
81 | 10 | MANN | 10 | 895.0079 | 43.4164
82 | 85 | MESA | 14 | 1691.6064 | 43.3487
83 | 152 | MIDWAY | 01 | 579.0618 | 42.3081
84 | 199 | LANE | 13 | 2059.3469 | 42.0978
85 | 30 | FIVE POINTS | 02 | 171.9575 | 42.0162
86 | 62 | WHITE | 01 | 237.2185 | 39.3772
87 | 100 | MANN | 12 | 1222.3488 | 37.2447
88 | 93 | PARKDALE | 01 | 271.4029 | 36.7608
89 | 114 | SCOTSDALE | 15 | 2246.8428 | 35.3995
90 | 86 | FABENS | 01 | 210.2854 | 34.1108
91 | #N/A | CHAPARRAL | 10 | 3452 | 33.3485
92 | 41 | LOMALAND | 01 | 416.4273 | 33.031
93 | 31 | SUMMIT | 02 | 237.2185 | 31.4309
94 | 61 | ALAMO | 20 | 1116.6881 | 30.397
95 | 181 | FABENS | 02 | 581.1336 | 29.2738
96 | 115 | WHITE | 02 | 216.5008 | 28.4295
97 | 90 | WRANGLER | 13 | 3039.2977 | 28.4138
98 | 99 | DIANA | 03 | 459.9346 | 27.7648
99 | 133 | THORN | 10 | 1781.7287 | 26.4462
100 | 27 | MILAGRO | 17 | 1483.3928 | 24.2775
101 | 60 | MISSION | 02 | 487.9036 | 24.1933
102 | 49 | LEO | 01 | 807.9933 | 23.817
103 | 125 | TOBIN | 02 | 601.8514 | 23.8065
104 | 108 | ZARAGOSA | 01 | 436.1092 | 23.7028
105 | 105 | HACIENDA | 01 | 275.5464 | 23.6911
106 | 134 | MULBERRY | 02 | 201.9983 | 23.2774
107 | 102 | RIO GRANDE | 15 | 2388.7596 | 22.6716
108 | 180 | COTTON | 02 | 130.522 | 21.0386
109 | 3 | AMERICAS | 11 | 1677.104 | 20.1556
110 | 82 | THORN | 13 | 2735.7823 | 19.3477
111 | 80 | VISTA | 15 | 2316.2474 | 18.9336
112 | 8 | AUSTIN | 04 | 623.6051 | 18.3033
113 | 113 | MONTOYA | 21 | 3629.7544 | 17.8434
114 | 28 | ASCARATE | 11 | 1498.9311 | 16.8553
115 | 66 | AUSTIN | 03 | 278.6541 | 15.905
116 | 153 | LEO | 12 | 1910.179 | 15.7556
117 | 92 | TOBIN | 01 | 613.2462 | 15.6185
118 | 123 | DALLAS | 17 | 1074.2167 | 15.5965
119 | 87 | LEO | 11 | 1476.1415 | 15.2621
120 | 119 | MANN | 11 | 1909.1431 | 15.1953
121 | 121 | CROMO | 11 | 871.1825 | 14.6456
122 | 103 | ASCARATE | 13 | 2293.4578 | 14.138
123 | 145 | HACIENDA | 02 | 371.8841 | 13.9156
124 | 190 | AUSTIN | 15 | 2406.3697 | 13.8325
125 | 156 | SANTA TERESA | 21 | 1959.9016 | 13.8175
126 | 67 | MANN | 13 | 1868.7434 | 13.5428
127 | 21 | DIANA | 01 | 220.6443 | 13.4107
128 | 22 | DALLAS | 04 | 157.4551 | 13.3435
129 | 186 | WRANGLER | 10 | 1732.0061 | 12.1755
130 | 150 | MORNINGSIDE | 01 | 298.336 | 11.8658
131 | 142 | MESA | 17 | 1075.2526 | 11.1946
132 | 171 | AUSTIN | 10 | 2008.5884 | 11.1153
133 | 95 | CROMO | 12 | 1780.6929 | 10.9278
134 | 139 | ZARAGOSA | 11 | 2131.8592 | 10.7207
135 | 129 | MILAGRO | 14 | 747.9117 | 10.5935
136 | 194 | COPPER | 11 | 1171.5902 | 10.1085
137 | 187 | DYER | 14 | 1353.9067 | 9.9172
138 | 192 | MESA | 13 | 1530.0078 | 9.8071
139 | 222 | SANTA FE | 05 | 439.2169 | 9.6308
140 | 116 | SCOTSDALE | 12 | 1840.7744 | 9.4645
141 | 63 | SUNSET | 02 | 252.7569 | 9.1867
142 | 127 | MESA | 12 | 2030.3421 | 8.6724
143 | 128 | ALTURA | 06 | 252.7569 | 8.0077
144 | 166 | SUNSET | 15 | 2022.0549 | 7.848
145 | 130 | TORNILLO | 01 | 75.6199 | 7.2997
146 | 106 | NEWTEX | 02 | 836.1731 | 7.1325
147 | 149 | CROMO | 13 | 620.4974 | 6.6479
148 | 146 | ALTURA | 03 | 330.4485 | 6.6183
149 | 218 | NEWTEX | 01 | 1146 | 6.4084
150 | 78 | VAN HORN | 02 | 186.46 | 6.1246
151 | 88 | CIELO | 02 | 123.2708 | 5.9949
152 | 72 | LEO | 02 | 347.0227 | 5.4348
153 | 126 | SOL | 15 | 2340.0728 | 5.3067
154 | 198 | SANTA FE | 02 | 362.5611 | 5.1853
155 | 168 | DALLAS | 13 | 1107.3651 | 4.9848
156 | 24 | SUNSET | 05 | 362.5611 | 4.9647
157 | 7 | LOMALAND | 02 | 193.7112 | 4.8577
158 | 136 | BEAUMONT | 01 | 533.4827 | 4.6843
159 | 144 | FIVE POINTS | 04 | 282.7976 | 4.3918
160 | 159 | ZARAGOSA | 10 | 1965.0811 | 3.6752
161 | 140 | ALTURA | 05 | 348.0586 | 3.6488
162 | 94 | CALIENTE | 11 | 1136.37 | 3.3774
163 | 189 | DYER | 12 | 1323.8659 | 3.3115
164 | 58 | FARMER | 21 | 1068.0014 | 3.0066
165 | 170 | CALIENTE | 10 | 1701.9653 | 2.7803
166 | 184 | AUSTIN | 16 | 1785.8723 | 2.5926
167 | 25 | SUMMIT | 01 | 214.429 | 2.3411
168 | 195 | SHEARMAN | 10 | 2867.3402 | 2.3283
169 | 160 | AUSTIN | 12 | 1293.8251 | 2.3117
170 | 154 | SCOTSDALE | 13 | 2346.2881 | 2.2474
171 | 43 | SANTA FE | 01 | 316.982 | 2.0853
172 | 167 | SANTA FE | 11 | 466.15 | 1.6132
173 | 11 | DALLAS | 01 | 269.3311 | 1.3663
174 | 151 | FT. HANCOCK | 01 | 380.1712 | 1.2784
175 | 132 | DALLAS | 16 | 1269.9997 | 1.0654
176 | 178 | AUSTIN | 17 | 1668.8169 | 0.98633
177 | 118 | SCOTSDALE | 11 | 2150.5052 | 0.92583
178 | 206 | AUSTIN | 11 | 1583.874 | 0.84855
179 | 97 | VAN HORN | 01 | 242.398 | 0.82509
180 | 172 | ALTURA | 01 | 198.8907 | 0.81955
181 | 45 | SANTA FE | 04 | 420.5709 | 0.81318
182 | 207 | AUSTIN | 13 | 1112.5446 | 0.7748
183 | 202 | AMERICAS | 12 | 1583.874 | 0.72102
184 | 191 | SUNSET | 14 | 2637.3729 | 0.6897
185 | 89 | ASCARATE | 02 | 291.0848 | 0.58402
186 | 40 | SHEARMAN | 11 | 2355.6111 | 0.50687
187 | 182 | VISCOUNT | 10 | 1687.4629 | 0.47112
188 | 175 | OCTAVIA | 01 | 266.2234 | 0.45075
189 | 201 | DALLAS | 12 | 1482.3569 | 0.29345
190 | 176 | DALLAS | 11 | 1308.3276 | 0.23006
191 | 169 | MESA | 18 | 691.9737 | 0.19509
192 | 165 | SUNSET | 08 | 344.951 | 0.11596
193 | 214 | LANE | 12 | 1944.3633 | 0.11109
194 | 208 | AUSTIN | 14 | 2122.5362 | 0.091871
195 | 98 | FIVE POINTS | 01 | 225.8238 | 0.088565
196 | 79 | MANN | 14 | 1840.7744 | 0.04346
197 | 200 | COPPER | 10 | 1715.4319 | 0.042555
198 | 210 | CROMO | 10 | 1742.365 | 0.035584
199 | 179 | FARAH | 11 | 1652.2426 | 0.035104
200 | 147 | ALTURA | 02 | 290.0489 | 0
201 | 204 | ASCARATE | 12 | 839.0699 | 0
202 | 5 | BUTTERFIELD | 11 | 40 | 0
203 | 185 | COPPER | 12 | 1690.5705 | 0
204 | 211 | CROMO | 14 | 11.3948 | 0
205 | 212 | DALLAS | 02 | 306.6231 | 0
206 | 158 | EAST | 02 | 251.721 | 0
207 | 117 | KEMP | 01 | 237.2185 | 0
208 | 174 | LATTA | 01 | 462.0064 | 0
209 | 215 | LEO | 13 | 963.3766 | 0
210 | 162 | MANN | 15 | 1093.8986 | 0
211 | 37 | MESA | 16 | 1466.8185 | 0
212 | 219 | RIO GRANDE | 11 | 1577.6586 | 0
213 | 220 | RIVER | 01 | 125.3425 | 0
214 | 221 | SANTA FE | 03 | 11.3948 | 0
215 | 183 | SANTA FE | 12 | 1868.7434 | 0
216 | 188 | SANTA FE | 10 | 1213.0258 | 0
217 | 193 | SOCORRO | 11 | 2353.5394 | 0
218 | 223 | SOL | 12 | 1968.1887 | 0
219 | 225 | SUNSET | 07 | 482.7242 | 0
220 | 224 | SUNSET | 01 | 328.3768 | 0
221 | 196 | SUNSET NORTH | 12 | 2454.0206 | 0
222 | 173 | SUNSET NORTH | 11 | 1310.3993 | 0
223 | 197 | SUNSET NORTH | 10 | 2278.9554 | 0
224 | 163 | VISCOUNT | 11 | 1780.6929 | 0
225 | 228 | WRANGLER | 12 | 11.3948 | 0
226 | 227 | WRANGLER | 11 | 1073.1808 | 0
* Data reflects revised Service Quality Report for 1998/1999 as submitted to the Commission
concurrently with this filing.

## Causes
El Paso Electric Company
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
2000 Reporting Year
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 34.92%
|  | Vegetation | 10.56%
|  | Animals and Birds | 11.12%
|  | People (Including cars and farm equip) | 6.67%
|  | Utility-owned Equipment | 18.19%
|  | Other | 2.375%
|  | Unknown | 14.4%