## Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | AEP West Texas Utilities
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 415
Due: |  | February 14, 2001
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 23436
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Division
Commission Staff
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mailto:mel.eckhoff@puc.state.tx.us

## Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
2000 Reporting Year
AEP West Texas Utilities
Project 23436

## System-SAIFI
AEP West Texas Utilities
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2000 | 0.73496 | 0.035263 | 0.014844 | 0.065214 | 0.04726 | 0.092326 | 0.042844 | 0.089404 | 0.015631 | 0.045865 | 0.09409 | 0.12599 | 0.064556
Scheduled
2000 | 0.022989 | 0.00094792 | 0.00088893 | 0.0008883 | 0.00068751 | 0.0029757 | 0.0023718 | 0.0010858 | 0.0019506 | 0.0016547 | 0.0021861 | 0.0067923 | 0.00049404
Outside Causes
2000 | 0.35487 | 0.026168 | 0.025537 | 0.052678 | 0.056486 | 0.073795 | 0.03363 | 0.011514 | 0.012432 | 0.0065664 | 0.011819 | 0.0045177 | 0.039408
Major Events
2000 | 0.049945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049699 | 0 | 0

## System-SAIDI
AEP West Texas Utilities
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2000 | 45.6953 | 1.0138 | 0.68929 | 4.6051 | 4.8919 | 3.4018 | 2.3234 | 6.3788 | 0.73857 | 2.25 | 4.0309 | 11.2094 | 4.0496
Scheduled
2000 | 1.0134 | 0.052467 | 0.054966 | 0.062927 | 0.035362 | 0.060249 | 0.1434 | 0.049895 | 0.064878 | 0.071115 | 0.24426 | 0.14927 | 0.021927
Outside Causes
2000 | 16.4102 | 1.4237 | 0.49536 | 1.4685 | 3.6987 | 3.9918 | 1.0954 | 1.3704 | 0.22671 | 0.15305 | 0.90385 | 0.75739 | 0.80366
Major Events
2000 | 7.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0222 | 0 | 0

## Feeder-SAIFI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System |  |  |  |  | Total Number of Feeders
With More Than 10 Customers |  |  |  |  | 415
Add or Delete Rows as Necessary
AEP West Texas Utilities
2000 SAIFI Ranking | 1999 SAIFI Ranking | Substation Identification | Feeder Identification | Number of Customers | 2000 SAIFI Value
1 | 81 | SA SOUTH | 4795 | 207 | 4.9179
2 | 329 | SONORA | 2045 | 797 | 4.2346
3 | 118 | SA WALNUT ST | 4635 | 1417 | 4.1588
4 | 137 | THROCKMORTON | 3190 | 711 | 4.0928
5 | 189 | BALLINGER | 4375 | 1199 | 4.0792
6 | 159 | AB HARTFORD ST | 3815 | 678 | 3.4749
7 | 116 | AB WALNUT ST | 3110 | 607 | 3.3954
8 | 104 | TEXON | 4345 | 134 | 3.3881
9 | 306 | ROBY | 3795 | 89 | 3.382
10 | 77 | SAND ROAD | 5195 | 646 | 3.3096
11 | 96 | AB HARTFORD ST | 3685 | 245 | 3.1388
12 | 177 | QUANAH | 3975 | 153 | 3.0719
13 | 315 | BRONTE | 3590 | 150 | 3
14 | 268 | AB DYESS 1 | 1775 | 300 | 2.8033
15 | 273 | VERNON | 1750 | 97 | 2.7216
16 | 144 | SA SOUTH | 3995 | 551 | 2.7187
17 | 88 | INDIAN MESA | 2695 | 150 | 2.7151
18 | 393 | SA SOUTH | 3500 | 888 | 2.6779
19 | 152 | ABILENE PLANT | 1570 | 280 | 2.4143
20 | 30 | SA COKE ST | 3905 | 115 | 2.3826
21 | 302 | BRONTE | 4160 | 369 | 2.2764
22 | 35 | RISING STAR | 5075 | 455 | 2.2703
23 | 162 | NORTH ANGELO 12KV BUS | 3120 | 1034 | 2.2534
24 | 203 | SA WALNUT ST | 3920 | 268 | 2.209
25 | 62 | MATADOR | 3030 | 545 | 2.189
26 | 25 | SA COKE ST | 4910 | 946 | 2.1818
27 | 211 | OZONA | 3810 | 807 | 2.171
28 | 117 | POWELL FIELD | 2528 | 35 | 2.1429
29 | 36 | SA LAKE DR | 5865 | 1129 | 2.124
30 | 258 | VERNON CITY PLANT | 5780 | 727 | 2.1169
31 | 316 | ONYX REA | 3260 | 103 | 2.1165
32 | 205 | SA CONCHO | 1705 | 283 | 2.0989
33 | 29 | SA SOUTH | 4255 | 172 | 2.0872
34 | 158 | CHRISTOVAL | 6615 | 802 | 2.086
35 | 234 | HAWLEY | 4455 | 613 | 2.0669
36 | 296 | BARNHART | 3725 | 111 | 2.0631
37 | 111 | SA WALNUT ST | 3925 | 659 | 2.0622
38 | 266 | VERNON | 3340 | 388 | 2.049
39 | 311 | AB HARTFORD ST | 3820 | 1435 | 2.0439
40 | 251 | AB HARTFORD ST | 3690 | 171 | 2.0409
41 | 185 | CEDAR GAP (TEC) | 5445 | 108 | 2.037
42 | 394 | ELDORADO | 1845 | 1066 | 2.031
43 | 281 | WYLIE | 6340 | 1284 | 2.0304
44 | 337 | SA COKE ST | 4915 | 197 | 2.0254
45 | 365 | AFTON | 2355 | 52 | 2.0192
46 | 207 | BRONTE | 3560 | 124 | 2.0161
47 | 356 | BRONTE AMBASSADOR | 6650 | 29 | 2
48 | 87 | PECOS VALLEY | 4075 | 19 | 1.9
49 | 198 | SA WALNUT ST | 3915 | 525 | 1.8571
50 | 38 | CLARENDON | 4040 | 757 | 1.8441
51 | 24 | OZONA | 3555 | 32 | 1.8438
52 | 80 | KNOX CITY | 3390 | 240 | 1.7458
53 | 69 | TANKERSLY (CVEC) | 5260 | 688 | 1.6788
54 | 253 | PUTNAM | 2131 | 195 | 1.6769
55 | 263 | SANTA ANNA | 3420 | 266 | 1.5526
56 | 6 | ALPINE 12KV | 3160 | 978 | 1.5394
57 | 126 | COLLEGE HILLS | 4845 | 322 | 1.5311
58 | 95 | AB MAPLE ST | 5750 | 103 | 1.4951
59 | 165 | ESTELLINE | 3535 | 121 | 1.4628
60 | 366 | FREISS RANCH | 4870 | 56 | 1.4286
61 | 397 | POWELL FIELD | 2529 | 14 | 1.4286
62 | 31 | VERNON | 4275 | 707 | 1.4215
63 | 397 | BOBCAT HILLS | 6655 | 10 | 1.4
64 | 21 | CLYDE | 1755 | 112 | 1.3926
65 | 181 | BEN FICKLIN | 6175 | 408 | 1.3701
66 | 369 | ASPERMONT | 312 | 85 | 1.3529
67 | 166 | WINTERS | 2113 | 811 | 1.3502
68 | 190 | SA AVENUE N | 1975 | 436 | 1.3463
69 | 228 | AB ELMDALE | 4520 | 75 | 1.32
70 | 105 | VALENTINE | 5590 | 708 | 1.3079
71 | 160 | ROUNDTOP | 4490 | 54 | 1.2963
72 | 235 | HUMBLE KEMPER | 1490 | 17 | 1.2941
73 | 397 | ACME BESTWALL | 4150 | 25 | 1.28
74 | 179 | RISING STAR | 5080 | 712 | 1.2669
75 | 61 | MERTZON (CVEC) | 2905 | 209 | 1.2632
76 | 134 | CHRISTOVAL | 6620 | 441 | 1.2608
77 | 127 | CROSS PLAINS | 1795 | 620 | 1.2323
78 | 136 | ROBY | 2276 | 352 | 1.2244
79 | 248 | COLLEGE HILLS | 5520 | 211 | 1.2133
80 | 153 | AB OIL MILL | 2780 | 455 | 1.211
81 | 168 | AB MCMURRY | 3245 | 886 | 1.1941
82 | 187 | WYLIE | 2675 | 891 | 1.1728
83 | 19 | CLYDE | 3630 | 331 | 1.1722
84 | 103 | HAMLIN | 3270 | 1063 | 1.1703
85 | 108 | HIGHLAND | 6385 | 731 | 1.1642
86 | 280 | RIO PECOS | 3835 | 144 | 1.1597
87 | 125 | MUNDAY | 6715 | 256 | 1.1562
88 | 210 | PADUCAH CITY | 1930 | 557 | 1.1508
89 | 218 | MORAN | 2107 | 426 | 1.1502
90 | 227 | BALLINGER | 4370 | 860 | 1.1488
91 | 9 | SA EMERSON ST | 4630 | 371 | 1.1482
92 | 75 | MORAN | 2108 | 202 | 1.1436
93 | 23 | NORTH ANGELO 12KV BUS | 3115 | 213 | 1.1408
94 | 169 | AB EAST 12KV | 4820 | 479 | 1.1399
95 | 307 | JUNCTION | 4340 | 892 | 1.1345
96 | 46 | HASKELL 12KV | 3495 | 1212 | 1.1312
97 | 180 | SA CONCHO | 1700 | 194 | 1.1237
98 | 154 | AB MCMURRY | 3235 | 357 | 1.1232
99 | 3 | SA CONCHO | 1715 | 276 | 1.1123
100 | 28 | CISCO | 1690 | 1021 | 1.1107
101 | 11 | AB SHELTON ST | 3045 | 470 | 1.1085
102 | 318 | AB SHELTON ST | 3060 | 1712 | 1.1075
103 | 149 | ASPR CONTINENTAL | 4800 | 28 | 1.1071
104 | 397 | PECAN BAYOU | 6815 | 1202 | 1.1015
105 | 26 | HASKELL 12KV | 3770 | 722 | 1.0983
106 | 146 | WINTERS | 3765 | 1046 | 1.0956
107 | 212 | BEN FICKLIN | 6180 | 1210 | 1.0926
108 | 339 | SANTA ANNA | 3415 | 479 | 1.0919
109 | 241 | SPUR | 417 | 281 | 1.089
110 | 259 | AB SHELTON ST | 4640 | 778 | 1.0887
111 | 20 | OZONA | 4185 | 1075 | 1.0874
112 | 110 | COLLEGE HILLS | 6145 | 459 | 1.0871
113 | 199 | NORTH ANGELO 12KV BUS | 3125 | 1513 | 1.0859
114 | 387 | QUANAH | 3530 | 584 | 1.0856
115 | 300 | ROCHESTER | 3290 | 65 | 1.0769
116 | 56 | AB SHELTON ST | 3040 | 406 | 1.0764
117 | 261 | PADUCAH CITY | 1935 | 424 | 1.0755
118 | 135 | TALPA ATLANTIC | 5180 | 81 | 1.0741
119 | 220 | AB MCMURRY | 4355 | 1175 | 1.074
120 | 89 | AB MCMURRY | 3240 | 318 | 1.0692
121 | 313 | CHILLICOTHE | 4530 | 583 | 1.0686
122 | 194 | KNOX CITY | 3300 | 632 | 1.0649
123 | 256 | BUSH KNOB | 5200 | 287 | 1.0627
124 | 317 | AILEEN | 4605 | 416 | 1.0601
125 | 78 | NORTH ANGELO 12KV BUS | 3130 | 376 | 1.0532
126 | 310 | ROCHESTER | 3295 | 283 | 1.053
127 | 285 | MEMPHIS | 3335 | 980 | 1.049
128 | 382 | AB OIL MILL | 3895 | 308 | 1.0422
129 | 319 | MCCAMEY | 3670 | 458 | 1.0415
130 | 42 | AB OIL MILL | 3900 | 651 | 1.0399
131 | 192 | MENARD | 3760 | 548 | 1.0347
132 | 71 | QUANAH | 3100 | 808 | 1.0334
133 | 244 | TUSCOLA | 3305 | 1036 | 1.0299
134 | 294 | ONYX REA | 3255 | 103 | 1.0291
135 | 44 | AB SHELTON ST | 3145 | 930 | 1.0247
136 | 360 | TRUSCOTT | 3845 | 43 | 1.0233
137 | 321 | BALLINGER | 4395 | 389 | 1.0231
138 | 55 | MATADOR | 3090 | 268 | 1.0187
139 | 293 | TWILIGHT TRAIL | 4285 | 1401 | 1.0186
140 | 157 | MASTERSON FIELD | 2101 | 167 | 1.018
141 | 64 | MCCAMEY | 2415 | 446 | 1.0179
142 | 255 | ANSON 12KV | 6635 | 589 | 1.0153
143 | 196 | BIG LAKE | 4665 | 231 | 1.013
144 | 50 | ABILENE PLANT | 1910 | 775 | 1.0077
145 | 262 | MCCAMEY | 2420 | 133 | 1.0075
146 | 279 | BENJAMIN (BEPC) | 5680 | 178 | 1.0056
147 | 312 | CISCO | 1685 | 193 | 1.0052
148 | 397 | TEXON | 5175 | 204 | 1.0049
149 | 245 | SA JACKSON ST | 4265 | 1149 | 1.0009
150 | 175 | EDITH HUMBLE | 6170 | 111 | 1
151 | 92 | SA WALNUT ST | 3910 | 486 | 1
152 | 178 | SWENSON | 136 | 35 | 1
153 | 13 | QUANAH | 100 | 52 | 0.98077
154 | 132 | FT DAVIS | 4515 | 395 | 0.89873
155 | 379 | AB RAINEY CREEK | 4225 | 244 | 0.87295
156 | 174 | MILES | 4670 | 474 | 0.84177
157 | 1 | SA GRAPE CREEK | 5365 | 132 | 0.81061
158 | 47 | RULE | 3378 | 135 | 0.78519
159 | 274 | FT DAVIS | 6570 | 134 | 0.78358
160 | 322 | ALPINE 12KV | 3875 | 688 | 0.76
161 | 90 | ALPINE 12KV | 3155 | 800 | 0.75133
162 | 51 | STAMFORD | 2815 | 729 | 0.72977
163 | 239 | WELLINGTON | 1770 | 234 | 0.68376
164 | 109 | SA JACKSON ST | 4690 | 406 | 0.67241
165 | 384 | MEMPHIS | 3025 | 385 | 0.66234
166 | 288 | MIDWAY LANE | 3440 | 86 | 0.61628
167 | 143 | WAGGONER | 5900 | 41 | 0.60976
168 | 57 | SPUDDER FLAT | 4175 | 60 | 0.6
169 | 257 | STAMFORD | 6255 | 49 | 0.55102
170 | 237 | RANKIN | 5735 | 17 | 0.52941
171 | 370 | VALERA HUMBLE | 7015 | 87 | 0.52874
172 | 72 | EOLA | 4950 | 235 | 0.5234
173 | 364 | SHAFTER | 5110 | 50 | 0.52
174 | 128 | AB VOGEL ST | 4410 | 328 | 0.51524
175 | 361 | IRAAN | 4305 | 43 | 0.48837
176 | 120 | AB COUNTRY CLUB | 4855 | 303 | 0.47855
177 | 275 | MERKEL | 1895 | 809 | 0.47342
178 | 397 | RANKIN | 6400 | 281 | 0.4306
179 | 277 | TUSCOLA | 3730 | 738 | 0.42547
180 | 22 | ROTAN | 1860 | 706 | 0.42493
181 | 150 | AB RAINEY CREEK | 4550 | 379 | 0.40633
182 | 79 | CROSS PLAINS | 2915 | 572 | 0.39161
183 | 4 | SHAMROCK | 144 | 525 | 0.38667
184 | 76 | CROSS PLAINS | 2920 | 569 | 0.38137
185 | 66 | AB CANYON ROCK | 5030 | 431 | 0.38051
186 | 145 | CHERRY CREEK TAP | 5245 | 11 | 0.36364
187 | 193 | AB COUNTRY CLUB | 4730 | 201 | 0.34328
188 | 240 | MUNDAY | 2080 | 772 | 0.3342
189 | 231 | STERLING CITY | 1445 | 711 | 0.33193
190 | 32 | AB OVER STREET 12KV | 1635 | 357 | 0.30812
191 | 142 | AB REBECCA LANE | 5550 | 651 | 0.30261
192 | 195 | AFTON | 2225 | 62 | 0.29032
193 | 122 | SA AVENUE N | 1730 | 739 | 0.28687
194 | 97 | SA JACKSON ST | 4695 | 245 | 0.27755
195 | 83 | IRAAN | 2055 | 348 | 0.26724
196 | 155 | ANSON REA (SEC) | 5215 | 494 | 0.26721
197 | 156 | AB REBECCA LANE | 2710 | 303 | 0.26403
198 | 396 | TWILIGHT TRAIL | 4290 | 1747 | 0.25816
199 | 219 | VERNON | 5000 | 511 | 0.25049
200 | 233 | SAND ROAD | 5655 | 737 | 0.2483
201 | 287 | PAULANN | 6280 | 678 | 0.24779
202 | 123 | PUTNAM | 2129 | 223 | 0.24215
203 | 223 | COLLEGE HILLS | 4835 | 295 | 0.24068
204 | 376 | COLLEGE HILLS | 5515 | 184 | 0.2337
205 | 349 | ASPR CONTINENTAL | 3830 | 13 | 0.23077
206 | 12 | CHILDRESS 69 | 1800 | 449 | 0.22272
207 | 269 | TRENT | 2850 | 18 | 0.22222
208 | 276 | TWILIGHT TRAIL | 3150 | 484 | 0.21694
209 | 74 | AB MAPLE ST | 5755 | 734 | 0.21662
210 | 33 | CISCO | 1680 | 573 | 0.21466
211 | 254 | AB DYESS 2 | 6335 | 371 | 0.21294
212 | 264 | WYLIE | 2665 | 902 | 0.20732
213 | 367 | ELDORADO | 2880 | 61 | 0.19672
214 | 202 | THROCKMORTON | 2090 | 58 | 0.18966
215 | 2 | HEDLEY | 5870 | 88 | 0.18182
216 | 40 | QUANAH | 1830 | 594 | 0.1734
217 | 343 | AB EAST 12KV | 4830 | 793 | 0.16772
218 | 70 | AB VOGEL ST | 4560 | 455 | 0.16484
219 | 138 | AB OVER STREET 12KV | 1840 | 827 | 0.16445
220 | 216 | MENARD | 3755 | 885 | 0.16045
221 | 397 | ROARING SPRINGS | 6155 | 25 | 0.16
222 | 124 | PECOS VALLEY | 4080 | 57 | 0.15789
223 | 191 | ALBANY | 3640 | 312 | 0.15705
224 | 93 | SA SOUTHLAND HILLS | 5055 | 563 | 0.15631
225 | 381 | AFTON | 2310 | 288 | 0.15278
226 | 236 | CISCO | 1675 | 901 | 0.15205
227 | 119 | TWILIGHT TRAIL | 5855 | 605 | 0.15041
228 | 107 | CLYDE | 3635 | 570 | 0.14955
229 | 397 | PECAN BAYOU | 6810 | 654 | 0.14759
230 | 10 | RULE | 3396 | 505 | 0.14653
231 | 8 | PRESIDIO | 6135 | 1017 | 0.14454
232 | 164 | WEINERT | 6490 | 139 | 0.14388
233 | 18 | MCELROY | 5165 | 164 | 0.14024
234 | 65 | VERHALEN | 4465 | 22 | 0.13636
235 | 246 | AB OVER STREET 12KV | 1645 | 504 | 0.13294
236 | 201 | AB EAST 12KV | 4825 | 558 | 0.13262
237 | 91 | KIRKLAND | 3545 | 39 | 0.12821
238 | 161 | AB VOGEL ST | 4405 | 709 | 0.12694
239 | 114 | SA SOUTHLAND HILLS | 5050 | 789 | 0.12548
240 | 102 | COLLEGE HILLS | 4840 | 490 | 0.12245
241 | 54 | SA LAKE DR | 5880 | 1570 | 0.12102
242 | 49 | MARFA | 1905 | 695 | 0.11942
243 | 82 | BRADY | 5015 | 201 | 0.1194
244 | 172 | MUNDAY | 3365 | 450 | 0.11778
245 | 59 | ROTAN | 1865 | 362 | 0.11602
246 | 283 | WEST YATES | 5595 | 150 | 0.11333
247 | 86 | SAND ROAD | 5295 | 427 | 0.11241
248 | 265 | AB SHELTON ST | 3050 | 1272 | 0.11006
249 | 7 | SA SOUTH | 2595 | 337 | 0.10979
250 | 247 | FT DAVIS | 3345 | 127 | 0.10236
251 | 15 | RIO PECOS | 513 | 40 | 0.1
252 | 358 | CEDAR GAP (TEC) | 4115 | 40 | 0.1
253 | 217 | SA JACKSON ST | 4250 | 214 | 0.098131
254 | 133 | HIGHLAND | 6370 | 554 | 0.095668
255 | 260 | PRESIDIO | 4540 | 823 | 0.092345
256 | 290 | AB ELM CREEK | 4780 | 586 | 0.090444
257 | 221 | VERNON | 1520 | 825 | 0.088485
258 | 345 | CHILDRESS 69 | 4865 | 893 | 0.086226
259 | 374 | FT CHADBOURNE | 6515 | 70 | 0.085714
260 | 27 | SA GRAPE CREEK | 4700 | 994 | 0.085513
261 | 173 | SA JACKSON ST | 4260 | 693 | 0.085137
262 | 101 | SA MATHIS FIELD | 5100 | 237 | 0.084388
263 | 386 | SONORA | 4805 | 559 | 0.084079
264 | 130 | PLASTERCO (MWEC) | 2720 | 205 | 0.082927
265 | 346 | FT CHADBOURNE | 6520 | 400 | 0.0825
266 | 129 | HAMLIN | 3775 | 354 | 0.081921
267 | 176 | CLYDE | 1760 | 367 | 0.081744
268 | 249 | BAIRD | 5125 | 682 | 0.079179
269 | 392 | SONORA | 4810 | 826 | 0.078692
270 | 250 | JAYTON | 6125 | 384 | 0.078125
271 | 99 | SA AVENUE N | 1695 | 1187 | 0.077506
272 | 335 | MCCAMEY | 2830 | 974 | 0.077002
273 | 206 | ROBERT LEE | 4120 | 286 | 0.076923
274 | 34 | SPUDDER FLAT | 4180 | 65 | 0.076923
275 | 67 | ROWENA | 4480 | 135 | 0.075
276 | 353 | HAROLD | 1495 | 41 | 0.073171
277 | 344 | BAIRD | 5120 | 431 | 0.071926
278 | 60 | MUNDAY REA (BKEC) | 2015 | 56 | 0.071429
279 | 84 | MARFA | 1900 | 776 | 0.070876
280 | 5 | ABILENE PLANT | 1565 | 284 | 0.070423
281 | 53 | MERKEL | 1890 | 603 | 0.069652
282 | 204 | INDIAN MESA | 2690 | 75 | 0.068966
283 | 48 | HEDLEY | 5845 | 322 | 0.068323
284 | 215 | AB MCMURRY | 4510 | 747 | 0.068273
285 | 188 | AB CANYON ROCK | 5035 | 685 | 0.067153
286 | 314 | AB ELM CREEK | 4775 | 597 | 0.067002
287 | 326 | ABILENE PLANT | 1735 | 151 | 0.066225
288 | 304 | AB COUNTRY CLUB | 4725 | 151 | 0.066225
289 | 272 | AB ELM CREEK | 1810 | 1451 | 0.066161
290 | 208 | ALBANY | 3655 | 669 | 0.06577
291 | 186 | SA MATHIS FIELD | 4790 | 31 | 0.064516
292 | 328 | MERTZON (CVEC) | 1530 | 632 | 0.063291
293 | 327 | AB ELM CREEK | 5045 | 606 | 0.062706
294 | 100 | SARAGOSA | 1590 | 16 | 0.0625
295 | 183 | AB ELM CREEK | 4745 | 725 | 0.06069
296 | 350 | KNOX CITY | 3985 | 17 | 0.058824
297 | 243 | ALBANY | 2029 | 223 | 0.058296
298 | 197 | PERKINS PROTHO | 5846 | 18 | 0.055556
299 | 85 | SA JACKSON ST | 4685 | 2737 | 0.054805
300 | 391 | CHILDRESS 69 | 2800 | 713 | 0.053296
301 | 140 | GRAYBACK | 3315 | 321 | 0.05296
302 | 151 | SARAGOSA | 1552 | 788 | 0.05203
303 | 301 | AB RAINEY CREEK | 4270 | 790 | 0.051899
304 | 43 | SAND ROAD | 5290 | 753 | 0.051793
305 | 141 | PAULANN | 6285 | 58 | 0.051724
306 | 354 | HAROLD | 3055 | 99 | 0.050505
307 | 213 | CHILDRESS 20TH ST | 5720 | 124 | 0.048387
308 | 336 | BEN FICKLIN | 6185 | 586 | 0.047782
309 | 395 | AB EAST 12KV | 5760 | 1091 | 0.047663
310 | 214 | AB MCMURRY | 4350 | 1145 | 0.047162
311 | 252 | BRADSHAW (CLIMAX) | 11301 | 43 | 0.046512
312 | 232 | AB OVER STREET 12KV | 3140 | 583 | 0.046312
313 | 325 | AB REBECCA LANE | 5555 | 1953 | 0.046083
314 | 200 | CLARENDON | 5005 | 764 | 0.045812
315 | 182 | VERNON CITY PLANT | 5840 | 67 | 0.044776
316 | 332 | AB SHELTON ST | 3435 | 338 | 0.044379
317 | 14 | STAMFORD | 4565 | 955 | 0.043979
318 | 397 | ASPERMONT | 6640 | 94 | 0.042553
319 | 238 | ALBANY | 3540 | 580 | 0.041379
320 | 363 | PEACOCK | 43 | 50 | 0.04
321 | 52 | CROWELL | 3490 | 52 | 0.038462
322 | 222 | AB SHELTON ST | 3660 | 600 | 0.038333
323 | 184 | ASPERMONT | 3380 | 728 | 0.037088
324 | 121 | ABILENE PLANT | 1575 | 298 | 0.036913
325 | 278 | SPUR | 414 | 280 | 0.035714
326 | 226 | SA AVENUE N | 1655 | 544 | 0.034926
327 | New | ALPINE 12KV | 6825 | 1586 | 0.034678
328 | 139 | ANSON 12KV | 6630 | 419 | 0.033413
329 | 45 | AB MCMURRY | 4360 | 1263 | 0.032462
330 | 289 | SUN VALLEY | 4300 | 93 | 0.032258
331 | 242 | BIG LAKE | 4655 | 1087 | 0.032199
332 | 271 | CHILDRESS 20TH ST | 5725 | 694 | 0.0317
333 | 112 | SA GRAPE CREEK | 5220 | 702 | 0.031339
334 | 342 | VERNON CITY PLANT | 5770 | 388 | 0.030928
335 | 41 | AB VOGEL ST | 4650 | 1013 | 0.030602
336 | 297 | AB ELM CREEK | 1815 | 505 | 0.029703
337 | 16 | SHAMROCK | 1835 | 75 | 0.026667
338 | 209 | JUNCTION | 4335 | 608 | 0.026316
339 | 230 | SA EMERSON ST | 4620 | 919 | 0.026115
340 | 229 | SA SOUTHLAND HILLS | 5455 | 624 | 0.025641
341 | 73 | WOODSON OIL FIELD | 30 | 40 | 0.025
342 | 292 | AILEEN | 6435 | 496 | 0.024194
343 | 324 | SA SOUTHLAND HILLS | 5860 | 142 | 0.021127
344 | 284 | TURKEY | 2980 | 381 | 0.020997
345 | 341 | AB ELM CREEK | 1825 | 774 | 0.020672
346 | 303 | AB WALNUT ST | 3785 | 1847 | 0.020032
347 | 295 | TURKEY | 3825 | 361 | 0.019391
348 | 68 | DUNEFIELD (N CRANE) | 3885 | 52 | 0.019231
349 | 397 | RANKIN | 6405 | 317 | 0.018927
350 | 113 | MCCAMEY | 2855 | 110 | 0.018182
351 | 380 | EDEN | 1780 | 278 | 0.017986
352 | 98 | ROBERT LEE | 4125 | 684 | 0.016082
353 | 37 | HIGHLAND | 6375 | 188 | 0.015957
354 | 225 | CROWELL | 3980 | 761 | 0.015769
355 | 167 | SHAMROCK | 148 | 1100 | 0.014545
356 | 267 | STAMFORD | 2835 | 641 | 0.014041
357 | 17 | WELLINGTON | 1765 | 856 | 0.01285
358 | 94 | SA SOUTH | 3990 | 318 | 0.012579
359 | 39 | GRAYBACK | 3320 | 321 | 0.012461
360 | 338 | IRAAN | 2050 | 430 | 0.011628
361 | 388 | CHILLICOTHE | 4525 | 621 | 0.011272
362 | 299 | SPUR | 5170 | 1155 | 0.011255
363 | 308 | ABILENE PLANT | 1915 | 93 | 0.010753
364 | 147 | TRENT | 4245 | 290 | 0.010345
365 | 131 | EDEN | 3195 | 513 | 0.0097466
366 | 397 | SHEFFIELD | 6430 | 208 | 0.0096154
367 | 397 | WINTERS | 2740 | 109 | 0.0091743
368 | 106 | AB RAINEY CREEK | 4220 | 132 | 0.0075758
369 | 148 | SA LAKE DR | 6030 | 957 | 0.0062696
370 | 309 | PAINT ROCK | 5235 | 186 | 0.0053763
371 | 224 | HASKELL 12KV | 5240 | 203 | 0.0049261
372 | 163 | SA EMERSON ST | 4625 | 211 | 0.0047393
373 | 331 | AB COUNTRY CLUB | 4735 | 504 | 0.0039683
374 | 291 | WELLINGTON | 3700 | 644 | 0.0031056
375 | 115 | CHILDRESS 69 | 1480 | 426 | 0.0023474
376 | 334 | PAULANN | 6310 | 580 | 0.0017241
377 | 347 | AB WALNUT ST | 3445 | 793 | 0.001261
378 | 385 | AILEEN | 4600 | 798 | 0.0012531
379 | 372 | PADUCAH CITY | 13 | 104 | 0
380 | 390 | SA CONCHO | 1710 | 701 | 0
381 | 397 | WEINERT | 3363 | 139 | 0
382 | 397 | FT DAVIS | 3347 | 387 | 0
383 | 397 | CROSS PLAINS | 5130 | 61 | 0
384 | 397 | EDITH HUMBLE | 3097 | 112 | 0
385 | 375 | ABILENE PLANT | 1740 | 184 | 0
386 | 389 | SA CONCHO | 1405 | 662 | 0
387 | 355 | CORINTH | 2590 | 28 | 0
388 | 368 | VERNON CITY PLANT | 5835 | 67 | 0
389 | 323 | SA EMERSON ST | 4860 | 394 | 0
390 | 351 | HAMLIN SHELL | 152 | 22 | 0
391 | 352 | HAMLIN SHELL | 6330 | 23 | 0
392 | 171 | PAINT CREEK | 3930 | 39 | 0
393 | 371 | ABILENE PLANT | 1580 | 88 | 0
394 | 340 | ABILENE PLANT | 3175 | 296 | 0
395 | 377 | VERNON CITY PLANT | 5785 | 194 | 0
396 | 397 | OAK CREEK #2 | 3213 | 706 | 0
397 | 282 | MELVIN | 4955 | 148 | 0
398 | 397 | VALERA HUMBLE | 8201 | 78 | 0
399 | 286 | MEMPHIS | 11 | 168 | 0
400 | 270 | CAREY | 6115 | 122 | 0
401 | 397 | CROCKETT HEIGHTS | 346OCR | 64 | 0
402 | 170 | HIGHLAND | 6380 | 2127 | 0
403 | 333 | ROWENA | 7041 | 80 | 0
404 | 359 | AB CANYON ROCK | 5025 | 40 | 0
405 | 63 | FLOMOT | 4089 | 83 | 0
406 | 397 | ANSON 12KV | 311 | 419 | 0
407 | 305 | MENARD | 3750 | 400 | 0
408 | 397 | PRESIDIO | 4535 | 1638 | 0
409 | 362 | VERNON CITY PLANT | 5830 | 49 | 0
410 | 378 | BIG LAKE | 4660 | 231 | 0
411 | 383 | SA CONCHO | 1725 | 345 | 0
412 | 397 | ANSON 12KV | 310 | 589 | 0
413 | 397 | GIRARD | 6260 | 41 | 0
414 | 373 | MEMPHIS | 12 | 119 | 0
415 | New | ALPINE 12KV | 6820 | 681 | 0

## Feeder-SAIDI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System |  |  |  |  | Total Number of Feeders
With More Than 10 Customers |  |  |  |  | 415
Add or Delete Rows as Necessary
AEP West Texas Utilities
2000 SAIDI Ranking | 1999 SAIDI Ranking | Substation Identification | Feeder Identification | Number of Customers | 2000 SAIDI Value
1 | 45 | TEXON | 4345 | 134 | 679.4701
2 | 46 | CLARENDON | 4040 | 757 | 579.9287
3 | 43 | INDIAN MESA | 2695 | 150 | 515.2402
4 | 256 | PUTNAM | 2131 | 195 | 457.7282
5 | 149 | WINTERS | 2113 | 811 | 364.9014
6 | 6 | OZONA | 3555 | 32 | 340.4375
7 | 183 | AB HARTFORD ST | 3815 | 678 | 336.1475
8 | 124 | WINTERS | 3765 | 1046 | 324.7304
9 | 238 | SA CONCHO | 1705 | 283 | 318.8092
10 | 218 | ABILENE PLANT | 1570 | 280 | 318.6071
11 | 295 | TWILIGHT TRAIL | 4285 | 1401 | 293.0792
12 | 119 | SA CONCHO | 1700 | 194 | 287.8608
13 | 127 | SA WALNUT ST | 4635 | 1417 | 251.8327
14 | 216 | QUANAH | 3975 | 153 | 245.5033
15 | 105 | MASTERSON FIELD | 2101 | 167 | 243.1916
16 | 79 | SWENSON | 136 | 35 | 236
17 | 228 | HAWLEY | 4455 | 613 | 233.7031
18 | 196 | THROCKMORTON | 3190 | 711 | 222.7511
19 | 315 | ONYX REA | 3260 | 103 | 221.7282
20 | 366 | FREISS RANCH | 4870 | 56 | 217.8571
21 | 144 | SA AVENUE N | 1975 | 436 | 195.2706
22 | 151 | KNOX CITY | 3390 | 240 | 181.2833
23 | 112 | SA SOUTH | 4795 | 207 | 181.1159
24 | 280 | MIDWAY LANE | 3440 | 86 | 177.8372
25 | 8 | SA SOUTH | 4255 | 172 | 175.157
26 | 110 | COLLEGE HILLS | 4845 | 322 | 171.7578
27 | 37 | PECOS VALLEY | 4075 | 19 | 171.5
28 | 96 | POWELL FIELD | 2528 | 35 | 165.0857
29 | 199 | SAND ROAD | 5195 | 646 | 164.1765
30 | 336 | CHILLICOTHE | 4530 | 583 | 163.319
31 | 209 | HUMBLE KEMPER | 1490 | 17 | 153.0588
32 | 267 | WYLIE | 6340 | 1284 | 141.9439
33 | 397 | BOBCAT HILLS | 6655 | 10 | 141.2
34 | 69 | ABILENE PLANT | 1910 | 775 | 139.88
35 | 302 | ROBY | 3795 | 89 | 138.6292
36 | 56 | VALENTINE | 5590 | 708 | 131.3051
37 | 28 | MERTZON (CVEC) | 2905 | 209 | 128.9234
38 | 326 | SONORA | 2045 | 797 | 127.8971
39 | 210 | OZONA | 3810 | 807 | 125.8662
40 | 230 | AB MCMURRY | 4355 | 1175 | 124.6621
41 | 365 | AFTON | 2355 | 52 | 121.6538
42 | 140 | SA WALNUT ST | 3925 | 659 | 121.0364
43 | 384 | MEMPHIS | 3025 | 385 | 118.5974
44 | 108 | STAMFORD | 2815 | 729 | 116.7956
45 | 162 | CHRISTOVAL | 6615 | 802 | 116.0087
46 | 274 | BUSH KNOB | 5200 | 287 | 115.8223
47 | 397 | POWELL FIELD | 2529 | 14 | 111.2857
48 | 71 | AB HARTFORD ST | 3685 | 245 | 109.0939
49 | 254 | COLLEGE HILLS | 5520 | 211 | 108.6825
50 | 94 | AB WALNUT ST | 3110 | 607 | 108.5684
51 | 184 | SA WALNUT ST | 3920 | 268 | 106.3731
52 | 100 | EDITH HUMBLE | 6170 | 111 | 106
53 | 75 | AB SHELTON ST | 3145 | 930 | 105.3731
54 | 262 | BENJAMIN (BEPC) | 5680 | 178 | 102.5562
55 | 76 | MATADOR | 3030 | 545 | 101.5596
56 | 107 | AB MAPLE ST | 5750 | 103 | 98.8738
57 | 16 | OZONA | 4185 | 1075 | 97.6214
58 | 31 | TANKERSLY (CVEC) | 5260 | 688 | 95.6904
59 | 152 | SA WALNUT ST | 3915 | 525 | 92.0343
60 | 234 | WELLINGTON | 1770 | 234 | 91.7906
61 | 35 | SPUDDER FLAT | 4175 | 60 | 91.3833
62 | 186 | NORTH ANGELO 12KV BUS | 3120 | 1034 | 90.852
63 | 215 | PADUCAH CITY | 1930 | 557 | 90.605
64 | 281 | MCCAMEY | 2420 | 133 | 90.0451
65 | 188 | AB ELMDALE | 4520 | 75 | 89.48
66 | 128 | WAGGONER | 5900 | 41 | 89.0244
67 | 360 | TRUSCOTT | 3845 | 43 | 88.9767
68 | 146 | CHRISTOVAL | 6620 | 441 | 87.9524
69 | 132 | AB RAINEY CREEK | 4550 | 379 | 87.2982
70 | 393 | SA SOUTH | 3500 | 888 | 85.8502
71 | 314 | MCCAMEY | 3670 | 458 | 84.0437
72 | 239 | BARNHART | 3725 | 111 | 82.4054
73 | 240 | VERNON | 3340 | 388 | 81.5593
74 | 153 | AB MCMURRY | 3245 | 886 | 80.5305
75 | 277 | VERNON | 1750 | 97 | 80.0825
76 | 300 | BRONTE | 4160 | 369 | 79.1111
77 | 164 | MENARD | 3760 | 548 | 79.031
78 | 13 | SA LAKE DR | 5865 | 1129 | 78.7848
79 | 308 | SANTA ANNA | 3420 | 266 | 78.5602
80 | 129 | ESTELLINE | 3535 | 121 | 78.1405
81 | 50 | SA EMERSON ST | 4630 | 371 | 77.5903
82 | 40 | RISING STAR | 5075 | 455 | 77.2703
83 | 321 | BRONTE | 3590 | 150 | 77
84 | 19 | SA COKE ST | 4910 | 946 | 76.2146
85 | 226 | BALLINGER | 4375 | 1199 | 76.1485
86 | 223 | PADUCAH CITY | 1935 | 424 | 75.7618
87 | 18 | SA COKE ST | 3905 | 115 | 75.4174
88 | 394 | ELDORADO | 1845 | 1066 | 75.0141
89 | 305 | AB DYESS 1 | 1775 | 300 | 74.0633
90 | 397 | ACME BESTWALL | 4150 | 25 | 73.36
91 | 155 | CROSS PLAINS | 1795 | 620 | 73.3129
92 | 85 | AB SHELTON ST | 3040 | 406 | 71.6059
93 | 161 | AB OIL MILL | 2780 | 455 | 70.4967
94 | 7 | NORTH ANGELO 12KV BUS | 3115 | 213 | 69.5117
95 | 397 | TEXON | 5175 | 204 | 68.1765
96 | 169 | ROUNDTOP | 4490 | 54 | 68.1481
97 | 22 | NORTH ANGELO 12KV BUS | 3130 | 376 | 67.9894
98 | 205 | NORTH ANGELO 12KV BUS | 3125 | 1513 | 67.4937
99 | 376 | COLLEGE HILLS | 5515 | 184 | 66.0761
100 | 247 | VERNON CITY PLANT | 5780 | 727 | 65.5213
101 | 379 | AB RAINEY CREEK | 4225 | 244 | 65.1844
102 | 180 | TALPA ATLANTIC | 5180 | 81 | 64.4444
103 | 52 | HASKELL 12KV | 3495 | 1212 | 63.0017
104 | 334 | SA COKE ST | 4915 | 197 | 62.4315
105 | 178 | SA SOUTH | 3995 | 551 | 61.7931
106 | 189 | ASPR CONTINENTAL | 4800 | 28 | 61.4643
107 | 361 | IRAAN | 4305 | 43 | 59.2558
108 | 369 | ASPERMONT | 312 | 85 | 58.4118
109 | 304 | AB SHELTON ST | 3060 | 1712 | 57.4936
110 | 272 | MUNDAY | 2080 | 772 | 57.2228
111 | 168 | AB MCMURRY | 3235 | 357 | 56.2493
112 | 200 | MEMPHIS | 3335 | 980 | 55.0847
113 | 130 | WYLIE | 2675 | 891 | 54.5365
114 | 341 | SANTA ANNA | 3415 | 479 | 54.2965
115 | 397 | PECAN BAYOU | 6815 | 1202 | 54.183
116 | 382 | AB OIL MILL | 3895 | 308 | 53.3636
117 | 118 | AB OIL MILL | 3900 | 651 | 51.9923
118 | 11 | SA WALNUT ST | 3910 | 486 | 49.6667
119 | 364 | SHAFTER | 5110 | 50 | 48.72
120 | 3 | SA GRAPE CREEK | 5365 | 132 | 48.0455
121 | 269 | MERKEL | 1895 | 809 | 47.9221
122 | 323 | JUNCTION | 4340 | 892 | 47.6345
123 | 273 | RANKIN | 5735 | 17 | 47.5882
124 | 171 | AB EAST 12KV | 4820 | 479 | 46.9896
125 | 156 | MUNDAY | 6715 | 256 | 45.9688
126 | 242 | TUSCOLA | 3730 | 738 | 45.7846
127 | 237 | AB HARTFORD ST | 3690 | 171 | 45.5731
128 | 160 | RISING STAR | 5080 | 712 | 44.7486
129 | 49 | SA CONCHO | 1715 | 276 | 44.3732
130 | 62 | AB CANYON ROCK | 5030 | 431 | 43.7332
131 | 194 | AB COUNTRY CLUB | 4730 | 201 | 43.2438
132 | 104 | PECOS VALLEY | 4080 | 57 | 43.0351
133 | 320 | AB HARTFORD ST | 3820 | 1435 | 41.4237
134 | 356 | BRONTE AMBASSADOR | 6650 | 29 | 41
135 | 38 | CLYDE | 3630 | 331 | 40.6254
136 | 176 | FT DAVIS | 4515 | 395 | 40.2456
137 | 145 | ROBY | 2276 | 352 | 40.1136
138 | 59 | MATADOR | 3090 | 268 | 38.8396
139 | 111 | AB MCMURRY | 3240 | 318 | 38.2704
140 | 109 | SA JACKSON ST | 4690 | 406 | 38.2217
141 | 113 | BIG LAKE | 4665 | 231 | 37.039
142 | 65 | COLLEGE HILLS | 6145 | 459 | 36.7059
143 | 172 | AB VOGEL ST | 4410 | 328 | 36.5183
144 | 66 | ALPINE 12KV | 3155 | 800 | 36.079
145 | 251 | ONYX REA | 3255 | 103 | 36.068
146 | 86 | VERNON | 4275 | 707 | 36.0594
147 | 197 | CEDAR GAP (TEC) | 5445 | 108 | 35.9259
148 | 179 | MILES | 4670 | 474 | 35.0823
149 | 316 | ROCHESTER | 3290 | 65 | 34.9692
150 | 99 | HIGHLAND | 6385 | 731 | 33.9234
151 | 328 | ROCHESTER | 3295 | 283 | 33.5336
152 | 60 | AB SHELTON ST | 3045 | 470 | 33.017
153 | 55 | MORAN | 2108 | 202 | 32.8564
154 | 67 | EOLA | 4950 | 235 | 31.6766
155 | 343 | AB EAST 12KV | 4830 | 793 | 30.8588
156 | 268 | BALLINGER | 4370 | 860 | 28.9651
157 | 133 | AFTON | 2225 | 62 | 28.6129
158 | 248 | AB SHELTON ST | 4640 | 778 | 28.4499
159 | 70 | CLYDE | 1755 | 112 | 27.183
160 | 340 | BALLINGER | 4395 | 389 | 27.0977
161 | 39 | CROSS PLAINS | 2915 | 572 | 26.9563
162 | 32 | RULE | 3378 | 135 | 25.8593
163 | 30 | SA SOUTHLAND HILLS | 5055 | 563 | 25.8384
164 | 396 | TWILIGHT TRAIL | 4290 | 1747 | 25.7499
165 | 115 | TWILIGHT TRAIL | 5855 | 605 | 24.9868
166 | 57 | SHAMROCK | 144 | 525 | 24.7962
167 | 198 | MORAN | 2107 | 426 | 24.7653
168 | 15 | MCCAMEY | 2415 | 446 | 24.3677
169 | 255 | SA JACKSON ST | 4265 | 1149 | 24.2359
170 | 246 | PAULANN | 6280 | 678 | 23.9676
171 | 48 | AB VOGEL ST | 4560 | 455 | 23.2088
172 | 289 | RIO PECOS | 3835 | 144 | 22.9444
173 | 297 | AILEEN | 4605 | 416 | 22.625
174 | 34 | HASKELL 12KV | 3770 | 722 | 22.1219
175 | 165 | AB COUNTRY CLUB | 4855 | 303 | 22.099
176 | 381 | AFTON | 2310 | 288 | 21.1632
177 | 143 | HAMLIN | 3270 | 1063 | 21.063
178 | 185 | QUANAH | 3100 | 808 | 21.0507
179 | 208 | TUSCOLA | 3305 | 1036 | 21.0299
180 | 263 | WYLIE | 2665 | 902 | 20.1763
181 | 92 | AB REBECCA LANE | 5550 | 651 | 19.8571
182 | 93 | IRAAN | 2055 | 348 | 19.6149
183 | 206 | KNOX CITY | 3300 | 632 | 19.3386
184 | 243 | SPUR | 417 | 281 | 19.1139
185 | 285 | TWILIGHT TRAIL | 3150 | 484 | 18.6798
186 | 80 | AB OVER STREET 12KV | 1635 | 357 | 18.6387
187 | 229 | BRONTE | 3560 | 124 | 18.4435
188 | 137 | CHERRY CREEK TAP | 5245 | 11 | 18.3636
189 | 324 | ALPINE 12KV | 3875 | 688 | 18.32
190 | 53 | CROSS PLAINS | 2920 | 569 | 17.3128
191 | 370 | VALERA HUMBLE | 7015 | 87 | 16.977
192 | 25 | CISCO | 1690 | 1021 | 16.8492
193 | 88 | SA JACKSON ST | 4695 | 245 | 16.7878
194 | 90 | SARAGOSA | 1590 | 16 | 16.75
195 | 332 | CISCO | 1685 | 193 | 16.5285
196 | 82 | QUANAH | 100 | 52 | 16.25
197 | 266 | TRENT | 2850 | 18 | 16.1111
198 | 213 | AB REBECCA LANE | 2710 | 303 | 16.0429
199 | 211 | COLLEGE HILLS | 4835 | 295 | 15.9763
200 | 175 | BEN FICKLIN | 6180 | 1210 | 15.8628
201 | 116 | AB MAPLE ST | 5755 | 734 | 15.7057
202 | 212 | STAMFORD | 6255 | 49 | 15.6327
203 | 166 | AB OVER STREET 12KV | 1840 | 827 | 15.5357
204 | 123 | PUTNAM | 2129 | 223 | 15.5202
205 | 203 | STERLING CITY | 1445 | 711 | 14.9381
206 | 21 | ALPINE 12KV | 3160 | 978 | 14.8686
207 | 284 | ANSON 12KV | 6635 | 589 | 13.9881
208 | 106 | MARFA | 1905 | 695 | 13.3453
209 | 33 | BRADY | 5015 | 201 | 13.1542
210 | 83 | CISCO | 1680 | 573 | 13.1449
211 | 387 | QUANAH | 3530 | 584 | 12.6541
212 | 201 | MUNDAY | 3365 | 450 | 12.58
213 | 4 | ROTAN | 1860 | 706 | 12.0382
214 | 271 | THROCKMORTON | 2090 | 58 | 11.7759
215 | 397 | ROARING SPRINGS | 6155 | 25 | 11.4
216 | 291 | WEST YATES | 5595 | 150 | 10.7133
217 | 235 | FT DAVIS | 6570 | 134 | 10.6269
218 | 9 | MCELROY | 5165 | 164 | 10.4634
219 | 98 | SA AVENUE N | 1730 | 739 | 10.3884
220 | 217 | AB EAST 12KV | 4825 | 558 | 10.1989
221 | 27 | SA LAKE DR | 5880 | 1570 | 9.9949
222 | 222 | VERNON | 5000 | 511 | 9.8004
223 | 359 | CEDAR GAP (TEC) | 4115 | 40 | 9.675
224 | 1 | HEDLEY | 5870 | 88 | 9.6705
225 | 173 | WEINERT | 6490 | 139 | 9.3525
226 | 42 | ABILENE PLANT | 1565 | 284 | 9.2148
227 | 245 | FT DAVIS | 3345 | 127 | 9.1102
228 | 126 | PLASTERCO (MWEC) | 2720 | 205 | 8.9854
229 | 354 | HAROLD | 1495 | 41 | 8.9756
230 | 117 | SA SOUTHLAND HILLS | 5050 | 789 | 8.7719
231 | 5 | SA SOUTH | 2595 | 337 | 8.4154
232 | 232 | ANSON REA (SEC) | 5215 | 494 | 8.2854
233 | 193 | AB DYESS 2 | 6335 | 371 | 8.1995
234 | 190 | ALBANY | 3640 | 312 | 8.1346
235 | 344 | BAIRD | 5120 | 431 | 8.0696
236 | 12 | RULE | 3396 | 505 | 8.0554
237 | 78 | BEN FICKLIN | 6175 | 408 | 7.9412
238 | 397 | PECAN BAYOU | 6810 | 654 | 7.8735
239 | 225 | AB OVER STREET 12KV | 1645 | 504 | 7.8075
240 | 312 | MERTZON (CVEC) | 1530 | 632 | 7.6725
241 | 167 | INDIAN MESA | 2690 | 75 | 7.5862
242 | 309 | AB COUNTRY CLUB | 4725 | 151 | 7.4834
243 | 174 | MENARD | 3755 | 885 | 7.2554
244 | 350 | KNOX CITY | 3985 | 17 | 7.2353
245 | 374 | FT CHADBOURNE | 6515 | 70 | 7.2
246 | 163 | HAMLIN | 3775 | 354 | 7.096
247 | 290 | AB ELM CREEK | 4780 | 586 | 6.8754
248 | 24 | PRESIDIO | 6135 | 1017 | 6.6018
249 | 195 | SA JACKSON ST | 4260 | 693 | 6.4242
250 | 29 | CHILDRESS 69 | 1800 | 449 | 6.4076
251 | 41 | VERHALEN | 4465 | 22 | 6.3636
252 | 349 | ASPR CONTINENTAL | 3830 | 13 | 6.2308
253 | 214 | AB MCMURRY | 4510 | 747 | 6.1901
254 | 207 | AB VOGEL ST | 4405 | 709 | 6.1537
255 | 114 | HIGHLAND | 6370 | 554 | 6.1354
256 | 264 | SAND ROAD | 5655 | 737 | 6.1194
257 | 367 | ELDORADO | 2880 | 61 | 5.9672
258 | 122 | SA GRAPE CREEK | 4700 | 994 | 5.9477
259 | 154 | CLYDE | 3635 | 570 | 5.9228
260 | 220 | SA JACKSON ST | 4250 | 214 | 5.771
261 | 44 | MERKEL | 1890 | 603 | 5.7496
262 | 95 | SA AVENUE N | 1695 | 1187 | 5.7313
263 | 257 | CISCO | 1675 | 901 | 5.727
264 | 283 | AB SHELTON ST | 3050 | 1272 | 5.7013
265 | 81 | KIRKLAND | 3545 | 39 | 5.6154
266 | 47 | SPUDDER FLAT | 4180 | 65 | 5.5846
267 | 318 | ABILENE PLANT | 1735 | 151 | 5.4305
268 | 299 | PRESIDIO | 4540 | 823 | 5.3329
269 | 102 | QUANAH | 1830 | 594 | 5.2997
270 | 150 | AB CANYON ROCK | 5035 | 685 | 5.2905
271 | 221 | BAIRD | 5125 | 682 | 5.239
272 | 10 | RIO PECOS | 513 | 40 | 5.225
273 | 261 | BRADSHAW (CLIMAX) | 11301 | 43 | 5.2093
274 | 244 | ALBANY | 2029 | 223 | 5.1883
275 | 397 | ASPERMONT | 6640 | 94 | 5.1064
276 | 386 | SONORA | 4805 | 559 | 5.0984
277 | 241 | VERNON | 1520 | 825 | 4.6291
278 | 142 | SA MATHIS FIELD | 4790 | 31 | 4.5161
279 | 252 | JAYTON | 6125 | 384 | 4.5156
280 | 397 | RANKIN | 6400 | 281 | 4.4591
281 | 275 | AB ELM CREEK | 1810 | 1451 | 4.4569
282 | 2 | ROTAN | 1865 | 362 | 4.2348
283 | 345 | FT CHADBOURNE | 6520 | 400 | 4.2175
284 | 322 | MCCAMEY | 2830 | 974 | 4.1253
285 | 120 | COLLEGE HILLS | 4840 | 490 | 4.0776
286 | 54 | SA MATHIS FIELD | 5100 | 237 | 4.0717
287 | 68 | SAND ROAD | 5295 | 427 | 3.9274
288 | 125 | GRAYBACK | 3315 | 321 | 3.8069
289 | 310 | AB ELM CREEK | 5045 | 606 | 3.7294
290 | 270 | ALBANY | 3540 | 580 | 3.6293
291 | 353 | HAROLD | 3055 | 99 | 3.5758
292 | 346 | CHILDRESS 69 | 4865 | 893 | 3.5588
293 | 36 | ROWENA | 4480 | 135 | 3.4625
294 | 298 | AB REBECCA LANE | 5555 | 1953 | 3.4347
295 | 294 | AB ELM CREEK | 4775 | 597 | 3.3786
296 | 101 | HEDLEY | 5845 | 322 | 3.3602
297 | 253 | AB OVER STREET 12KV | 3140 | 583 | 3.2607
298 | 397 | WINTERS | 2740 | 109 | 3.2385
299 | 296 | AB RAINEY CREEK | 4270 | 790 | 3.2038
300 | 139 | MARFA | 1900 | 776 | 3.2023
301 | 333 | AB SHELTON ST | 3435 | 338 | 3.1361
302 | 250 | AB MCMURRY | 4350 | 1145 | 3.0629
303 | 204 | PERKINS PROTHO | 5846 | 18 | 3.0556
304 | 219 | CLARENDON | 5005 | 764 | 3.0458
305 | 282 | AB WALNUT ST | 3785 | 1847 | 3.0314
306 | 337 | BEN FICKLIN | 6185 | 586 | 3.0171
307 | 392 | SONORA | 4810 | 826 | 2.9613
308 | 249 | ALBANY | 3655 | 669 | 2.9477
309 | 77 | SA JACKSON ST | 4685 | 2737 | 2.8699
310 | 391 | CHILDRESS 69 | 2800 | 713 | 2.8008
311 | 74 | CROWELL | 3490 | 52 | 2.7885
312 | 395 | AB EAST 12KV | 5760 | 1091 | 2.7305
313 | 157 | SARAGOSA | 1552 | 788 | 2.7272
314 | 141 | ABILENE PLANT | 1575 | 298 | 2.698
315 | 192 | AB ELM CREEK | 4745 | 725 | 2.6303
316 | 63 | STAMFORD | 4565 | 955 | 2.5267
317 | 313 | TURKEY | 3825 | 361 | 2.4875
318 | 170 | ASPERMONT | 3380 | 728 | 2.4698
319 | 51 | SAND ROAD | 5290 | 753 | 2.4316
320 | 84 | MUNDAY REA (BKEC) | 2015 | 56 | 2.4107
321 | 131 | AB MCMURRY | 4360 | 1263 | 2.1845
322 | 276 | SUN VALLEY | 4300 | 93 | 2.1398
323 | 397 | RANKIN | 6405 | 317 | 2.1388
324 | 158 | CLYDE | 1760 | 367 | 2.0954
325 | 236 | BIG LAKE | 4655 | 1087 | 2.0626
326 | 227 | SHAMROCK | 148 | 1100 | 2.0291
327 | 17 | SHAMROCK | 1835 | 75 | 1.9733
328 | 233 | SA AVENUE N | 1655 | 544 | 1.9412
329 | 202 | SA SOUTHLAND HILLS | 5455 | 624 | 1.9151
330 | 258 | CHILDRESS 20TH ST | 5720 | 124 | 1.9032
331 | 135 | PAULANN | 6285 | 58 | 1.8966
332 | 224 | AB SHELTON ST | 3660 | 600 | 1.8367
333 | 14 | DUNEFIELD (N CRANE) | 3885 | 52 | 1.8077
334 | 363 | PEACOCK | 43 | 50 | 1.8
335 | 279 | AB ELM CREEK | 1815 | 505 | 1.7941
336 | 58 | AB VOGEL ST | 4650 | 1013 | 1.7828
337 | 331 | SA SOUTHLAND HILLS | 5860 | 142 | 1.7324
338 | 187 | SA EMERSON ST | 4620 | 919 | 1.7312
339 | 181 | ROBERT LEE | 4120 | 286 | 1.6853
340 | 231 | TURKEY | 2980 | 381 | 1.6719
341 | 73 | MCCAMEY | 2855 | 110 | 1.5091
342 | 91 | HIGHLAND | 6375 | 188 | 1.4628
343 | 87 | SA GRAPE CREEK | 5220 | 702 | 1.4359
344 | 138 | SA SOUTH | 3990 | 318 | 1.3994
345 | 148 | CROWELL | 3980 | 761 | 1.3811
346 | 292 | CHILDRESS 20TH ST | 5725 | 694 | 1.3127
347 | 121 | ANSON 12KV | 6630 | 419 | 1.2959
348 | 311 | SPUR | 414 | 280 | 1.2107
349 | 347 | VERNON CITY PLANT | 5770 | 388 | 1.1134
350 | 338 | AB ELM CREEK | 1825 | 774 | 1.093
351 | 288 | STAMFORD | 2835 | 641 | 0.9532
352 | 317 | IRAAN | 2050 | 430 | 0.9
353 | New | ALPINE 12KV | 6825 | 1586 | 0.8947
354 | 134 | AB RAINEY CREEK | 4220 | 132 | 0.83333
355 | 20 | GRAYBACK | 3320 | 321 | 0.82555
356 | 103 | EDEN | 3195 | 513 | 0.82456
357 | 26 | WELLINGTON | 1765 | 856 | 0.81776
358 | 303 | SPUR | 5170 | 1155 | 0.81385
359 | 380 | EDEN | 1780 | 278 | 0.79856
360 | 397 | SHEFFIELD | 6430 | 208 | 0.70673
361 | 388 | CHILLICOTHE | 4525 | 621 | 0.68599
362 | 97 | TRENT | 4245 | 290 | 0.67586
363 | 147 | VERNON CITY PLANT | 5840 | 67 | 0.67164
364 | 64 | ROBERT LEE | 4125 | 684 | 0.59211
365 | 301 | AILEEN | 6435 | 496 | 0.56653
366 | 89 | SA EMERSON ST | 4625 | 211 | 0.51185
367 | 72 | WOODSON OIL FIELD | 30 | 40 | 0.475
368 | 259 | JUNCTION | 4335 | 608 | 0.46711
369 | 182 | SA LAKE DR | 6030 | 957 | 0.46499
370 | 319 | AB WALNUT ST | 3445 | 793 | 0.40479
371 | 329 | AB COUNTRY CLUB | 4735 | 504 | 0.31548
372 | 286 | PAINT ROCK | 5235 | 186 | 0.24731
373 | 287 | ABILENE PLANT | 1915 | 93 | 0.21505
374 | 136 | HASKELL 12KV | 5240 | 203 | 0.18227
375 | 325 | PAULANN | 6310 | 580 | 0.16724
376 | 177 | CHILDRESS 69 | 1480 | 426 | 0.14085
377 | 385 | AILEEN | 4600 | 798 | 0.13409
378 | 293 | WELLINGTON | 3700 | 644 | 0.099379
379 | 342 | ABILENE PLANT | 3175 | 296 | 0
380 | 389 | SA CONCHO | 1405 | 662 | 0
381 | 355 | CORINTH | 2590 | 28 | 0
382 | 351 | HAMLIN SHELL | 152 | 22 | 0
383 | 335 | MENARD | 3750 | 400 | 0
384 | 397 | ANSON 12KV | 310 | 589 | 0
385 | 397 | CROCKETT HEIGHTS | 346OCR | 64 | 0
386 | 397 | WEINERT | 3363 | 139 | 0
387 | 159 | PAINT CREEK | 3930 | 39 | 0
388 | 352 | HAMLIN SHELL | 6330 | 23 | 0
389 | 368 | VERNON CITY PLANT | 5835 | 67 | 0
390 | 358 | AB CANYON ROCK | 5025 | 40 | 0
391 | 377 | VERNON CITY PLANT | 5785 | 194 | 0
392 | 383 | SA CONCHO | 1725 | 345 | 0
393 | 191 | CAREY | 6115 | 122 | 0
394 | 397 | OAK CREEK #2 | 3213 | 706 | 0
395 | 373 | MEMPHIS | 12 | 119 | 0
396 | 307 | MEMPHIS | 11 | 168 | 0
397 | 265 | MELVIN | 4955 | 148 | 0
398 | 397 | ANSON 12KV | 311 | 419 | 0
399 | 397 | VALERA HUMBLE | 8201 | 78 | 0
400 | 260 | HIGHLAND | 6380 | 2127 | 0
401 | 397 | FT DAVIS | 3347 | 387 | 0
402 | 362 | VERNON CITY PLANT | 5830 | 49 | 0
403 | 378 | BIG LAKE | 4660 | 231 | 0
404 | 390 | SA CONCHO | 1710 | 701 | 0
405 | 372 | PADUCAH CITY | 13 | 104 | 0
406 | 330 | SA EMERSON ST | 4860 | 394 | 0
407 | 397 | PRESIDIO | 4535 | 1638 | 0
408 | 397 | EDITH HUMBLE | 3097 | 112 | 0
409 | 23 | FLOMOT | 4089 | 83 | 0
410 | New | ALPINE 12KV | 6820 | 681 | 0
411 | 375 | ABILENE PLANT | 1740 | 184 | 0
412 | 397 | CROSS PLAINS | 5130 | 61 | 0
413 | 339 | ROWENA | 7041 | 80 | 0
414 | 371 | ABILENE PLANT | 1580 | 88 | 0
415 | 397 | GIRARD | 6260 | 41 | 0

## Causes
AEP West Texas Utilities
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
2000 Reporting Year
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 14%
|  | Vegetation | 9.333%
|  | Animals and Birds | 18.67%
|  | People (Including cars and farm equip) | 4.667%
|  | Utility-owned Equipment | 30.67%
|  | Other | 6.667%
|  | Unknown | 16%