## Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | TEXAS-NEW MEXICO POWER COMPANY
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 265
Due: |  | February 14, 2001
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 23436
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Division
Commission Staff
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mailto:mel.eckhoff@puc.state.tx.us

## Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
2000 Reporting Year
TEXAS-NEW MEXICO POWER COMPANY
Project 23436

## System-SAIFI
TEXAS-NEW MEXICO POWER COMPANY
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2000 | 0.7435 | 0.0591 | 0.0367 | 0.0468 | 0.044 | 0.0807 | 0.1075 | 0.0937 | 0.0576 | 0.0619 | 0.0431 | 0.0675 | 0.0447
Scheduled
2000 | 0.022 | 0.0004 | 0.0006 | 0.0057 | 0.0006 | 0.0013 | 0.002 | 0.0096 | 0.0007 | 0.0008 | 0.0002 | 0 | 0.0001
Outside Causes
2000 | 0.0303 | 0 | 0 | 0 | 0 | 0.0092 | 0.0091 | 0 | 0.0004 | 0 | 0 | 0.0116 | 0
Major Events
2000 | 0.0997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0997

## System-SAIDI
TEXAS-NEW MEXICO POWER COMPANY
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2000 | 51.2638 | 5.5936 | 4.1173 | 3.8048 | 3.1555 | 5.1676 | 7.0739 | 5.3622 | 2.9861 | 4.1205 | 2.553 | 4.6467 | 2.6826
Scheduled
2000 | 0.9161 | 0.0262 | 0.0427 | 0.3411 | 0.09 | 0.1575 | 0.0454 | 0.0507 | 0.0601 | 0.0684 | 0.0082 | 0.0014 | 0.0243
Outside Causes
2000 | 2.2289 | 0 | 0 | 0 | 0.0003 | 0.5496 | 0.5477 | 0 | 0.0158 | 0 | 0 | 1.1155 | 0
Major Events
2000 | 145.0887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145.0887

## Feeder-SAIFI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System | [5 empty] | Total Number of Feeders
With More Than 10 Customers | [5 empty] | 265
Add or Delete Rows as Necessary
TEXAS-NEW MEXICO POWER COMPANY
2000 SAIFI Ranking | 1999 SAIFI Ranking | Substation Identification | Feeder Identification | Customer Interruptions | Num of Cust on Feeder | 2000 SAIFI Value
1 | 19 | SUBS-BG,TALCO WEST SUB | 13909 12.5 KV | 3339 | 451 | 7.4035
2 | 37 | DEPORT | 22164 22.0 KV | 9690 | 1685 | 5.7507
3 | 55 | SUBS-LW,JONES STREET SUB | 1412 12.5 KV | 5103 | 981 | 5.2018
4 | 14 | SUBS-BG,RED RIVER SUB | 2252 22.0 KV | 7431 | 1578 | 4.7091
5 | 79 | SUBS-LW,LAKEPOINTE SUB | 2508 25.0 KV | 1363 | 296 | 4.6047
6 | 7 | SUBS-PC,PYOTE SUB | 25P217 25.0 KV | 331 | 81 | 4.0864
7 | 16 | SUBS-PC,PYOTE SUB | 25P312 25.0 KV | 470 | 132 | 3.5606
8 | 131 | SUBS-BG,RED RIVER SUB | 2262 22.0 KV | 324 | 91 | 3.5604
9 | 1 | SUBS-PC,FLAT TOP SUB | 26P02 25.0 KV | 254 | 81 | 3.1358
10 | 10 | SUBS-PC,COCHISE SUB | 25P47 25.0 KV | 60 | 20 | 3
11 | 6 | SUBS-PC,FLAT TOP SUB | 26P01 25.0 KV | 326 | 115 | 2.8348
12 | 13 | SUBS-WC,WEST COLUMBIA SUB | 1234 12.5 KV | 2452 | 971 | 2.5252
13 | 216 | SUBS-WI,WHITNEY #1 SUB | 22450 22.0 KV | 1882 | 767 | 2.4537
14 | 18 | SUBS-PC,STAFFORD SUB | 12P83 12.5 KV | 1065 | 439 | 2.426
15 | 172 | SUBS-TC,TEJAS SUB | 1212 12.5 KV | 798 | 337 | 2.368
16 | 42 | SUBS-LW,WEST SUB | 1235 12.5 KV | 2887 | 1228 | 2.351
17 | 59 | SUBS-LW,SOUTH SUB | 1102 12.5 KV | 3545 | 1613 | 2.1978
18 | 195 | SUBS-GT,GATESVILLE #2 SUB | 22725 22.0 KV | 1864 | 853 | 2.1852
19 | 248 | SUBS-LW,LAKEPOINTE SUB | 2512 25.0 KV | 2843 | 1338 | 2.1248
20 | 120 | EMORY TU | TU-1201 12.5 KV | 2852 | 1352 | 2.1095
21 | 257 | SUBS-KR,WINKLER CO. NO.6 SUB | 25K11 25.0 KV | 99 | 47 | 2.1064
22 | 89 | SUBS-AG,ANGLETON SUB | 1240 12.5 KV | 2746 | 1341 | 2.0477
23 | 26 | SUBS-LW,WEST SUB | 1234 12.5 KV | 1845 | 912 | 2.023
24 | 64 | SUBS-LW,SOUTH SUB | 1104 12.5 KV | 6183 | 3091 | 2.0003
25 | 137 | SUBS-GT,SYCAMORE SUB | 24105 25.0 KV | 215 | 108 | 1.9907
26 | 71 | SUBS-KR,WICKETT SUB | 12K449 12.5 KV | 345 | 180 | 1.9167
27 | 142 | SUBS-WW,WHITEWRIGHT SUB | 12574 12.5 KV | 293 | 171 | 1.7135
28 | 90 | SUBS-WC,OLD OCEAN SUB | 1260 12.5 KV | 746 | 442 | 1.6878
29 | 155 | SUBS-CL,HANDLEY 22KV SUB | 22825 22.0 KV | 166 | 101 | 1.6436
30 | 40 | SUBS-TC,NORTHSIDE SUB | 1293 12.5 KV | 1020 | 631 | 1.6165
31 | 12 | SUBS-LW,SOUTH SUB | 1103 12.5 KV | 2175 | 1389 | 1.5659
32 | 8 | SUBS-DC,LEAGUE CITY SUB | 1281 12.5 KV | 1247 | 798 | 1.5627
33 | 17 | SUBS-PC,LONE STAR SUB | 25P171 25.0 KV | 68 | 47 | 1.4468
34 | 140 | SUBS-WC,SWEENY SUB | 1129 12.5 KV | 929 | 651 | 1.427
35 | 125 | SUBS-FR,BELDING SUB | 12F161 12.5 KV | 68 | 48 | 1.4167
36 | 103 | SUBS-FI,FRIENDSWOOD SUB | 1253 12.5 KV | 1527 | 1088 | 1.4035
37 | 45 | SUBS-SR,THURBER 22KV SUB | 1490 22.0 KV | 1228 | 884 | 1.3891
38 | 41 | SUBS-PC,REEVES CO. NO.4 SUB | 13P37 12.5 KV | 136 | 99 | 1.3737
39 | 132 | SUBS-TC,NORTHSIDE SUB | 1295 12.5 KV | 1974 | 1447 | 1.3642
40 | 35 | SUBS-TC,TEJAS SUB | 1215 12.5 KV | 2137 | 1569 | 1.362
41 | 95 | SUBS-FI,FRIENDSWOOD SUB | 1251 12.5 KV | 2114 | 1568 | 1.3482
42 | 21 | SUBS-FI,ALVIN SUB | 1230 12.5 KV | 1789 | 1346 | 1.3291
43 | 88 | SUBS-DC,DICKINSON SUB | 1267 12.5 KV | 1037 | 787 | 1.3177
44 | 143 | SUBS-TC,LAMARQUE SUB | 1202 12.5 KV | 700 | 532 | 1.3158
45 | 146 | SUBS-TC,NORTHSIDE SUB | 1292 12.5 KV | 1655 | 1259 | 1.3145
46 | 141 | SUBS-AG,ANGLETON SUB | 1241 12.5 KV | 1818 | 1414 | 1.2857
47 | 68 | SUBS-TC,LAMARQUE SUB | 1110 12.5 KV | 396 | 313 | 1.2652
48 | 46 | SUBS-TC,LAMARQUE SUB | 1205 12.5 KV | 1162 | 954 | 1.218
49 | 198 | SUBS-WC,SWEENY SUB | 1263 12.5 KV | 683 | 571 | 1.1961
50 | 39 | SUBS-PI,CLIMAX SUB | 2270 22.0 KV | 398 | 334 | 1.1916
51 | 159 | SUBS-AG,ANGLETON SUB | 1153 12.5 KV | 1629 | 1370 | 1.1891
52 | 53 | SUBS-TC,NORTHSIDE SUB | 1228 12.5 KV | 1687 | 1431 | 1.1789
53 | 203 | SUBS-TC,TEJAS SUB | 1217 12.5 KV | 719 | 613 | 1.1729
54 | 150 | SUBS-FI,FRIENDSWOOD SUB | 1252 12.5 KV | 1674 | 1443 | 1.1601
55 | 58 | SUBS-PC,W.D. FAULKNER SUB | 12P259 12.5 KV | 154 | 135 | 1.1407
56 | 34 | SUBS-TC,LAMARQUE SUB | 1204 12.5 KV | 1553 | 1367 | 1.1361
57 | 107 | SUBS-WI,HILL CO SUB | 22125 22.0 KV | 318 | 284 | 1.1197
58 | 192 | SUBS-TC,FREEWAY PARK SUB | 1101 12.5 KV | 1557 | 1416 | 1.0996
59 | 123 | SUBS-GE,GLEN ROSE #3 SUB | 23875 25.0 KV | 993 | 906 | 1.096
60 | 139 | SUBS-FR,DOWNTOWN SUB | 12F130 12.5 KV | 767 | 700 | 1.0957
61 | 112 | SUBS-PI,CLIMAX SUB | 22110 22.0 KV | 1526 | 1400 | 1.09
62 | 47 | SUBS-FR,PUCKETT SUB | 25F14 25.0 KV | 13 | 12 | 1.0833
63 | 73 | SUBS-GE,GLEN ROSE #2 SUB | 22305 22.0 KV | 890 | 830 | 1.0723
64 | 232 | SUBS-GT,CORYELL #1 SUB | 22155 22.0 KV | 634 | 592 | 1.0709
65 | 29 | SUBS-LW,LAKEPOINTE SUB | 2536 25.0 KV | 106 | 99 | 1.0707
66 | 224 | SUBS-WI,WHITNEY #1 SUB | 22455 22.0 KV | 456 | 427 | 1.0679
67 | 193 | SUBS-PC,COCHISE SUB | 25P48 25.0 KV | 274 | 258 | 1.062
68 | 218 | SUBS-GT,CORYELL CO #1 SUB | 22160 22.0 KV | 71 | 67 | 1.0597
69 | 212 | SUBS-PC,PECOS MAIN SUB | 2P03 2.4 KV | 368 | 350 | 1.0514
70 | 20 | SUBS-PC,LONE STAR SUB | 25P174 25.0 KV | 29 | 28 | 1.0357
71 | 133 | SUBS-WC,WEST COLUMBIA SUB | 1233 12.5 KV | 718 | 700 | 1.0257
72 | 252 | SUBS-LO,FRONTIER SUB | 4236 4.0 KV | 360 | 355 | 1.0141
73 | 36 | SUBS-PC,REEVES CO. NO.4 SUB | 12P28 12.5 KV | 143 | 142 | 1.007
74 | 65 | SUBS-LW,WEST SUB | 1233 12.5 KV | 511 | 510 | 1.002
75 | 246 | SUBS-VL,VALLEY MILLS SUB | 22565 22.0 KV | 560 | 559 | 1.0018
76 | 69 | SUBS-LW,TI SUB | 1012 12.5 KV | 2223 | 2219 | 1.0018
77 | 82 | SUBS-LW,WEST SUB | 1222 12.5 KV | 974 | 973 | 1.001
78 | 178 | SUBS-LO,LEONARD SUB | 12682 12.5 KV | 265 | 265 | 1
79 | 51 | SUBS-LW,WEST SUB | 1221 12.5 KV | 692 | 702 | 0.9858
80 | 27 | SUBS-LO,LEONARD SUB | 12678 12.5 KV | 562 | 599 | 0.9382
81 | 50 | SUBS-DC,DICKINSON SUB | 1274 12.5 KV | 1130 | 1402 | 0.806
82 | 128 | SUBS-AG,ANGLETON SUB | 1155 12.5 KV | 565 | 709 | 0.7969
83 | 92 | SUBS-GE,GLEN ROSE #2 SUB | 22300 22.0 KV | 844 | 1061 | 0.7955
84 | 102 | SUBS-WC,SWEENY SUB | 1128 12.5 KV | 510 | 643 | 0.7932
85 | 56 | SUBS-PC,WORSHAM FIELD SUB | 13P98 12.5 KV | 55 | 73 | 0.7534
86 | 165 | SUBS-AG,ANGLETON SUB | 1154 12.5 KV | 1481 | 2031 | 0.7292
87 | 202 | SUBS-LW,LAKEPOINTE SUB | 2516 25.0 KV | 533 | 745 | 0.7154
88 | 4 | SUBS-SN,SANDERSON SUB | 4S27 4.0 KV | 74 | 105 | 0.7048
89 | 93 | SUBS-HM,HAMILTON COUNTY SUB | 2340 2.4 KV | 93 | 132 | 0.7045
90 | 207 | SUBS-ON,OLNEY SWCH STA | 1431 12.5 KV | 546 | 784 | 0.6964
91 | 111 | SUBS-DC,DICKINSON SUB | 1277 12.5 KV | 843 | 1285 | 0.656
92 | 185 | SUBS-ON,OLNEY SWCH STA | 1685 12.5 KV | 353 | 569 | 0.6204
93 | 97 | SUBS-MR,WALNUT SPRINGS 22KV | 2210 22.0 KV | 239 | 403 | 0.5931
94 | 63 | SUBS-DC,DICKINSON SUB | 1272 12.5 KV | 603 | 1039 | 0.5804
95 | 226 | SUBS-WW,WHITEWRIGHT SUB | 12698 12.5 KV | 339 | 609 | 0.5567
96 | 197 | SUBS-FR,AIRPORT SUB | 12F271 12.5 KV | 186 | 340 | 0.5471
97 | 57 | SUBS-WC,BRAZORIA SUB | 1291 12.5 KV | 236 | 464 | 0.5086
98 | 196 | SUBS-BR,BRYSONS SUB | 1230 12.5 KV | 271 | 538 | 0.5037
99 | 199 | SUBS-KR,KERMIT NO. 2 SUB | 12K48 12.5 KV | 245 | 487 | 0.5031
100 | 201 | SUBS-WW,BLUE RIDGE SUB | 22700 22.0 KV | 165 | 334 | 0.494
101 | 91 | SUBS-FI,ALVIN SUB | 1257 12.5 KV | 818 | 1685 | 0.4855
102 | 134 | SUBS-WC,WEST COLUMBIA SUB | 1237 12.5 KV | 499 | 1065 | 0.4685
103 | 175 | SUBS-NC,SAINT JO SUB | 408 4.0 KV | 95 | 205 | 0.4634
104 | 124 | SUBS-WC,WEST COLUMBIA SUB | 1235 12.5 KV | 318 | 689 | 0.4615
105 | 94 | SUBS-EO,LONE OAK SUB | 13384 12.5 KV | 175 | 385 | 0.4545
106 | 254 | SUBS-WW,WHITEWRIGHT SUB | 12753 12.5 KV | 55 | 122 | 0.4508
107 | 163 | SUBS-WI,HILL CO SUB | 23340 22.0 KV | 373 | 850 | 0.4388
108 | 11 | SUBS-WC,BRAZORIA SUB | 1271 12.5 KV | 722 | 1652 | 0.437
109 | 161 | SUBS-TC,FREEWAY PARK SUB | 1102 12.5 KV | 90 | 208 | 0.4327
110 | 9 | SUBS-WC,BRAZORIA SUB | 1270 12.5 KV | 597 | 1430 | 0.4175
111 | 121 | SUBS-DC,DICKINSON SUB | 1279 12.5 KV | 521 | 1271 | 0.4099
112 | 30 | SUBS-PC,WORSHAM FIELD SUB | 13P97 12.5 KV | 25 | 64 | 0.3906
113 | 184 | SUBS-PC,STAFFORD SUB | 13P50 12.5 KV | 97 | 250 | 0.388
114 | 126 | SUBS-FI,ALVIN SUB | 1117 12.5 KV | 546 | 1414 | 0.3861
115 | 44 | SUBS-GE,GLEN ROSE #1 SUB | 22295 22.0 KV | 255 | 661 | 0.3858
116 | 66 | SUBS-FR,DOWNTOWN SUB | 12F114 12.5 KV | 297 | 800 | 0.3713
117 | 160 | SUBS-WC,OLD OCEAN SUB | 1261 12.5 KV | 58 | 165 | 0.3515
118 | 114 | SUBS-PI,CLIMAX SUB | 2267 22.0 KV | 164 | 469 | 0.3497
119 | 153 | SUBS-FI,ALVIN SUB | 1259 12.5 KV | 252 | 723 | 0.3485
120 | 23 | SUBS-BR,BRYSONS SUB | 1233 12.5 KV | 44 | 127 | 0.3465
121 | 188 | SUBS-TC,HEIGHTS SUB | 1134 12.5 KV | 294 | 884 | 0.3326
122 | 145 | SUBS-FR,16TH STREET SUB | 13F14 12.5 KV | 299 | 920 | 0.325
123 | 158 | SUBS-TC,FREEWAY PARK SUB | 1299 12.5 KV | 222 | 686 | 0.3236
124 | 171 | SUBS-TC,FREEWAY PARK SUB | 1103 12.5 KV | 416 | 1313 | 0.3168
125 | 108 | SUBS-FI,FRIENDSWOOD SUB | 1107 12.5 KV | 372 | 1192 | 0.3121
126 | 119 | SUBS-PC,PECOS MAIN SUB | 12P02 12.5 KV | 308 | 1011 | 0.3046
127 | 211 | SUBS-PC,STAFFORD SUB | 12P82 12.5 KV | 78 | 258 | 0.3023
128 | 117 | SUBS-AG,ANGLETON SUB | 1244 12.5 KV | 308 | 1021 | 0.3017
129 | 72 | SUBS-MR,MERIDIAN 22KV SUB | 23210 22.0 KV | 209 | 699 | 0.299
130 | 130 | SUBS-FI,ALVIN SUB | 1116 12.5 KV | 608 | 2069 | 0.2939
131 | 241 | SUBS-CL,HANDLEY 22KV SUB | 22820 22.0 KV | 8 | 29 | 0.2759
132 | 98 | SUBS-NC,NOCONA SUB | 13374 12.5 KV | 189 | 704 | 0.2685
133 | 179 | SUBS-HM,HAMILTON COUNTY SUB | 2345 2.4 KV | 31 | 116 | 0.2672
134 | 33 | SUBS-HC,HICO CITY SUB | 390 4.0 KV | 96 | 367 | 0.2616
135 | 96 | SUBS-FR,GOMEZ SUB | 25F05 25.0 KV | 6 | 23 | 0.2609
136 | 60 | SUBS-SR,THURBER 12.5KV SUB | 1447 12.5 KV | 157 | 611 | 0.257
137 | 24 | SUBS-TC,HEIGHTS SUB | 1132 12.5 KV | 240 | 937 | 0.2561
138 |  | SUBS-FI,FRIENDSWOOD SUB | 1109 12.5 | 313 | 1267 | 0.247
139 | 209 | SUBS-MR,WALNUT SPRINGS 12.5 | 1270 12.5 KV | 8 | 33 | 0.2424
140 | 149 | SUBS-FI,FRIENDSWOOD SUB | 1108 12.5 KV | 406 | 1695 | 0.2395
141 | 135 | SUBS-NC,NOCONA SUB | 12490 12.5 KV | 96 | 402 | 0.2388
142 | 174 | ELIASVILLE POD | 1300 12.5 KV | 38 | 163 | 0.2331
143 | 115 | SUBS-PL,KRUGERVILLE SUB | 2604 22.0 KV | 304 | 1307 | 0.2326
144 | 151 | SUBS-FI,MAGNOLIA SUB | 1144 12.5 KV | 250 | 1101 | 0.2271
145 | 109 | SUBS-FI,ALVIN SUB | 1115 12.5 KV | 277 | 1225 | 0.2261
146 | 105 | SUBS-DC,DICKINSON SUB | 1266 12.5 KV | 109 | 489 | 0.2229
147 | 101 | SUBS-TC,FREEWAY PARK SUB | 1298 12.5 KV | 239 | 1108 | 0.2157
148 | 189 | SUBS-HM,HAMILTON COUNTY SUB | 24015 25.0 KV | 56 | 260 | 0.2154
149 | 25 | SUBS-PC,PECOS MAIN SUB | 12P01 12.5 KV | 23 | 107 | 0.215
150 | 169 | SUBS-FR,16TH STREET SUB | 12F72 12.5 KV | 47 | 220 | 0.2136
151 | 52 | SUBS-GT,CORYELL CO #2 SUB | 22365 22.0 KV | 117 | 561 | 0.2086
152 | 99 | SUBS-FI,MAGNOLIA SUB | 1145 12.5 KV | 364 | 1774 | 0.2052
153 | 116 | SUBS-NC,NOCONA SUB | 13610 12.5 KV | 139 | 693 | 0.2006
154 | 148 | SUBS-WC,SWEENY SUB | 1264 12.5 KV | 224 | 1130 | 0.1982
155 | 164 | SUBS-NC,NOCONA SUB | 13370 12.5 KV | 126 | 671 | 0.1878
156 | 129 | SUBS-FR,16TH STREET SUB | 12F71 12.5 KV | 193 | 1050 | 0.1838
157 | 177 | SUBS-FI,ALVIN SUB | 1232 12.5 KV | 204 | 1120 | 0.1821
158 | 110 | SUBS-DC,LEAGUE CITY SUB | 1282 12.5 KV | 324 | 1827 | 0.1773
159 | 113 | SUBS-TC,NORTHSIDE SUB | 1294 12.5 KV | 176 | 1006 | 0.175
160 | 22 | SUBS-FR,PUCKETT SUB | 25F18 25.0 KV | 6 | 36 | 0.1667
161 | 217 | SUBS-BG,RED RIVER SUB | 2229 22.0 KV | 72 | 451 | 0.1596
162 | 138 | SUBS-TC,LAMARQUE SUB | 1201 12.5 KV | 139 | 878 | 0.1583
163 | 83 | SUBS-HC,HICO CITY SUB | 395 4.0 KV | 98 | 619 | 0.1583
164 | 65 | SUBS-AG,ANGLETON SUB | 1242 12.5 KV | 217 | 1389 | 0.1562
165 | 168 | SUBS-DC,LEAGUE CITY SUB | 1283 12.5 KV | 258 | 1718 | 0.1502
166 | 157 | SUBS-FI,ALVIN SUB | 1231 12.5 KV | 262 | 1781 | 0.1471
167 | 104 | SUBS-DC,LEAGUE CITY SUB | 1285 12.5 KV | 249 | 1732 | 0.1438
168 | 38 | SUBS-TC,FREEWAY PARK SUB | 1297 12.5 KV | 51 | 366 | 0.1393
169 | 122 | SUBS-LW,JONES STREET SUB | 1411 12.5 KV | 202 | 1466 | 0.1378
170 | 106 | SUBS-AG,ANGLETON SUB | 1243 12.5 KV | 168 | 1327 | 0.1266
171 | 127 | SUBS-FI,ALVIN SUB | 1254 12.5 KV | 166 | 1360 | 0.1221
172 | 231 | SUBS-LO,LEONARD SUB | 14635 12.5 KV | 65 | 558 | 0.1165
173 | 233 | SUBS-WW,WHITEWRIGHT SUB | 12575 12.5 KV | 70 | 622 | 0.1125
174 | 144 | SUBS-ON,GRAHAM SUB | 12605 12.5 KV | 15 | 134 | 0.1119
175 | 204 | SUBS-LW,SOUTH SUB | 1107 12.5 KV | 205 | 1899 | 0.108
176 | 87 | SUBS-PL,KRUGERVILLE SUB | 2608 25.0 KV | 191 | 1850 | 0.1032
177 | 100 | SUBS-ON,GRAHAM SUB | 1245 12.5 KV | 21 | 206 | 0.1019
178 | 86 | SUBS-NC,PETROLIA SUB | 12260 12.5 KV | 76 | 751 | 0.1012
179 | 253 | SUBS-LO,TRENTON SUB | 4120 4.0 KV | 21 | 209 | 0.1005
180 | 84 | SUBS-SR,THURBER 22KV SUB | 22890 22.0 KV | 20 | 199 | 0.1005
181 | 255 | SUBS-WW,WHITEWRIGHT SUB | 13563 12.5 KV | 42 | 433 | 0.097
182 | 205 | SUBS-LW,JONES STREET SUB | 1413 12.5 KV | 91 | 944 | 0.0964
183 | 262 | SUBS-PC,STAFFORD SUB | 12P99 12.5 KV | 22 | 229 | 0.0961
184 | 154 | SUBS-DC,SOUTH SHORE SUB | 1190 12.5 KV | 228 | 2510 | 0.0908
185 | 223 | SUBS-LW,SOUTH SUB | 1108 12.5 KV | 208 | 2367 | 0.0879
186 | 183 | SUBS-WI,WHITNEY #2 SUB | 22460 22.0 KV | 27 | 311 | 0.0868
187 | 31 | SUBS-HM,HAMILTON CITY #2 22 | 23820 25.0 KV | 31 | 364 | 0.0852
188 | 186 | SUBS-TC,HEIGHTS SUB | 1224 12.5 KV | 100 | 1198 | 0.0835
189 | 32 | SUBS-LW,WEST SUB | 1223 12.5 KV | 118 | 1418 | 0.0832
190 | 48 | SUBS-WC,BRAZORIA SUB | 1290 12.5 KV | 75 | 907 | 0.0827
191 | 238 | SUBS-CL,CLIFTON #1 22 KV | 22495 22.0 KV | 22 | 275 | 0.08
192 | 215 | SUBS-GT,GATESVILLE #1 4KV | 422 4.0 KV | 15 | 191 | 0.0785
193 | 115 | SUBS-DC,LEAGUE CITY SUB | 1284 12.5 KV | 47 | 645 | 0.0729
194 | 118 | SUBS-DC,LEAGUE CITY SUB | 1280 12.5 KV | 58 | 804 | 0.0721
195 | 152 | SUBS-TC,TEJAS SUB | 1214 12.5 KV | 32 | 447 | 0.0716
196 | 208 | SUBS-LW,TI SUB | 1033 12.5 | 124 | 1831 | 0.0677
197 | 180 | SUBS-TC,HEIGHTS SUB | 1222 12.5 KV | 37 | 589 | 0.0628
198 | 147 | SUBS-DC,SOUTH SHORE SUB | 1192 12.5 KV | 82 | 1344 | 0.061
199 | 77 | SUBS-KR,KERMIT NO.1 SUB | 4K04 4.0 KV | 25 | 425 | 0.0588
200 | 176 | SUBS-LW,WEST SUB | 1201 12.5 KV | 63 | 1101 | 0.0572
201 | 156 | SUBS-TC,LAMARQUE SUB | 1203 12.5 KV | 19 | 336 | 0.0565
202 | 220 | SUBS-LW,WEST SUB | 1203 12.5 KV | 41 | 775 | 0.0529
203 | 61 | SUBS-KR,WICKETT SUB | 12K446 12.5 KV | 1 | 20 | 0.05
204 | 210 | SUBS-FR,AIRPORT SUB | 12F44 12.5 KV | 45 | 915 | 0.0492
205 | 227 | SUBS-CL,LAKE WHITNEY SUB | 1230 12.5 KV | 26 | 537 | 0.0484
206 | 187 | SUBS-CL,LAKE WHITNEY SUB | 12355 12.5 KV | 43 | 890 | 0.0483
207 | 214 | SUBS-PC,PECOS MAIN SUB | 12P03 12.5 KV | 15 | 320 | 0.0469
208 | 173 | SUBS-FI,MAGNOLIA SUB | 1150 12.5 KV | 5 | 116 | 0.0431
209 | 250 | SUBS-LW,WEST SUB | 1202 12.5 KV | 45 | 1049 | 0.0429
210 | 228 | SUBS-ON,OLNEY SWCH STA | 1690 12.5 KV | 22 | 543 | 0.0405
211 | 43 | SUBS-KR,CALIFORNIA SUB | 12K87 12.5 KV | 2 | 52 | 0.0385
212 | 221 | SUBS-KR,KERMIT NO. 2 SUB | 4K06 4.0 KV | 6 | 160 | 0.0375
213 | 167 | SUBS-FI,MAGNOLIA SUB | 1149 12.5 KV | 70 | 1942 | 0.036
214 | 194 | SUBS-VL,VALLEY MILLS SUB | 22575 22.0 KV | 15 | 466 | 0.0322
215 | 229 | SUBS-MR,WALNUT SPRINGS 22KV | 2215 22.0 KV | 7 | 227 | 0.0308
216 | 28 | SUBS-KR,KERMIT NO.1 SUB | 4K03 4.0 KV | 6 | 200 | 0.03
217 | 242 | SUBS-GT,GATESVILLE #1 4KV | 413 4.0 KV | 5 | 167 | 0.0299
218 | 190 | SUBS-NC,SAINT JO SUB | 401 4.0 KV | 13 | 461 | 0.0282
219 | 234 | SUBS-KR,KERMIT NO. 2 SUB | 12K98 12.5 KV | 11 | 396 | 0.0278
220 | 191 | SUBS-LW,SOUTH SUB | 1109 12.5 KV | 19 | 707 | 0.0269
221 | 206 | SUBS-LW,TI SUB | 1032 12.5 KV | 71 | 2662 | 0.0267
222 | 166 | SUBS-AG,ANGLETON SUB | 1245 12.5 KV | 15 | 598 | 0.0251
223 | 136 | SUBS-NC,NOCONA SUB | 12486 12.5 KV | 5 | 234 | 0.0214
224 | 170 | SUBS-DC,SOUTH SHORE SUB | 1195 12.5 KV | 17 | 1135 | 0.015
225 | 181 | SUBS-HM,HAMILTON CITY #1 22 | 22780 22.0 KV | 11 | 784 | 0.014
226 | 260 | SUBS-PC,PECOS MAIN SUB | 2P06 2.4 KV | 3 | 220 | 0.0136
227 | 3 | SUBS-SN,SANDERSON SUB | 4S26 4.0 KV | 3 | 235 | 0.0128
228 | 244 | SUBS-GT,GATESVILLE #2 4KV | 429 4.0 KV | 4 | 317 | 0.0126
229 | 225 | SUBS-LO,LEONARD SUB | 14631 12.5 KV | 3 | 273 | 0.011
230 | 219 | SUBS-MR,WALNUT SPRINGS 22KV | 2200 22.0 KV | 4 | 407 | 0.0098
231 | 237 | SUBS-CL,CLIFTON #1 22 KV | 22485 22.0 KV | 1 | 179 | 0.0056
232 | 78 | SUBS-MR,MERIDIAN 4KV SUB | 680 4.0 KV | 2 | 387 | 0.0052
233 | 182 | SUBS-PC,PECOS MAIN SUB | 12P362 12.5 KV | 5 | 1040 | 0.0048
234 | 49 | SUBS-HM,HAMILTON CITY #1 22 | 22785 22.0 KV | 1 | 251 | 0.004
235 | 222 | SUBS-GT,GATESVILLE #1 4KV | 419 4.0 KV | 1 | 247 | 0.004
236 | 75 | SUBS-KR,KEYSTONE SUB | 12K437 12.5 KV | 2 | 575 | 0.0035
237 | 249 | SUBS-LW,LAKEPOINTE SUB | 2532 25.0 KV | 1 | 594 | 0.0017
238 | 74 | SUBS-CL,CLIFTON #2 22KV | 23165 22.0 KV | 0 | 30 | 0
239 | 235 | SUBS-CL,CLIFTON #2 4KV | 4160 4.0 KV | 0 | 439 | 0
240 | 236 | SUBS-CL,CLIFTON #2 4KV | 4165 4.0 KV | 0 | 482 | 0
241 | 54 | SUBS-CL,CLIFTON #1 22 KV | 22480 22.0 KV | 0 | 86 | 0
242 | 239 | SUBS-CL,CLIFTON #1 4KV SUB | 405 4.0 KV | 0 | 100 | 0
243 | 230 | SUBS-CL,CLIFTON #1 4KV SUB | 407 4.0 KV | 0 | 482 | 0
244 | 240 | SUBS-CL,CLIFTON #1 4KV SUB | 490 4.0 KV | 0 | 27 | 0
245 | 200 | SUBS-GT,GATESVILLE #2 SUB | 23065 22.0 KV | 0 | 88 | 0
246 | 243 | SUBS-GT,GATESVILLE #2 4KV | 426 4.0 KV | 0 | 296 | 0
247 | 245 | SUBS-GT,SYCAMORE SUB | 24100 25.0 KV | 0 | 42 | 0
248 | 213 | SUBS-HM,HAMILTON CITY #2 22 | 23825 25.0 KV | 0 | 125 | 0
249 | 67 | SUBS-MR,MERIDIAN 22KV SUB | 23205 22.0 KV | 0 | 131 | 0
250 | 80 | SUBS-MR,MERIDIAN 4KV SUB | 690 4.0 KV | 0 | 287 | 0
251 | 85 | SUBS-VL,VALLEY MILLS SUB | 22570 22.0 KV | 0 | 414 | 0
252 | 247 | SUBS-WI,WHITNEY #2 SUB | 22469 22.0 KV | 0 | 123 | 0
253 | 251 | SUBS-EO,LONE OAK SUB | 13388 12.5 KV | 0 | 43 | 0
254 |  | SUBS-WC,CLEMONS DOME SUB | 1175 12.5 KV | 0 | 12 | 0
255 | 81 | SUBS-KR,CALIFORNIA SUB | 12K86 12.5 KV | 0 | 47 | 0
256 | 256 | SUBS-KR,KERMIT NO. 2 SUB | 4K07 4.0 KV | 0 | 385 | 0
257 | 70 | SUBS-KR,KERMIT NO.1 SUB | 4K02 4.0 KV | 0 | 180 | 0
258 | 76 | SUBS-KR,KERMIT NO.1 SUB | 4K05 4.0 KV | 0 | 375 | 0
259 | 258 | SUBS-PC,PECOS MAIN SUB | 2P04 2.4 KV | 0 | 111 | 0
260 | 259 | SUBS-PC,PECOS MAIN SUB | 2P05 2.5 KV | 0 | 44 | 0
261 | 261 | SUBS-PC,STAFFORD SUB | 12P50 12.5 KV | 0 | 250 | 0
262 | 162 | SUBS-FR,DOWNTOWN SUB | 4F52 4.0 KV | 0 | 175 | 0
263 | 263 | SUBS-FR,GOMEZ SUB | 25F61 25.0 KV | 0 | 13 | 0
264 | 2 | SUBS-SN,SANDERSON SUB | 4S28 4.0 KV | 0 | 310 | 0
265 | 264 | SUBS-CL,CLIFTON#2 22KV | 24370 22.0 | 0 | 176 | 0

## Feeder-SAIDI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System |  |  |  |  | Total Number of Feeders
With More Than 10 Customers |  |  |  |  | 265
Add or Delete Rows as Necessary
TEXAS-NEW MEXICO POWER COMPANY
2000 SAIDI Ranking | 1999 SAIDI Ranking | Substation Identification | Feeder Identification | Num of Cust on Feeder | 2000 SAIDI Value
1 | 76 | SUBS-KR,WICKETT SUB | 12K449 12.5 KV | 180 | 885.1556
2 | 15 | SUBS-BG,TALCO WEST SUB | 13909 12.5 KV | 451 | 471.1064
3 | 33 | DEPORT | 22164 22.0 KV | 1685 | 436.0184
4 | 10 | SUBS-PC,PYOTE SUB | 25P217 25.0 KV | 81 | 370.321
5 | 52 | SUBS-PC,W.D. FAULKNER SUB | 12P259 12.5 KV | 135 | 354.4074
6 | 14 | SUBS-PC,PYOTE SUB | 25P312 25.0 KV | 132 | 351.7803
7 | 5 | SUBS-PC,FLAT TOP SUB | 26P02 25.0 KV | 81 | 349.3086
8 | 69 | SUBS-BG,RED RIVER SUB | 2252 22.0 KV | 1578 | 318.91
9 | 171 | SUBS-GT,SYCAMORE SUB | 24105 25.0 KV | 108 | 315.3704
10 | 57 | SUBS-BG,RED RIVER SUB | 2262 22.0 KV | 91 | 300.8791
11 | 108 | SUBS-FR,BELDING SUB | 12F161 12.5 KV | 48 | 294.5625
12 | 40 | SUBS-LW,JONES STREET SUB | 1412 12.5 KV | 981 | 290.7441
13 | 6 | SUBS-PC,FLAT TOP SUB | 26P01 25.0 KV | 115 | 268.1913
14 | 50 | SUBS-LW,LAKEPOINTE SUB | 2508 25.0 KV | 296 | 252.7534
15 | 248 | SUBS-LW,LAKEPOINTE SUB | 2512 25.0 KV | 1338 | 233.3027
16 | 126 | EMORY TU | TU-1201 12.5 KV | 1352 | 231.088
17 | 170 | SUBS-TC,TEJAS SUB | 1212 12.5 KV | 337 | 196.3027
18 | 39 | SUBS-WC,OLD OCEAN SUB | 1260 12.5 KV | 442 | 194.2873
19 | 257 | SUBS-KR,WINKLER CO. NO.6 SUB | 25K11 25.0 KV | 47 | 182.7021
20 | 77 | SUBS-GE,GLEN ROSE #2 SUB | 22305 22.0 KV | 830 | 158.8084
21 | 46 | SUBS-LW,WEST SUB | 1222 12.5 KV | 973 | 157.6053
22 | 191 | SUBS-ON,OLNEY SWCH STA | 1685 12.5 KV | 569 | 155.58
23 | 61 | SUBS-LW,LAKEPOINTE SUB | 2536 25.0 KV | 99 | 150.4141
24 | 18 | SUBS-WC,WEST COLUMBIA SUB | 1234 12.5 KV | 971 | 149.1998
25 | 97 | SUBS-FI,FRIENDSWOOD SUB | 1253 12.5 KV | 1088 | 148.4559
26 | 47 | SUBS-PC,STAFFORD SUB | 12P83 12.5 KV | 439 | 139.467
27 | 150 | SUBS-WW,WHITEWRIGHT SUB | 12574 12.5 KV | 171 | 139.0409
28 | 81 | SUBS-TC,LAMARQUE SUB | 1205 12.5 KV | 954 | 134.0629
29 | 60 | SUBS-GE,GLEN ROSE #2 SUB | 22300 22.0 KV | 1061 | 131.7201
30 | 42 | SUBS-PC,REEVES CO. NO.4 SUB | 13P37 12.5 KV | 99 | 131.0303
31 | 59 | SUBS-LO,LEONARD SUB | 12678 12.5 KV | 599 | 126.1736
32 | 11 | SUBS-PC,COCHISE SUB | 25P47 25.0 KV | 20 | 126
33 | 218 | SUBS-WW,WHITEWRIGHT SUB | 12698 12.5 KV | 609 | 121.2233
34 | 68 | SUBS-PC,WORSHAM FIELD SUB | 13P98 12.5 KV | 73 | 116.8082
35 | 112 | SUBS-CL,HANDLEY 22KV SUB | 22825 22.0 KV | 101 | 116.6733
36 | 85 | SUBS-LW,WEST SUB | 1235 12.5 KV | 1228 | 116.0708
37 | 23 | SUBS-LW,SOUTH SUB | 1103 12.5 KV | 1389 | 113.0274
38 | 48 | SUBS-LW,SOUTH SUB | 1102 12.5 KV | 1613 | 112.827
39 | 53 | SUBS-LW,SOUTH SUB | 1104 12.5 KV | 3091 | 106.0162
40 | 49 | SUBS-PI,CLIMAX SUB | 2270 22.0 KV | 334 | 103.9311
41 | 221 | SUBS-GT,CORYELL CO #1 SUB | 22160 22.0 KV | 67 | 103.1343
42 | 194 | SUBS-LO,LEONARD SUB | 12682 12.5 KV | 265 | 103
43 | 7 | SUBS-DC,LEAGUE CITY SUB | 1281 12.5 KV | 798 | 100.1216
44 | 66 | SUBS-FR,PUCKETT SUB | 25F14 25.0 KV | 12 | 100.0833
45 | 75 | SUBS-DC,DICKINSON SUB | 1274 12.5 KV | 1402 | 96.6091
46 | 58 | SUBS-PC,LONE STAR SUB | 25P171 25.0 KV | 47 | 94.7872
47 | 83 | SUBS-FI,FRIENDSWOOD SUB | 1251 12.5 KV | 1568 | 94.1798
48 | 154 | SUBS-WC,SWEENY SUB | 1129 12.5 KV | 651 | 92.9493
49 | 28 | SUBS-LW,WEST SUB | 1234 12.5 KV | 912 | 86.4254
50 | 246 | SUBS-VL,VALLEY MILLS SUB | 22565 22.0 KV | 559 | 86.0805
51 | 208 | SUBS-LW,LAKEPOINTE SUB | 2516 25.0 KV | 745 | 85.8523
52 | 67 | SUBS-TC,NORTHSIDE SUB | 1293 12.5 KV | 631 | 81.9778
53 | 187 | SUBS-TC,FREEWAY PARK SUB | 1101 12.5 KV | 1416 | 81.411
54 | 201 | SUBS-GT,GATESVILLE #2 SUB | 22725 22.0 KV | 853 | 80.8769
55 | 89 | SUBS-TC,TEJAS SUB | 1215 12.5 KV | 1569 | 80.6507
56 | 222 | SUBS-WI,WHITNEY #1 SUB | 22450 22.0 KV | 767 | 79.2934
57 | 119 | SUBS-SR,THURBER 22KV SUB | 1490 22.0 KV | 884 | 78.7624
58 | 210 | SUBS-WC,SWEENY SUB | 1263 12.5 KV | 571 | 77.1138
59 | 117 | SUBS-DC,DICKINSON SUB | 1277 12.5 KV | 1285 | 76.8265
60 | 94 | SUBS-MR,WALNUT SPRINGS 22KV | 2210 22.0 KV | 403 | 75.4491
61 | 36 | SUBS-PC,LONE STAR SUB | 25P174 25.0 KV | 28 | 72.1429
62 | 74 | SUBS-AG,ANGLETON SUB | 1240 12.5 KV | 1341 | 72.0768
63 | 38 | SUBS-PC,REEVES CO. NO.4 SUB | 12P28 12.5 KV | 142 | 71.662
64 | 234 | SUBS-GT,CORYELL #1 SUB | 22155 22.0 KV | 592 | 71.2365
65 | 64 | SUBS-WI,HILL CO SUB | 22125 22.0 KV | 284 | 69.5986
66 | 129 | SUBS-PI,CLIMAX SUB | 22110 22.0 KV | 1400 | 69.16
67 | 123 | SUBS-TC,LAMARQUE SUB | 1202 12.5 KV | 532 | 67.0489
68 | 128 | SUBS-AG,ANGLETON SUB | 1155 12.5 KV | 709 | 65.5402
69 | 206 | SUBS-BR,BRYSONS SUB | 1230 12.5 KV | 538 | 65.3048
70 | 79 | SUBS-HM,HAMILTON COUNTY SUB | 2340 2.4 KV | 132 | 64.4091
71 | 163 | SUBS-PC,STAFFORD SUB | 13P50 12.5 KV | 250 | 63.68
72 | 200 | SUBS-TC,TEJAS SUB | 1217 12.5 KV | 613 | 63.2969
73 | 43 | SUBS-LW,TI SUB | 1012 12.5 KV | 2219 | 62.1113
74 | 132 | SUBS-FI,FRIENDSWOOD SUB | 1252 12.5 KV | 1443 | 61.5856
75 | 29 | SUBS-LW,WEST SUB | 1221 12.5 KV | 702 | 58.1595
76 | 252 | SUBS-LO,FRONTIER SUB | 4236 4.0 KV | 355 | 55.3239
77 | 92 | SUBS-TC,LAMARQUE SUB | 1110 12.5 KV | 313 | 54.7029
78 | 27 | SUBS-FI,ALVIN SUB | 1230 12.5 KV | 1346 | 54.1456
79 | 149 | SUBS-LW,WEST SUB | 1233 12.5 KV | 510 | 54.1275
80 | 141 | SUBS-FR,DOWNTOWN SUB | 12F130 12.5 KV | 700 | 53.4443
81 | 99 | SUBS-GE,GLEN ROSE #3 SUB | 23875 25.0 KV | 906 | 52.8091
82 | 26 | SUBS-TC,LAMARQUE SUB | 1204 12.5 KV | 1367 | 50.4638
83 | 110 | SUBS-TC,NORTHSIDE SUB | 1295 12.5 KV | 1447 | 47.5722
84 | 111 | SUBS-WC,SWEENY SUB | 1128 12.5 KV | 643 | 47.5179
85 | 91 | SUBS-DC,DICKINSON SUB | 1267 12.5 KV | 787 | 47.4257
86 | 20 | SUBS-HC,HICO CITY SUB | 390 4.0 KV | 367 | 46.9455
87 | 19 | SUBS-FR,GOMEZ SUB | 25F05 25.0 KV | 23 | 45.1304
88 | 232 | SUBS-WI,WHITNEY #1 SUB | 22455 22.0 KV | 427 | 44.1171
89 | 133 | SUBS-WC,WEST COLUMBIA SUB | 1235 12.5 KV | 689 | 43.0435
90 | 135 | SUBS-AG,ANGLETON SUB | 1153 12.5 KV | 1370 | 42.9336
91 | 139 | SUBS-TC,NORTHSIDE SUB | 1292 12.5 KV | 1259 | 41.386
92 | 24 | SUBS-WC,BRAZORIA SUB | 1271 12.5 KV | 1652 | 39.1864
93 | 115 | SUBS-DC,DICKINSON SUB | 1272 12.5 KV | 1039 | 37.3879
94 | 71 | SUBS-FI,ALVIN SUB | 1257 12.5 KV | 1685 | 36.9175
95 | 80 | SUBS-EO,LONE OAK SUB | 13384 12.5 KV | 385 | 36.7299
96 | 73 | SUBS-FI,FRIENDSWOOD SUB | 1107 12.5 KV | 1192 | 36.3607
97 | 51 | SUBS-WC,BRAZORIA SUB | 1291 12.5 KV | 464 | 35.1487
98 | 160 | SUBS-AG,ANGLETON SUB | 1241 12.5 KV | 1414 | 35.1068
99 | 152 | SUBS-TC,FREEWAY PARK SUB | 1102 12.5 KV | 208 | 34.5769
100 | 16 | SUBS-TC,HEIGHTS SUB | 1132 12.5 KV | 937 | 33.413
101 | 124 | SUBS-DC,LEAGUE CITY SUB | 1285 12.5 KV | 1732 | 33.1039
102 | 177 | SUBS-WI,HILL CO SUB | 23340 22.0 KV | 850 | 32.5047
103 | 12 | SUBS-WC,BRAZORIA SUB | 1270 12.5 KV | 1430 | 32.3587
104 | 95 | SUBS-TC,NORTHSIDE SUB | 1228 12.5 KV | 1431 | 32.3585
105 | 179 | SUBS-TC,FREEWAY PARK SUB | 1103 12.5 KV | 1313 | 32.3153
106 | 164 | SUBS-NC,SAINT JO SUB | 408 4.0 KV | 205 | 31.7317
107 | 121 | SUBS-NC,NOCONA SUB | 12490 12.5 KV | 402 | 31.3955
108 | 45 | SUBS-BR,BRYSONS SUB | 1233 12.5 KV | 127 | 31.2362
109 | 166 | SUBS-FI,ALVIN SUB | 1259 12.5 KV | 723 | 29.8465
110 | 86 | SUBS-MR,MERIDIAN 22KV SUB | 23210 22.0 KV | 699 | 28.6423
111 | 54 | SUBS-GT,CORYELL CO #2 SUB | 22365 22.0 KV | 561 | 28.0945
112 | 113 | SUBS-WC,SWEENY SUB | 1264 12.5 KV | 1130 | 27.9779
113 | 103 | SUBS-PI,CLIMAX SUB | 2267 22.0 KV | 469 | 27.4755
114 | 215 | SUBS-ON,OLNEY SWCH STA | 1431 12.5 KV | 784 | 26.5599
115 | 175 | SUBS-WW,BLUE RIDGE SUB | 22700 22.0 KV | 334 | 25.3563
116 | 127 | SUBS-FI,ALVIN SUB | 1117 12.5 KV | 1414 | 25.1874
117 | 254 | SUBS-WW,WHITEWRIGHT SUB | 12753 12.5 KV | 122 | 25
118 | 143 | SUBS-WC,WEST COLUMBIA SUB | 1237 12.5 KV | 1065 | 24.8732
119 | 37 | SUBS-HC,HICO CITY SUB | 395 4.0 KV | 619 | 23.6866
120 | 233 | SUBS-WW,WHITEWRIGHT SUB | 12575 12.5 KV | 622 | 23.5209
121 | 62 | SUBS-PC,PECOS MAIN SUB | 12P02 12.5 KV | 1011 | 22.9832
122 | 3 | SUBS-SN,SANDERSON SUB | 4S27 4.0 KV | 105 | 22.6286
123 | 217 | SUBS-BG,RED RIVER SUB | 2229 22.0 KV | 451 | 22.2639
124 | 116 | SUBS-AG,ANGLETON SUB | 1244 12.5 KV | 1021 | 21.8237
125 | 114 | SUBS-DC,DICKINSON SUB | 1279 12.5 KV | 1271 | 21.8214
126 | 198 | SUBS-FR,AIRPORT SUB | 12F271 12.5 KV | 340 | 21.8206
127 | 183 | SUBS-PC,COCHISE SUB | 25P48 25.0 KV | 258 | 21.686
128 | 96 | SUBS-FI,ALVIN SUB | 1115 12.5 KV | 1225 | 21.4351
129 | 241 | SUBS-CL,HANDLEY 22KV SUB | 22820 22.0 KV | 29 | 21.3793
130 | 84 | SUBS-FR,DOWNTOWN SUB | 12F114 12.5 KV | 800 | 20.6988
131 | 130 | SUBS-FI,ALVIN SUB | 1116 12.5 KV | 2069 | 20.695
132 | 63 | SUBS-GE,GLEN ROSE #1 SUB | 22295 22.0 KV | 661 | 20.5991
133 | 120 | SUBS-TC,FREEWAY PARK SUB | 1299 12.5 KV | 686 | 20.4344
134 | 199 | SUBS-KR,KERMIT NO. 2 SUB | 12K48 12.5 KV | 487 | 20.1848
135 | 17 | SUBS-PC,PECOS MAIN SUB | 12P01 12.5 KV | 107 | 20.028
136 | 34 | SUBS-PC,WORSHAM FIELD SUB | 13P97 12.5 KV | 64 | 19.8438
137 | 148 | SUBS-AG,ANGLETON SUB | 1154 12.5 KV | 2031 | 19.8277
138 | 158 | SUBS-WC,OLD OCEAN SUB | 1261 12.5 KV | 165 | 19.7455
139 | 151 | SUBS-FI,MAGNOLIA SUB | 1144 12.5 KV | 1101 | 18.4896
140 | 193 | SUBS-TC,HEIGHTS SUB | 1134 12.5 KV | 884 | 18.4559
141 | 72 | SUBS-TC,FREEWAY PARK SUB | 1298 12.5 KV | 1108 | 17.8637
142 | 186 | SUBS-HM,HAMILTON COUNTY SUB | 24015 25.0 KV | 260 | 17.7885
143 | 21 | SUBS-TC,FREEWAY PARK SUB | 1297 12.5 KV | 366 | 17.2459
144 | 181 | ELIASVILLE POD | 1300 12.5 KV | 163 | 16.4785
145 | 182 | SUBS-HM,HAMILTON COUNTY SUB | 2345 2.4 KV | 116 | 15.4052
146 | 136 | SUBS-TC,LAMARQUE SUB | 1201 12.5 KV | 878 | 15.361
147 | 155 | SUBS-FI,FRIENDSWOOD SUB | 1108 12.5 KV | 1695 | 15.1487
148 | 140 | SUBS-FR,16TH STREET SUB | 13F14 12.5 KV | 920 | 15.0859
149 | 55 | SUBS-KR,WICKETT SUB | 12K446 12.5 KV | 20 | 14.75
150 | 168 | SUBS-NC,NOCONA SUB | 13370 12.5 KV | 671 | 14.7273
151 | 173 | SUBS-MR,WALNUT SPRINGS 12.5 | 1270 12.5 KV | 33 | 14.5455
152 | 101 | SUBS-FI,MAGNOLIA SUB | 1145 12.5 KV | 1774 | 14.1116
153 | 90 | SUBS-AG,ANGLETON SUB | 1242 12.5 KV | 1389 | 13.4118
154 | 153 | SUBS-WC,WEST COLUMBIA SUB | 1233 12.5 KV | 700 | 13.3571
155 |  | SUBS-FI,FRIENDSWOOD SUB | 1109 12.5 | 1267 | 12.4009
156 | 41 | SUBS-NC,PETROLIA SUB | 12260 12.5 KV | 751 | 12.2357
157 | 104 | SUBS-NC,NOCONA SUB | 13374 12.5 KV | 704 | 12.1449
158 | 118 | SUBS-SR,THURBER 12.5KV SUB | 1447 12.5 KV | 611 | 11.4435
159 | 207 | SUBS-LW,JONES STREET SUB | 1413 12.5 KV | 944 | 11.0339
160 | 107 | SUBS-DC,LEAGUE CITY SUB | 1282 12.5 KV | 1827 | 10.7811
161 | 220 | SUBS-PC,STAFFORD SUB | 12P82 12.5 KV | 258 | 10.1434
162 | 219 | SUBS-LW,SOUTH SUB | 1108 12.5 KV | 2367 | 10.1381
163 | 98 | SUBS-TC,NORTHSIDE SUB | 1294 12.5 KV | 1006 | 10.1193
164 | 25 | SUBS-PL,KRUGERVILLE SUB | 2604 22.0 KV | 1307 | 10.1079
165 | 106 | SUBS-DC,DICKINSON SUB | 1266 12.5 KV | 489 | 9.728
166 | 176 | SUBS-FI,ALVIN SUB | 1232 12.5 KV | 1120 | 9.6027
167 | 159 | SUBS-DC,SOUTH SHORE SUB | 1190 12.5 KV | 2510 | 8.9984
168 | 109 | SUBS-DC,LEAGUE CITY SUB | 1280 12.5 KV | 804 | 8.6381
169 | 9 | SUBS-FR,PUCKETT SUB | 25F18 25.0 KV | 36 | 8.5833
170 | 134 | SUBS-NC,NOCONA SUB | 13610 12.5 KV | 693 | 8.5483
171 | 230 | SUBS-KR,KERMIT NO. 2 SUB | 12K98 12.5 KV | 396 | 8.5354
172 | 174 | SUBS-FR,16TH STREET SUB | 12F72 12.5 KV | 220 | 8.5273
173 | 125 | SUBS-LW,JONES STREET SUB | 1411 12.5 KV | 1466 | 8.4488
174 | 161 | SUBS-DC,LEAGUE CITY SUB | 1283 12.5 KV | 1718 | 8.2678
175 | 144 | SUBS-FI,ALVIN SUB | 1254 12.5 KV | 1360 | 8.0985
176 | 205 | SUBS-LW,SOUTH SUB | 1107 12.5 KV | 1899 | 8.0911
177 | 209 | SUBS-PC,PECOS MAIN SUB | 2P03 2.4 KV | 350 | 7.7714
178 | 35 | SUBS-KR,CALIFORNIA SUB | 12K87 12.5 KV | 52 | 7.6923
179 | 138 | SUBS-FI,ALVIN SUB | 1231 12.5 KV | 1781 | 7.6873
180 | 145 | SUBS-SR,THURBER 22KV SUB | 22890 22.0 KV | 199 | 7.3065
181 | 202 | SUBS-LW,WEST SUB | 1203 12.5 KV | 775 | 7.3032
182 | 105 | SUBS-ON,GRAHAM SUB | 1245 12.5 KV | 206 | 6.9854
183 | 93 | SUBS-AG,ANGLETON SUB | 1243 12.5 KV | 1327 | 6.9736
184 | 122 | SUBS-FR,16TH STREET SUB | 12F71 12.5 KV | 1050 | 6.5924
185 | 102 | SUBS-DC,LEAGUE CITY SUB | 1284 12.5 KV | 645 | 6.4682
186 | 156 | SUBS-TC,TEJAS SUB | 1214 12.5 KV | 447 | 6.4049
187 | 146 | SUBS-PL,KRUGERVILLE SUB | 2608 25.0 KV | 1850 | 6.3503
188 | 172 | SUBS-ON,GRAHAM SUB | 12605 12.5 KV | 134 | 6.0821
189 | 100 | SUBS-WC,BRAZORIA SUB | 1290 12.5 KV | 907 | 5.8324
190 | 226 | SUBS-ON,OLNEY SWCH STA | 1690 12.5 KV | 543 | 5.488
191 | 262 | SUBS-PC,STAFFORD SUB | 12P99 12.5 KV | 229 | 4.8646
192 | 184 | SUBS-TC,HEIGHTS SUB | 1222 12.5 KV | 589 | 4.8438
193 | 31 | SUBS-KR,KERMIT NO.1 SUB | 4K04 4.0 KV | 425 | 4.7059
194 | 192 | SUBS-LW,TI SUB | 1032 12.5 KV | 2662 | 4.704
195 | 2 | SUBS-SN,SANDERSON SUB | 4S26 4.0 KV | 235 | 4.6468
196 | 157 | SUBS-DC,SOUTH SHORE SUB | 1192 12.5 KV | 1344 | 4.4784
197 | 22 | SUBS-LW,WEST SUB | 1223 12.5 KV | 1418 | 4.4549
198 | 165 | SUBS-FI,MAGNOLIA SUB | 1149 12.5 KV | 1942 | 4.3239
199 | 190 | SUBS-TC,HEIGHTS SUB | 1224 12.5 KV | 1198 | 4.2771
200 | 255 | SUBS-WW,WHITEWRIGHT SUB | 13563 12.5 KV | 433 | 3.9931
201 | 212 | SUBS-LW,TI SUB | 1033 12.5 | 1831 | 3.9268
202 | 167 | SUBS-TC,LAMARQUE SUB | 1203 12.5 KV | 336 | 3.5387
203 | 228 | SUBS-LO,LEONARD SUB | 14635 12.5 KV | 558 | 3.4946
204 | 169 | SUBS-VL,VALLEY MILLS SUB | 22575 22.0 KV | 466 | 3.2725
205 | 180 | SUBS-LW,WEST SUB | 1201 12.5 KV | 1101 | 3.0845
206 | 253 | SUBS-LO,TRENTON SUB | 4120 4.0 KV | 209 | 2.5837
207 | 203 | SUBS-WI,WHITNEY #2 SUB | 22460 22.0 KV | 311 | 2.5691
208 | 242 | SUBS-GT,GATESVILLE #1 4KV | 413 4.0 KV | 167 | 2.4551
209 | 142 | SUBS-FI,MAGNOLIA SUB | 1150 12.5 KV | 116 | 2.4138
210 | 238 | SUBS-CL,CLIFTON #1 22 KV | 22495 22.0 KV | 275 | 2.4
211 | 188 | SUBS-GT,GATESVILLE #1 4KV | 422 4.0 KV | 191 | 2.356
212 | 56 | SUBS-HM,HAMILTON CITY #2 22 | 23820 25.0 KV | 364 | 2.294
213 | 231 | SUBS-KR,KERMIT NO. 2 SUB | 4K06 4.0 KV | 160 | 2.25
214 | 196 | SUBS-CL,LAKE WHITNEY SUB | 12355 12.5 KV | 890 | 2.1955
215 | 250 | SUBS-LW,WEST SUB | 1202 12.5 KV | 1049 | 2.1859
216 | 204 | SUBS-FR,AIRPORT SUB | 12F44 12.5 KV | 915 | 2.176
217 | 227 | SUBS-CL,LAKE WHITNEY SUB | 1230 12.5 KV | 537 | 2.0708
218 | 8 | SUBS-KR,KERMIT NO.1 SUB | 4K03 4.0 KV | 200 | 1.8
219 | 244 | SUBS-GT,GATESVILLE #2 4KV | 429 4.0 KV | 317 | 1.6404
220 | 178 | SUBS-LW,SOUTH SUB | 1109 12.5 KV | 707 | 1.5743
221 | 229 | SUBS-MR,WALNUT SPRINGS 22KV | 2215 22.0 KV | 227 | 1.5419
222 | 137 | SUBS-DC,SOUTH SHORE SUB | 1195 12.5 KV | 1135 | 1.5145
223 | 195 | SUBS-NC,SAINT JO SUB | 401 4.0 KV | 461 | 1.3796
224 | 147 | SUBS-AG,ANGLETON SUB | 1245 12.5 KV | 598 | 1.2993
225 | 260 | SUBS-PC,PECOS MAIN SUB | 2P06 2.4 KV | 220 | 1.1591
226 | 197 | SUBS-PC,PECOS MAIN SUB | 12P03 12.5 KV | 320 | 1
227 | 214 | SUBS-MR,WALNUT SPRINGS 22KV | 2200 22.0 KV | 407 | 0.5897
228 | 162 | SUBS-NC,NOCONA SUB | 12486 12.5 KV | 234 | 0.5
229 | 249 | SUBS-LW,LAKEPOINTE SUB | 2532 25.0 KV | 594 | 0.4663
230 | 185 | SUBS-PC,PECOS MAIN SUB | 12P362 12.5 KV | 1040 | 0.4596
231 | 189 | SUBS-HM,HAMILTON CITY #1 22 | 22780 22.0 KV | 784 | 0.4082
232 | 224 | SUBS-GT,GATESVILLE #1 4KV | 419 4.0 KV | 247 | 0.3036
233 | 223 | SUBS-LO,LEONARD SUB | 14631 12.5 KV | 273 | 0.2198
234 | 237 | SUBS-CL,CLIFTON #1 22 KV | 22485 22.0 KV | 179 | 0.2067
235 | 88 | SUBS-MR,MERIDIAN 4KV SUB | 680 4.0 KV | 387 | 0.155
236 | 65 | SUBS-KR,KEYSTONE SUB | 12K437 12.5 KV | 575 | 0.0696
237 | 44 | SUBS-HM,HAMILTON CITY #1 22 | 22785 22.0 KV | 251 | 0.0558
238 | 131 | SUBS-CL,CLIFTON #2 22KV | 23165 22.0 KV | 30 | 0
239 | 235 | SUBS-CL,CLIFTON #2 4KV | 4160 4.0 KV | 439 | 0
240 | 236 | SUBS-CL,CLIFTON #2 4KV | 4165 4.0 KV | 482 | 0
241 | 13 | SUBS-CL,CLIFTON #1 22 KV | 22480 22.0 KV | 86 | 0
242 | 239 | SUBS-CL,CLIFTON #1 4KV SUB | 405 4.0 KV | 100 | 0
243 | 225 | SUBS-CL,CLIFTON #1 4KV SUB | 407 4.0 KV | 482 | 0
244 | 240 | SUBS-CL,CLIFTON #1 4KV SUB | 490 4.0 KV | 27 | 0
245 | 211 | SUBS-GT,GATESVILLE #2 SUB | 23065 22.0 KV | 88 | 0
246 | 243 | SUBS-GT,GATESVILLE #2 4KV | 426 4.0 KV | 296 | 0
247 | 245 | SUBS-GT,SYCAMORE SUB | 24100 25.0 KV | 42 | 0
248 | 216 | SUBS-HM,HAMILTON CITY #2 22 | 23825 25.0 KV | 125 | 0
249 | 82 | SUBS-MR,MERIDIAN 22KV SUB | 23205 22.0 KV | 131 | 0
250 | 87 | SUBS-MR,MERIDIAN 4KV SUB | 690 4.0 KV | 287 | 0
251 | 70 | SUBS-VL,VALLEY MILLS SUB | 22570 22.0 KV | 414 | 0
252 | 247 | SUBS-WI,WHITNEY #2 SUB | 22469 22.0 KV | 123 | 0
253 | 251 | SUBS-EO,LONE OAK SUB | 13388 12.5 KV | 43 | 0
254 |  | SUBS-WC,CLEMONS DOME SUB | 1175 12.5 KV | 12 | 0
255 | 78 | SUBS-KR,CALIFORNIA SUB | 12K86 12.5 KV | 47 | 0
256 | 256 | SUBS-KR,KERMIT NO. 2 SUB | 4K07 4.0 KV | 385 | 0
257 | 30 | SUBS-KR,KERMIT NO.1 SUB | 4K02 4.0 KV | 180 | 0
258 | 32 | SUBS-KR,KERMIT NO.1 SUB | 4K05 4.0 KV | 375 | 0
259 | 258 | SUBS-PC,PECOS MAIN SUB | 2P04 2.4 KV | 111 | 0
260 | 259 | SUBS-PC,PECOS MAIN SUB | 2P05 2.5 KV | 44 | 0
261 | 261 | SUBS-PC,STAFFORD SUB | 12P50 12.5 KV | 250 | 0
262 | 213 | SUBS-FR,DOWNTOWN SUB | 4F52 4.0 KV | 175 | 0
263 | 263 | SUBS-FR,GOMEZ SUB | 25F61 25.0 KV | 13 | 0
264 | 1 | SUBS-SN,SANDERSON SUB | 4S28 4.0 KV | 310 | 0
265 | 264 | SUBS-CL,CLIFTON#2 22KV | 24370 22.0 | 176 | 0

## Causes
TEXAS-NEW MEXICO POWER COMPANY
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
2000 Reporting Year
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 29.02%
|  | Vegetation | 13.2%
|  | Animals and Birds | 17.77%
|  | People (Including cars and farm equip) | 5.89%
|  | Utility-owned Equipment | 26.02%
|  | Other | 8.1%
Unknown