## Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | Austin Energy
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 238
Due: |  | February 14, 2001
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 23436
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Mel Eckhoff, Engineering Specialist
Electric Division
Commission Staff
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mailto:mel.eckhoff@puc.state.tx.us

## Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
2000 Reporting Year
Austin Energy
Project 23436

## System-SAIFI
Austin Energy
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2000 | 0.90248 | 0.036026 | 0.038876 | 0.070679 | 0.064266 | 0.092438 | 0.076112 | 0.080147 | 0.10814 | 0.13001 | 0.076006 | 0.078193 | 0.051586
Scheduled
2000 | 0.017154 | 0.00095471 | 0.00087111 | 0.0005606 | 0.0010751 | 0.0010647 | 0.0013401 | 0.00063403 | 0.0012648 | 0.0017772 | 0.0045537 | 0.0019622 | 0.0010956
Outside Causes
2000 | 0.11379 | 0.01942 |  |  |  |  | 0.009762 |  | 0.011311 | 0.0098865 | 0.010677 | 0.012469 | 0.040263
Major Events
2000 | [12 empty] | *
* Austin Energy was unable to calculate SAIDI and SAIFI for the ice storm of December 13, 2000.

## System-SAIDI
Austin Energy
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2000 | 87.2871 | 2.1871 | 3.4293 | 3.456 | 7.3534 | 24.1699 | 4.1476 | 11.0532 | 6.971 | 8.6003 | 6.2346 | 5.9373 | 3.7475
Scheduled
2000 | 2.0838 | 0.097612 | 0.13731 | 0.057531 | 0.15891 | 0.14291 | 0.10933 | 0.061446 | 0.16872 | 0.1325 | 0.80974 | 0.15609 | 0.051751
Outside Causes
2000 | 5.1896 | 0.17478 |  |  |  |  | 0.78545 |  | 1.5305 | 0.066101 | 0.50059 | 0.19951 | 1.9326
Major Events
2000 | [12 empty] | *
* Austin Energy was unable to calculate SAIDI and SAIFI for the ice storm of December 13, 2000.

## Feeder-SAIFI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System | [5 empty] | Total Number of Feeders
With More Than 10 Customers | [5 empty] | 238
Add or Delete Rows as Necessary
Austin Energy
2000 SAIFI Ranking | 1999 SAIFI Ranking | 1999 Number of Customers | Substation Identification | Feeder Identification | 2000 Number of Customers | 2000 SAIFI Value
1 | 4 | 1652 | Northland | NL14 | 737 | 5.2822
2 | 125 | 2039 | Lakeway | LW02 | 2494 | 4.3184
3 | 140 | 3366 | Daffin Gin | DG01 | 3963 | 4.1554
4 | 97 | 2295 | Fiskville | FV05 | 3288 | 3.6901
5 | 84 | 792 | Northland | NL02 | 618 | 3.6553
6 | 52 | 2287 | Northland | NL08 | 2439 | 3.6335
7 | not in service |  | Wheless Lane | WL07 | 2403 | 3.3962
8 | 114 | 949 | Seaholm Plant | SP07 | 946 | 3.3235
9 | 83 | 1918 | Summit | SU02 | 2284 | 3.2128
10 | 76 | 471 | Walnut Creek | WC07 | 323 | 3.0495
11 | 91 | 439 | Warren | WA02 | 464 | 2.8254
12 | 82 | 1117 | Bergstrom | BE06 | 1486 | 2.6931
13 | 31 | 1783 | Patton Lane | PL02 | 1062 | 2.5678
14 | 117 | 2050 | Warren | WA06 | 1996 | 2.5276
15 | 44 | 2428 | Brodie Lane | BL01 | 2415 | 2.4261
16 | 60 | 1578 | Jollyville | JV03 | 1766 | 2.3941
17 | not in service |  | Techridge | TR02 | 1607 | 2.3877
18 | 58 | 2524 | Magnesium Plant | MP03 | 1224 | 2.2851
19 | 173 | 2282 | Kingsbery | KB06 | 2822 | 2.2679
20 | 8 | 1149 | Riverplace | RP05 | 1708 | 2.2541
21 | 127 | 1527 | Bergstrom | BE05 | 1611 | 2.2353
22 | 77 | 1101 | Steck | ST05 | 1086 | 2.221
23 | 80 | 1212 | Seaholm Plant | SP09 | 1269 | 2.1812
24 | 120 | 1509 | Jollyville | JV05 | 1693 | 2.1748
25 | 12 | 1262 | Lakeway | LW04 | 1013 | 2.155
26 | 49 | 467 | Brodie Lane | BL05 | 1817 | 2.1348
27 | 222 | 1532 | Summit | SU04 | 1487 | 2.1338
28 | 21 | 2178 | Pedernales | PE04 | 1949 | 2.0236
29 | 74 | 619 | Brodie Lane | BL03 | 1483 | 2.0074
30 | 36 | 2413 | Slaughter Lane | SL05 | 2644 | 2.0034
31 | 202 | 1192 | Hamilton | HM09 | 840 | 1.925
32 | 46 | 2214 | North | NO02 | 2844 | 1.9142
33 | 87 | 484 | Walnut Creek | WC08 | 582 | 1.8849
34 | 59 | 688 | Warren | WA05 | 660 | 1.7848
35 | 102 | 985 | Steck | ST06 | 948 | 1.7658
36 | 95 | 1188 | Wheless Lane | WL04 | 1648 | 1.713
37 | 180 | 893 | Sprinkle | SK01 | 384 | 1.7057
38 | 14 | 725 | Koenig Lane | KL01 | 838 | 1.6981
39 | 109 | 386 | Carson Creek | CC05 | 451 | 1.6186
40 | 78 | 180 | Warren | WA04 | 178 | 1.6011
41 | not in service |  | Kingsbery | KB02 | 82 | 1.5244
42 | 158 | 1433 | Seaholm Plant | SP01 | 1671 | 1.5177
43 | 40 | 1797 | Warren | WA01 | 1997 | 1.4842
44 | 15 | 2159 | North | NO01 | 2037 | 1.4585
45 | 99 | 1792 | Cardinal Lane | CL01 | 1828 | 1.4584
46 | 30 | 2293 | Wheless Lane | WL01 | 2272 | 1.4243
47 | 90 | 2519 | Koenig Lane | KL06 | 2582 | 1.3939
48 | 123 | 1093 | Lakeway | LW03 | 1287 | 1.3932
49 | 93 | 1724 | Hi-Cross | HC01 | 2113 | 1.3687
50 | 17 | 864 | Bee Creek | BC06 | 952 | 1.3613
51 | 28 | 1442 | Northland | NL01 | 541 | 1.342
52 | 198 | 768 | Wheless Lane | WL05 | 777 | 1.3346
53 | 164 | 2662 | North | NO07 | 2751 | 1.3315
54 | 219 | 673 | Hamilton | HM04 | 674 | 1.3249
55 | 88 | 1229 | Burleson | BU07 | 1251 | 1.3229
56 | 126 | 1165 | Sprinkle | SK03 | 828 | 1.308
57 | 150 | 595 | Barton | BA01 | 516 | 1.3043
58 | 221 | 574 | North | NO09 | 591 | 1.3012
59 | 10 | 2707 | Salem Walk | SW02 | 2617 | 1.2973
60 | 133 | 881 | Warren | WA03 | 881 | 1.294
61 | 2 | 376 | Cameron | CM01 | 320 | 1.2781
62 | 122 | 1878 | Salem Walk | SW01 | 2110 | 1.2758
63 | 119 | 1098 | Dessau | DE01 | 1622 | 1.2756
64 | 134 | 1214 | Seaholm Plant | SP02 | 1240 | 1.2742
65 | 64 | 2474 | Cardinal Lane | CL03 | 1854 | 1.2697
66 | 115 | 2109 | Zilker | ZL03 | 2031 | 1.2413
67 | 22 | 1283 | Commons Ford | CF02 | 1402 | 1.2361
68 | 161 | 1789 | Pedernales | PE07 | 1674 | 1.2234
69 | 154 | 897 | Cardinal Lane | CL04 | 882 | 1.2234
70 | 148 | 1899 | Walnut Creek | WC10 | 2497 | 1.2227
71 | 89 | 1024 | Howard Lane | HL01 | 957 | 1.2153
72 | 132 | 1224 | Burleson | BU01 | 1192 | 1.2013
73 | 199 | 140 | Commons Ford | CF03 | 347 | 1.196
74 | 200 | 1510 | Barton | BA09 | 1752 | 1.1906
75 | 147 | 1036 | Cameron | CM04 | 1515 | 1.1822
76 | 204 | 1655 | Brodie Lane | BL02 | 660 | 1.1818
77 | 57 | 1780 | Zilker | ZL02 | 1730 | 1.1803
78 | 178 | 710 | Burleson | BU06 | 697 | 1.1564
79 | 16 | 3357 | Kingsbery | KB03 | 2618 | 1.1211
80 | 61 | 2281 | Magnesium Plant | MP02 | 2980 | 1.1185
81 | 135 | 943 | Onion Creek | OC04 | 1268 | 1.1167
82 | 73 | 2025 | Oak Hill | OH05 | 2221 | 1.1081
83 | 218 | 448 | Summit | SU01 | 151 | 1.0861
84 | 32 | 221 | Bergstrom | BE02 | 260 | 1.0846
85 | not in service |  | Trading Post | TP01 | 972 | 1.073
86 | 159 | 1420 | Cardinal Lane | CL06 | 1889 | 1.0704
87 | 192 | 568 | Howard Lane | HL05 | 750 | 1.0573
88 | 205 | 768 | Jett | JE02 | 1401 | 1.055
89 | 68 | 601 | Koenig Lane | KL08 | 587 | 1.0375
90 | 35 | 872 | Hi-Cross | HC06 | 1037 | 1.0328
91 | not in service |  | Patton Lane | PL03 | 2030 | 1.0305
92 | 72 | 283 | Williamson | WI05 | 106 | 1.0283
93 | not in service |  | Hamilton | HM06 | 330 | 1.0061
94 | 207 | 980 | Oak Hill | OH06 | 940 | 1.0053
95 | 67 | 3166 | Howard Lane | HL04 | 3144 | 1.0025
96 | 187 | 957 | Summit | SU03 | 927 | 1.0011
97 | 165 | 60 | Burleson | BU04 | 79 | 0.94937
98 | 190 | 820 | Kingsbery | KB01 | 874 | 0.93707
99 | 38 | 1757 | Cardinal Lane | CL11 | 2168 | 0.91421
100 | 66 | 441 | Koenig Lane | KL12 | 441 | 0.90249
101 | 112 | 2265 | Cardinal Lane | CL12 | 2364 | 0.8769
102 | 106 | 96 | Sprinkle | SK02 | 113 | 0.87611
103 | 7 | 1077 | Cardinal Lane | CL08 | 1174 | 0.86201
104 | 108 | 2320 | Fiskville | FV06 | 2602 | 0.80746
105 | 29 | 1455 | Commons Ford | CF04 | 1461 | 0.80424
106 | not in service |  | Steck | ST07 | 729 | 0.79835
107 | 43 | 1704 | Austin Dam | AD02 | 896 | 0.79688
108 | 11 | 2123 | Northland | NL11 | 2146 | 0.79404
109 | 193 | 34 | Daffin Gin | DG02 | 131 | 0.77863
110 | 206 | 1366 | Hamilton | HM01 | 1501 | 0.77615
111 | 130 | 1318 | Bee Creek | BC03 | 1324 | 0.72885
112 | 85 | 506 | Northland | NL15 | 1553 | 0.64327
113 | not in service |  | Seaholm Plant | SP12 | 2272 | 0.636
114 | 81 | 582 | Bee Creek | BC02 | 612 | 0.61438
115 | 186 | 2162 | Williamson | WI02 | 846 | 0.5922
116 | 139 | 2230 | Austin Dam | AD05 | 2292 | 0.58857
117 | 92 | 3649 | Hi-Cross | HC09 | 1495 | 0.58127
118 | 177 | 61 | Lakeshore | LS04 | 70 | 0.55714
119 | 45 | 1168 | Austin Dam | AD01 | 1198 | 0.55092
120 | 113 | 997 | Lakeshore | LS01 | 1239 | 0.55044
121 | 71 | 1273 | Magnesium Plant | MP05 | 1852 | 0.53348
122 | 39 | 1873 | Williamson | WI09 | 1877 | 0.52264
123 | 167 | 1709 | Koenig Lane | KL07 | 1687 | 0.51986
124 | 101 | 1744 | Wheless Lane | WL02 | 791 | 0.51075
125 | 105 | 2129 | Salem Walk | SW06 | 1415 | 0.50954
126 | 94 | 3097 | Salem Walk | SW08 | 1873 | 0.5024
127 | 96 | 2660 | Koenig Lane | KL14 | 2735 | 0.49726
128 | 191 | 2086 | McNeil | MC01 | 260 | 0.49615
129 | 86 | 1078 | Patton Lane | PL01 | 1266 | 0.49605
130 | 3 | 2018 | Koenig Lane | KL03 | 1354 | 0.4904
131 | 146 | 1602 | Howard Lane | HL02 | 1795 | 0.47799
132 | 37 | 1793 | Brodie Lane | BL04 | 2263 | 0.45471
133 | 79 | 837 | Pedernales | PE09 | 752 | 0.45346
134 | 100 | 2226 | Koenig Lane | KL10 | 2256 | 0.4375
135 | 56 | 372 | Commons Ford | CF01 | 533 | 0.42026
136 | 137 | 1017 | North | NO08 | 1069 | 0.4116
137 | 189 | 3235 | Williamson | WI01 | 1680 | 0.41012
138 | 201 | 889 | Cameron | CM03 | 248 | 0.39113
139 | 124 | 2036 | Steck | ST01 | 2012 | 0.39016
140 | 116 | 2314 | Salem Walk | SW04 | 2207 | 0.38514
141 | 98 | 1285 | North | NO04 | 1325 | 0.35925
142 | 118 | 613 | Jollyville | JV02 | 14 | 0.35714
143 | 153 | 1888 | McNeil | MC08 | 1837 | 0.35493
144 | 107 | 963 | Magnesium Plant | MP09 | 1020 | 0.34608
145 | 25 | 1139 | Commons Ford | CF05 | 1233 | 0.34388
146 | 110 | 1884 | Magnesium Plant | MP07 | 1964 | 0.33248
147 | 55 | 2408 | Fiskville | FV03 | 2651 | 0.3312
148 | 170 | 3043 | McNeil | MC06 | 2828 | 0.3285
149 | 34 | 1399 | Bee Creek | BC05 | 1980 | 0.31869
150 | 111 | 2119 | Salem Walk | SW05 | 2168 | 0.31227
151 | 54 | 2938 | Magnesium Plant | MP06 | 3164 | 0.31195
152 | not in service |  | Williamson | WI03 | 10 | 0.3
153 | 211 | 157 | Jollyville | JV08 | 781 | 0.29962
154 | 121 | 412 | Kingsbery | KB05 | 403 | 0.28288
155 | 5 | 3146 | Pedernales | PE02 | 3020 | 0.25629
156 | 48 | 4172 | Slaughter Lane | SL01 | 3298 | 0.24955
157 | not in service |  | Seaholm Plant | SP11 | 369 | 0.24932
158 | 174 | 287 | Lakeshore | LS06 | 348 | 0.24425
159 | 18 | 2253 | Burleson | BU09 | 3785 | 0.24359
160 | 20 | 1144 | Jollyville | JV04 | 1712 | 0.24182
161 | not in service |  | Wheless Lane | WL08 | 1947 | 0.23575
162 | 210 | 2790 | Northland | NL13 | 1589 | 0.2297
163 | 149 | 600 | Kingsbery | KB04 | 619 | 0.22456
164 | 151 | 1458 | Hamilton | HM11 | 2204 | 0.2196
165 | not in service |  | Dessau | DE02 | 1343 | 0.21147
166 | 47 | 1281 | Slaughter Lane | SL04 | 889 | 0.20697
167 | 26 | 3165 | Williamson | WI11 | 3063 | 0.20209
168 | 70 | 1733 | Jett | JE03 | 1782 | 0.20202
169 | 129 | 2262 | Fiskville | FV01 | 2518 | 0.20016
170 | not in service |  | Steck | ST08 | 145 | 0.2
171 | 184 | 1505 | Cameron | CM02 | 1490 | 0.1953
172 | not in service |  | Fiskville | FV04 | 31 | 0.19355
173 | 181 | 3416 | Hi-Cross | HC08 | 3673 | 0.1933
174 | 19 | 2409 | Pedernales | PE01 | 1181 | 0.18459
175 | not in service |  | Oak Hill | OH01 | 941 | 0.18278
176 | 209 | 2702 | Hamilton | HM05 | 2600 | 0.18231
177 | 175 | 920 | Barton | BA05 | 896 | 0.1808
178 | 65 | 3015 | Slaughter Lane | SL02 | 2601 | 0.1807
179 | 131 | 677 | Bergstrom | BE03 | 725 | 0.17931
180 | 42 | 1966 | Salem Walk | SW07 | 1906 | 0.17209
181 | 194 | 2053 | Wheless Lane | WL03 | 1906 | 0.17156
182 | 104 | 1300 | Steck | ST02 | 1292 | 0.17105
183 | 168 | 967 | North | NO06 | 950 | 0.16842
184 | 50 | 198 | Jett | JE06 | 204 | 0.16667
185 | 53 | 1696 | Oak Hill | OH02 | 2007 | 0.15944
186 | 33 | 756 | Cameron | CM05 | 504 | 0.15476
187 | 24 | 550 | Summit | SU05 | 164 | 0.15244
188 | 195 | 960 | Hi-Cross | HC05 | 2489 | 0.15026
189 | 183 | 208 | Hamilton | HM10 | 240 | 0.14583
190 | 212 | 3380 | Williamson | WI06 | 2939 | 0.14495
191 | 156 | 2048 | Hi-Cross | HC03 | 1487 | 0.14324
192 | 172 | 2975 | Angus Valley | AG03 | 2936 | 0.14237
193 | 128 | 2175 | Northland | NL12 | 2489 | 0.12294
194 | 13 | 2729 | Oak Hill | OH03 | 2453 | 0.11781
195 | 51 | 1499 | Cardinal Lane | CL09 | 618 | 0.1165
196 | 41 | 1609 | Pedernales | PE05 | 1438 | 0.11613
197 | not in service |  | Austin Dam | AD06 | 923 | 0.11376
198 | 166 | 3040 | Wheless Lane | WL06 | 1416 | 0.10664
199 | not in service |  | Hi-Cross | HC07 | 1458 | 0.10288
200 | 188 | 709 | Steck | ST03 | 729 | 0.10014
201 | 144 | 787 | Barton | BA03 | 1997 | 0.098648
202 | 163 | 736 | Barton | BA04 | 727 | 0.097662
203 | 220 | 445 | Hamilton | HM08 | 955 | 0.097382
204 | 142 | 2438 | Angus Valley | AG02 | 1899 | 0.096367
205 | 62 | 2239 | Steck | ST04 | 2097 | 0.095374
206 | 63 | 3970 | McNeil | MC07 | 2564 | 0.093604
207 | 152 | 1059 | Koenig Lane | KL13 | 1057 | 0.085147
208 | 155 | 1818 | Cameron | CM06 | 2414 | 0.07995
209 | 145 | 150 | Carson Creek | CC02 | 228 | 0.078947
210 | 143 | 993 | Cardinal Lane | CL07 | 953 | 0.073452
211 | not in service |  | Carson Creek | CC03 | 3563 | 0.072972
212 | 169 | 498 | Barton | BA02 | 295 | 0.071186
213 | 182 | 3707 | Burleson | BU08 | 3808 | 0.068277
214 | 138 | 1784 | Jett | JE04 | 1932 | 0.065735
215 | not in service |  | Dessau | DE03 | 962 | 0.06341
216 | 203 | 1766 | Oak Hill | OH04 | 1961 | 0.061703
217 | 171 | 366 | Riverplace | RP04 | 779 | 0.061617
218 | 157 | 13 | Burleson | BU05 | 52 | 0.057692
219 | 162 | 1591 | Barton | BA07 | 1547 | 0.054945
220 | 69 | 3645 | Carson Creek | CC06 | 132 | 0.05303
221 | 213 | 2882 | Williamson | WI08 | 1383 | 0.050615
222 | 6 | 1934 | Seaholm Plant | SP06 | 1837 | 0.050082
223 | 197 | 113 | Burleson | BU03 | 143 | 0.041958
224 | 23 | 2463 | Howard Lane | HL03 | 2072 | 0.033301
225 | 176 | 305 | Summit | SU06 | 164 | 0.030488
226 | 208 | 468 | North | NO05 | 440 | 0.027273
227 | 214 | 972 | Howard Lane | HL06 | 852 | 0.025822
228 | 9 | 12 | Bergstrom | BE04 | 47 | 0.021277
229 | 179 | 899 | Hamilton | HM03 | 1005 | 0.014925
230 | 75 | 1455 | Williamson | WI10 | 1368 | 0.01462
231 | 196 | 512 | Jollyville | JV07 | 1027 | 0.012658
232 | 141 | 2221 | McNeil | MC02 | 2181 | 0.0064191
233 | 160 | 2236 | McNeil | MC05 | 2712 | 0.005531
234 | 1 | 961 | Seaholm Plant | SP05 | 1585 | 0.00063091
235 | not in service |  | Hi-Cross | HC02 | 527 | 0
236 | not in service |  | Burleson | BUO2 | 82 | 0
237 | not in service |  | Fiskville | FV02 | 990 | 0
238 | not in service |  | Barton | BA08 | 246 | 0

## Feeder-SAIDI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System | [5 empty] | Total Number of Feeders
With More Than 10 Customers | [5 empty] | 238
Add or Delete Rows as Necessary
Austin Energy
2000 SAIDI Ranking | 1999 SAIDI Ranking | 1999 Number of Customers | Substation Identification | Feeder Identification | 2000 Number of Customers | 2000 SAIDI Value
1 | 1 | 1652 | Northland | NL14 | 737 | 801.3683
2 | 19 | 1117 | Bergstrom | BE06 | 1486 | 502.7709
3 | 87 | 439 | Warren | WA02 | 464 | 477.7787
4 | 30 | 471 | Walnut Creek | WC07 | 323 | 466.4737
5 | 200 | 1192 | Hamilton | HM09 | 840 | 418.3076
6 | 59 | 1704 | Austin Dam | AD02 | 896 | 399.1897
7 | 17 | 688 | Warren | WA05 | 660 | 385.0364
8 | 54 | 792 | Northland | NL02 | 618 | 342.3341
9 | 60 | 1797 | Warren | WA01 | 1997 | 335.4852
10 | 21 | 1783 | Patton Lane | PL02 | 1062 | 299.2836
11 | 122 | 2050 | Warren | WA06 | 1996 | 299.2269
12 | 63 | 2287 | Northland | NL08 | 2439 | 298.2782
13 | 74 | 2214 | North | NO02 | 2844 | 297.0012
14 | 161 | 1433 | Seaholm Plant | SP01 | 1671 | 294.8592
15 | 32 | 484 | Walnut Creek | WC08 | 582 | 285.8952
16 | 69 | 872 | Hi-Cross | HC06 | 1037 | 285.4513
17 | 12 | 221 | Bergstrom | BE02 | 260 | 254.9885
18 | 114 | 1188 | Wheless Lane | WL04 | 1648 | 251.1341
19 | 85 | 1918 | Summit | SU02 | 2284 | 248.6525
20 | 104 | 2129 | Salem Walk | SW06 | 1415 | 233.9399
21 | 210 | 768 | Jett | JE02 | 1401 | 217.7434
22 | 117 | 3366 | Daffin Gin | DG01 | 3963 | 211.433
23 | 115 | 2039 | Lakeway | LW02 | 2494 | 207.1787
24 | 171 | 889 | Cameron | CM03 | 248 | 204.3952
25 | 25 | 2123 | Northland | NL11 | 2146 | 199.3751
26 | 150 | 710 | Burleson | BU06 | 697 | 199.1334
27 | not in service |  | Techridge | TR02 | 1607 | 196.6062
28 | 35 | 2159 | North | NO01 | 2037 | 195.5811
29 | 92 | 2295 | Fiskville | FV05 | 3288 | 193.0587
30 | 129 | 1792 | Cardinal Lane | CL01 | 1828 | 190.2281
31 | 100 | 2320 | Fiskville | FV06 | 2602 | 189.1457
32 | not in service |  | Wheless Lane | WL07 | 2403 | 187.8736
33 | not in service |  | Steck | ST07 | 729 | 181.8985
34 | 67 | 2660 | Koenig Lane | KL14 | 2735 | 181.4494
35 | 219 | 673 | Hamilton | HM04 | 674 | 180.7757
36 | 175 | 1709 | Koenig Lane | KL07 | 1687 | 180.1612
37 | 109 | 1229 | Burleson | BU07 | 1251 | 179.7618
38 | 154 | 2230 | Austin Dam | AD05 | 2292 | 177.2866
39 | 11 | 180 | Warren | WA04 | 178 | 173.9888
40 | 86 | 2519 | Koenig Lane | KL06 | 2582 | 165.0101
41 | 116 | 1509 | Jollyville | JV05 | 1693 | 164.5915
42 | 53 | 1578 | Jollyville | JV03 | 1766 | 163.337
43 | 27 | 2413 | Slaughter Lane | SL05 | 2644 | 162.0825
44 | 99 | 386 | Carson Creek | CC05 | 451 | 153.9195
45 | 23 | 864 | Bee Creek | BC06 | 952 | 152.8981
46 | 198 | 768 | Wheless Lane | WL05 | 777 | 150.565
47 | 197 | 820 | Kingsbery | KB01 | 874 | 146.5423
48 | 66 | 3357 | Kingsbery | KB03 | 2618 | 146.1216
49 | 142 | 881 | Warren | WA03 | 881 | 145.0363
50 | 18 | 1442 | Northland | NL01 | 541 | 144.658
51 | 162 | 2662 | North | NO07 | 2751 | 143.0927
52 | 137 | 619 | Brodie Lane | BL03 | 1483 | 142.8908
53 | 133 | 2938 | Magnesium Plant | MP06 | 3164 | 138.5101
54 | 221 | 1532 | Summit | SU04 | 1487 | 136.9596
55 | 39 | 506 | Northland | NL15 | 1553 | 136.434
56 | 61 | 1101 | Steck | ST05 | 1086 | 131.4907
57 | 123 | 1527 | Bergstrom | BE05 | 1611 | 127.3088
58 | 64 | 985 | Steck | ST06 | 948 | 126.5257
59 | 7 | 1262 | Lakeway | LW04 | 1013 | 124.0059
60 | 24 | 1757 | Cardinal Lane | CL11 | 2168 | 121.4737
61 | 181 | 2086 | McNeil | MC01 | 260 | 119.8
62 | 43 | 1273 | Magnesium Plant | MP05 | 1852 | 118.5508
63 | 72 | 1878 | Salem Walk | SW01 | 2110 | 118.0953
64 | 218 | 448 | Summit | SU01 | 151 | 117.4768
65 | 172 | 893 | Sprinkle | SK01 | 384 | 116.1849
66 | 128 | 1899 | Walnut Creek | WC10 | 2497 | 113.8771
67 | 48 | 1455 | Commons Ford | CF04 | 1461 | 113.501
68 | 96 | 2265 | Cardinal Lane | CL12 | 2364 | 112.3617
69 | 107 | 2524 | Magnesium Plant | MP03 | 1224 | 109.7941
70 | 201 | 957 | Summit | SU03 | 927 | 109.4196
71 | 124 | 1888 | McNeil | MC08 | 1837 | 107.2188
72 | 103 | 1165 | Sprinkle | SK03 | 828 | 104.5169
73 | 163 | 60 | Burleson | BU04 | 79 | 104.4304
74 | 160 | 595 | Barton | BA01 | 516 | 103.4961
75 | 16 | 725 | Koenig Lane | KL01 | 838 | 100.658
76 | 140 | 1017 | North | NO08 | 1069 | 99.8859
77 | 44 | 2428 | Brodie Lane | BL01 | 2415 | 98.3379
78 | not in service |  | Seaholm Plant | SP12 | 2272 | 97.6206
79 | 125 | 1780 | Zilker | ZL02 | 1730 | 97.1575
80 | 191 | 1505 | Cameron | CM02 | 1490 | 94.1678
81 | 26 | 2474 | Cardinal Lane | CL03 | 1854 | 93.7065
82 | 52 | 1724 | Hi-Cross | HC01 | 2113 | 92.2003
83 | 3 | 376 | Cameron | CM01 | 320 | 90.8
84 | 119 | 613 | Jollyville | JV02 | 14 | 89.6429
85 | 127 | 568 | Howard Lane | HL05 | 750 | 88.2218
86 | 194 | 34 | Daffin Gin | DG02 | 131 | 85.6718
87 | 42 | 1212 | Seaholm Plant | SP09 | 1269 | 82.4933
88 | 91 | 283 | Williamson | WI05 | 106 | 81.4623
89 | 105 | 997 | Lakeshore | LS01 | 1239 | 80.0137
90 | 120 | 1093 | Lakeway | LW03 | 1287 | 79.3574
91 | 58 | 3649 | Hi-Cross | HC09 | 1495 | 78.0502
92 | 179 | 2282 | Kingsbery | KB06 | 2822 | 77.3942
93 | 193 | 2162 | Williamson | WI02 | 846 | 76.8865
94 | 190 | 3043 | McNeil | MC06 | 2828 | 76.0258
95 | 83 | 1024 | Howard Lane | HL01 | 957 | 75.9634
96 | 4 | 1149 | Riverplace | RP05 | 1708 | 75.4423
97 | not in service |  | Kingsbery | KB02 | 82 | 75.0122
98 | 111 | 1318 | Bee Creek | BC03 | 1324 | 72.4267
99 | 93 | 1214 | Seaholm Plant | SP02 | 1240 | 72.4065
100 | 8 | 1283 | Commons Ford | CF02 | 1402 | 71.1526
101 | 211 | 1366 | Hamilton | HM01 | 1501 | 69.3764
102 | 209 | 1655 | Brodie Lane | BL02 | 660 | 68.4879
103 | 94 | 949 | Seaholm Plant | SP07 | 946 | 67.7791
104 | 139 | 1224 | Burleson | BU01 | 1192 | 67.5631
105 | not in service |  | Wheless Lane | WL08 | 1947 | 65.5085
106 | 79 | 582 | Bee Creek | BC02 | 612 | 65.3235
107 | 28 | 2293 | Wheless Lane | WL01 | 2272 | 64.4595
108 | 136 | 600 | Kingsbery | KB04 | 619 | 64.4507
109 | 97 | 96 | Sprinkle | SK02 | 113 | 63.5133
110 | 46 | 372 | Commons Ford | CF01 | 533 | 63.0338
111 | 34 | 1873 | Williamson | WI09 | 1877 | 61.9723
112 | 14 | 2178 | Pedernales | PE04 | 1949 | 61.636
113 | not in service |  | Hamilton | HM06 | 330 | 61.4182
114 | 88 | 3166 | Howard Lane | HL04 | 3144 | 61.3375
115 | 6 | 2018 | Koenig Lane | KL03 | 1354 | 60.599
116 | 178 | 897 | Cardinal Lane | CL04 | 882 | 60.2517
117 | 45 | 1793 | Brodie Lane | BL04 | 2263 | 60.2223
118 | 176 | 1458 | Hamilton | HM11 | 2204 | 59.7854
119 | 49 | 3097 | Salem Walk | SW08 | 1873 | 59.6636
120 | 20 | 1077 | Cardinal Lane | CL08 | 1174 | 59.4557
121 | 185 | 140 | Commons Ford | CF03 | 347 | 58.0749
122 | 196 | 3235 | Williamson | WI01 | 1680 | 56.1685
123 | 222 | 574 | North | NO09 | 591 | 56.1489
124 | 81 | 1744 | Wheless Lane | WL02 | 791 | 55.6448
125 | 71 | 1300 | Steck | ST02 | 1292 | 55.5193
126 | 110 | 2314 | Salem Walk | SW04 | 2207 | 55.1232
127 | 151 | 2025 | Oak Hill | OH05 | 2221 | 54.5799
128 | 147 | 1036 | Cameron | CM04 | 1515 | 54.3485
129 | not in service |  | Trading Post | TP01 | 972 | 53.7819
130 | 165 | 441 | Koenig Lane | KL12 | 441 | 53.6961
131 | 82 | 2109 | Zilker | ZL03 | 2031 | 52.6957
132 | 77 | 2119 | Salem Walk | SW05 | 2168 | 52.4096
133 | 68 | 2226 | Koenig Lane | KL10 | 2256 | 52.379
134 | 108 | 1078 | Patton Lane | PL01 | 1266 | 51.0569
135 | 57 | 1139 | Commons Ford | CF05 | 1233 | 50.9773
136 | 55 | 1281 | Slaughter Lane | SL04 | 889 | 50.9336
137 | 148 | 1602 | Howard Lane | HL02 | 1795 | 50.605
138 | not in service |  | Steck | ST08 | 145 | 50.2759
139 | 73 | 4172 | Slaughter Lane | SL01 | 3298 | 46.9845
140 | 76 | 1168 | Austin Dam | AD01 | 1198 | 44.8289
141 | 168 | 61 | Lakeshore | LS04 | 70 | 44.5857
142 | 153 | 1098 | Dessau | DE01 | 1622 | 41.8002
143 | 206 | 1510 | Barton | BA09 | 1752 | 41.1067
144 | 126 | 1884 | Magnesium Plant | MP07 | 1964 | 41.1008
145 | 205 | 2790 | Northland | NL13 | 1589 | 39.3858
146 | 173 | 287 | Lakeshore | LS06 | 348 | 39.2213
147 | 121 | 2036 | Steck | ST01 | 2012 | 39.008
148 | 98 | 2281 | Magnesium Plant | MP02 | 2980 | 37.651
149 | 13 | 2707 | Salem Walk | SW02 | 2617 | 37.5799
150 | 167 | 709 | Steck | ST03 | 729 | 37.2346
151 |  |  | Austin Dam | AD06 | 923 | 37.221
152 | 50 | 1285 | North | NO04 | 1325 | 37.0377
153 | 204 | 2053 | Wheless Lane | WL03 | 1906 | 36.5525
154 | 36 | 2253 | Burleson | BU09 | 3785 | 35.749
155 | 37 | 756 | Cameron | CM05 | 504 | 35.7202
156 | not in service |  | Fiskville | FV04 | 31 | 35.5161
157 | 186 | 1420 | Cardinal Lane | CL06 | 1889 | 34.8391
158 | 75 | 837 | Pedernales | PE09 | 752 | 34.1596
159 | 188 | 3416 | Hi-Cross | HC08 | 3673 | 33.11
160 | 149 | 467 | Brodie Lane | BL05 | 1817 | 32.3357
161 | 31 | 1733 | Jett | JE03 | 1782 | 31.3967
162 | 131 | 943 | Onion Creek | OC04 | 1268 | 30.9885
163 | 15 | 3146 | Pedernales | PE02 | 3020 | 30.193
164 | 33 | 1399 | Bee Creek | BC05 | 1980 | 30.1318
165 | 146 | 963 | Magnesium Plant | MP09 | 1020 | 29.5275
166 | 29 | 1144 | Jollyville | JV04 | 1712 | 27.8394
167 | 199 | 3380 | Williamson | WI06 | 2939 | 27.248
168 | not in service |  | Patton Lane | PL03 | 2030 | 26.6182
169 | 155 | 2975 | Angus Valley | AG03 | 2936 | 26.2405
170 | 89 | 2408 | Fiskville | FV03 | 2651 | 26.1068
171 | 47 | 3165 | Williamson | WI11 | 3063 | 25.4316
172 | not in service |  | Williamson | WI03 | 10 | 25.2
173 | 158 | 1789 | Pedernales | PE07 | 1674 | 24.3906
174 | 102 | 601 | Koenig Lane | KL08 | 587 | 24.3901
175 | 138 | 150 | Carson Creek | CC02 | 228 | 23.5789
176 | 220 | 445 | Hamilton | HM08 | 955 | 22.6136
177 | 212 | 157 | Jollyville | JV08 | 781 | 21.4609
178 | 135 | 412 | Kingsbery | KB05 | 403 | 20.7841
179 | 41 | 2409 | Pedernales | PE01 | 1181 | 20.5995
180 | 78 | 3015 | Slaughter Lane | SL02 | 2601 | 20.3429
181 | 170 | 920 | Barton | BA05 | 896 | 20.1384
182 | 141 | 677 | Bergstrom | BE03 | 725 | 20.1062
183 | 130 | 2175 | Northland | NL12 | 2489 | 19.505
184 | 132 | 736 | Barton | BA04 | 727 | 19.0468
185 | not in service |  | Seaholm Plant | SP11 | 369 | 19
186 | not in service |  | Oak Hill | OH01 | 941 | 17.9065
187 | 22 | 1696 | Oak Hill | OH02 | 2007 | 17.1261
188 | 143 | 2048 | Hi-Cross | HC03 | 1487 | 15.9045
189 | 159 | 2262 | Fiskville | FV01 | 2518 | 15.1839
190 | not in service |  | Dessau | DE02 | 1343 | 15.0141
191 | 95 | 1966 | Salem Walk | SW07 | 1906 | 14.3001
192 | 195 | 960 | Hi-Cross | HC05 | 2489 | 13.636
193 | not in service |  | Carson Creek | CC03 | 3563 | 13.2554
194 | 9 | 3970 | McNeil | MC07 | 2564 | 13.0761
195 | 177 | 13 | Burleson | BU05 | 52 | 12.9423
196 | 62 | 1499 | Cardinal Lane | CL09 | 618 | 12.822
197 | 38 | 550 | Summit | SU05 | 164 | 12.6341
198 | 202 | 2702 | Hamilton | HM05 | 2600 | 12.4485
199 | 145 | 2239 | Steck | ST04 | 2097 | 12.2818
200 | 169 | 2438 | Angus Valley | AG02 | 1899 | 11.8352
201 | not in service |  | Hi-Cross | HC07 | 1458 | 11.7462
202 | 40 | 1609 | Pedernales | PE05 | 1438 | 11.4513
203 | 215 | 980 | Oak Hill | OH06 | 940 | 11.3362
204 | 118 | 1818 | Cameron | CM06 | 2414 | 10.2742
205 | 5 | 2729 | Oak Hill | OH03 | 2453 | 9.8345
206 | 70 | 787 | Barton | BA03 | 1997 | 9.5223
207 | 152 | 3707 | Burleson | BU08 | 3808 | 9.5003
208 | 180 | 967 | North | NO06 | 950 | 9.0053
209 | 56 | 198 | Jett | JE06 | 204 | 9
210 | 183 | 208 | Hamilton | HM10 | 240 | 8.975
211 | 166 | 498 | Barton | BA02 | 295 | 8.3898
212 | 106 | 993 | Cardinal Lane | CL07 | 953 | 8.3158
213 | 134 | 1784 | Jett | JE04 | 1932 | 8.0818
214 | 187 | 3040 | Wheless Lane | WL06 | 1416 | 7.935
215 | 101 | 366 | Riverplace | RP04 | 779 | 7.3094
216 | 203 | 1766 | Oak Hill | OH04 | 1961 | 7.1815
217 | 156 | 1059 | Koenig Lane | KL13 | 1057 | 5.8013
218 | 84 | 1934 | Seaholm Plant | SP06 | 1837 | 4.8655
219 | 207 | 2882 | Williamson | WI08 | 1383 | 4.6059
220 | 182 | 1591 | Barton | BA07 | 1547 | 4.5792
221 | not in service |  | Dessau | DE03 | 962 | 4.3389
222 | 184 | 305 | Summit | SU06 | 164 | 4.2866
223 | 80 | 3645 | Carson Creek | CC06 | 132 | 4.2803
224 | 51 | 2463 | Howard Lane | HL03 | 2072 | 2.6626
225 | 216 | 972 | Howard Lane | HL06 | 852 | 2.3498
226 | 112 | 1455 | Williamson | WI10 | 1368 | 2.1857
227 | 189 | 512 | Jollyville | JV07 | 1027 | 2.0331
228 | 192 | 113 | Burleson | BU03 | 143 | 1.8601
229 | 208 | 468 | North | NO05 | 440 | 1.1864
230 | 144 | 2236 | McNeil | MC05 | 2712 | 1.0428
231 | 157 | 899 | Hamilton | HM03 | 1005 | 0.98109
232 | 90 | 2221 | McNeil | MC02 | 2181 | 0.66667
233 | 2 | 12 | Bergstrom | BE04 | 47 | 0.25532
234 | 10 | 961 | Seaholm Plant | SP05 | 1585 | 0.029653
235 | not in service |  | Hi-Cross | HC02 | 527 | 0
236 | not in service |  | Fiskville | FV02 | 990 | 0
237 | not in service |  | Burleson | BU02 | 82 | 0
238 | not in service |  | Barton | BA08 | 246 | 0

## Causes
Austin Energy
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
2000 Reporting Year
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 21.54%
|  | Vegetation | 11.26%
|  | Animals and Birds | 20.17%
|  | People (Including cars and farm equip) | 4.9%
|  | Utility-owned Equipment | 22.04%
Other
|  | Unknown | 20.09%