DOCKET NO. 23429

# APPLICATION OF ENTERGY		§		BEFORE THE

# GULF STATES, INC. TO AMEND ITS	§		PUBLIC UTILITY

# CERTIFICATE OF CONVENIENCE		§		COMMISSION OF

# AND NECESSITY FOR A PROPOSED	§		TEXAS

# TRANSMISSION LINE IN		§

MONTGOMERGY COUNTY, TEXAS	§

RESPONSE TO LINE 820 TECHNICAL

CONFERENCE OUTSTANDING QUESTIONS

Q. Why was Line 403 de-energized?

A.  Line 403, constructed in 1981, originally connected Goslin Substation to Oak Ridge Substation with the anticipation of load growth north of these two substations in an area known as the Trade Center.  In 1992, Hughes Tools, a large industrial plant, relocated from the Houston area to south central Montgomery County.  This industrial plant created a need for another 138kV source south of the proposed Forest Substation site and almost directly between Oak Ridge and Goslin Substations.  At that time, the plan to construct Forest Substation was thus altered to construct Metro Substation.  In addition to the new substation, this plan entailed the construction of Line 169 (Oak Ridge to Metro) and Line 803 (Metro to Goslin) and the de-energization of Line 403.