## Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | Entergy Texas, Inc.
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 376
Due: |  | February 12, 2010
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 37855
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
T. Brian Almon, Engineering Specialist
Electric Division
Commission Staff
Voice: | 512 936 7348
Fax: | 512 936 7361
E-mail: | mailto: brian.almon@puc.state.tx.us

## Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
Substantive Rule §25.81
2009 Reporting Year
Amended November 30, 2010
Entergy Texas, Inc.
Project 37855

## System-SAIFI
Entergy Texas, Inc.
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2009 | 1.67 | 0.075 | 0.083 | 0.19967 | 0.1799 | 0.086 | 0.15337 | 0.20649 | 0.14011 | 0.16809 | 0.20253 | 0.046 | 0.12981
Scheduled
2009 | 0.025652 | 0.00191 | 0.00071 | 0.00243 | 0.00182 | 0.00219 | 0.00361 | 0.0026 | 0.0046 | 0.00093 | 0.00191 | 0.00073 | 0.00222
Outside Causes
2009 | 0.33495 | 0.012831 | 0.015047 | 0.055588 | 0.045825 | 0.005565 | 0.006146 | 0.035508 | 0.029983 | 0.038809 | 0.037728 | 0.017984 | 0.033939
Major Events
2009 | 1.8e-05 | 0 | 0 | 1.8e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## System-SAIDI
Entergy Texas, Inc.
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2009 | 168.4703 | 7.0225 | 7.2759 | 23.7482 | 18.6432 | 8.2571 | 11.8646 | 23.095 | 13.0499 | 15.1546 | 22.6929 | 4.8231 | 12.846
Scheduled
2009 | 2.1978 | 0.2685 | 0.0479 | 0.2013 | 0.0929 | 0.185 | 0.3164 | 0.3135 | 0.2792 | 0.0675 | 0.1258 | 0.0666 | 0.2332
Outside Causes
2009 | 24.0412 | 2.0308 | 2.2777 | 3.8374 | 3.018 | 0.3545 | 0.3528 | 2.3094 | 1.4122 | 3.7244 | 2.1978 | 0.7619 | 1.7643
Major Events
2009 | 0.0026 | 0 | 0 | 0.0026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Feeder-SAIFI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System |  |  |  |  | Total Number of Feeders
With More Than 10 Customers |  |  |  |  | 376
Add or Delete Rows as Necessary
Entergy Texas, Inc.
2009 SAIFI Ranking | 2008 SAIFI Ranking | Substation Identification | Feeder Identification | Number of Customers | 2009 SAIFI Value
1 | 122 | HANKAMER | 207HA | 702 | 6.7293
2 | 233 | CRYSTAL | 566CR | 1419 | 6.3354
3 | 301 | STOWELL | 234ST | 141 | 6.2695
4 | 29 | CHINA | 93CHI | 1215 | 6.0551
5 | 341 | HIMEX | 222HI | 172 | 5.8256
6 | 141 | STOWELL | 232ST | 1044 | 5.3487
7 | #N/A | FORT WORTH | 567FT | 687 | 5.3275
8 | 41 | CHEEK | 166CH | 331 | 5.2447
9 | #N/A | HIMEX | 223HI | 2416 | 5.1651
10 | 315 | GRIMES | 981GR | 323 | 4.7059
11 | 99 | LONGMIRE | 580LM | 1429 | 4.6697
12 | 15 | LOVELLS LAKE | 141LV | 717 | 4.5732
13 | 6 | PEE DEE | 809PD | 1552 | 4.5277
14 | 11 | SPLENDORA | 309SP | 1206 | 4.3342
15 | 131 | RIVTRIN | 269RV | 2920 | 4.3137
16 | 142 | CALVERT | 6CAL | 1588 | 4.1908
17 | 303 | HIMEX | 221HI | 102 | 4.1471
18 | 282 | OAK RIDGE | 742OK | 2442 | 4.1319
19 | #N/A | JOHNSTOWN | 544JT | 2360 | 4.1182
20 | 58 | APOLLO | 321AP | 848 | 4.0861
21 | 160 | HEARNE | 25HRN | 228 | 3.9737
22 | 65 | NECHES | 193NE | 1032 | 3.938
23 | 180 | YANKEE DOODLE | 22YAN | 2381 | 3.9177
24 | 121 | LINDBERGH | 40LNB | 1152 | 3.895
25 | 109 | BAYSHORE | 213BA | 1605 | 3.7408
26 | 51 | WARREN | 592WR | 2042 | 3.74
27 | 28 | CONROE BULK | 572CN | 1277 | 3.7392
28 | 157 | CONAIR | 513CN | 1364 | 3.728
29 | 96 | WARREN | 506WR | 1380 | 3.6551
30 | 20 | DOUCETTE | 569DC | 184 | 3.6304
31 | 4 | CLEVELAND | 425CV | 1948 | 3.6124
32 | 129 | LACON | 539LA | 1118 | 3.5823
33 | 119 | HUNTSVILLE | 600HU | 1775 | 3.4935
34 | 300 | CHEEK | 165CH | 103 | 3.4854
35 | 8 | GOSLIN | 708GL | 2204 | 3.4324
36 | 358 | CENTRAL | 130CE | 687 | 3.3916
37 | 366 | HEARNE | 28HRN | 26 | 3.3846
38 | 284 | PORT ACRES SUB | 67PTA | 577 | 3.383
39 | 172 | MCHALE | 113MC | 626 | 3.3754
40 | 325 | HANKS | 24HKS | 840 | 3.2738
41 | 10 | CHEEK | 160CH | 1198 | 3.187
42 | 27 | SPLENDORA | 307SP | 1606 | 3.1594
43 | 153 | NAVASOTA | 905NA | 2271 | 3.1594
44 | 232 | APOLLO | 320AP | 1417 | 3.1475
45 | 294 | CROWDER | 104CD | 1573 | 3.1265
46 | 13 | TRANSCO | 48TCO | 178 | 3.0674
47 | 30 | CLEVELAND | 426CV | 2840 | 3.0377
48 | 182 | FRONT STREET | 307FR | 492 | 3
49 | 19 | DOUCETTE | 568DC | 491 | 2.831
50 | 5 | NEW CANEY | 335NC | 1588 | 2.7752
51 | 234 | HUNTSVILLE | 607HU | 3321 | 2.7721
52 | 23 | MCDONALD | 477MD | 1324 | 2.7621
53 | 242 | EGYPT | 550EP | 2143 | 2.7522
54 | 14 | CRYSTAL | 570CR | 749 | 2.725
55 | 309 | CROCKETT | 65CRK | 504 | 2.7083
56 | 44 | NEW CANEY | 333NC | 5598 | 2.6851
57 | 196 | WEST ORANGE | 393WO | 732 | 2.6066
58 | 261 | ECHO | 70ECH | 1504 | 2.5725
59 | 154 | ADAMS BAYOU | 332AD | 596 | 2.5705
60 | 70 | SHEAWILL | 536SH | 1176 | 2.5604
61 | 243 | KOLBS | 36KOL | 1265 | 2.5518
62 | #N/A | JOHNSTOWN | 345JT | 1004 | 2.5339
63 | 107 | CLEVELAND | 406CV | 1441 | 2.5316
64 | 288 | CONAIR | 515CN | 2068 | 2.529
65 | 57 | CORRIGAN BULK | 238CR | 590 | 2.5237
66 | 84 | WINSHIRE | 240WS | 1087 | 2.4931
67 | 238 | ELIZABETH | 123EL | 2381 | 2.4725
68 | 9 | RIVTRIN | 268RV | 2517 | 2.4418
69 | 168 | WINFREE | 340WN | 1026 | 2.423
70 | 231 | OAK RIDGE | 743OK | 1659 | 2.4057
71 | 125 | CHINA | 92CHI | 594 | 2.3973
72 | 162 | MANCHESTER | 67MAN | 1004 | 2.3865
73 | 340 | YANKEE DOODLE | 24YAN | 336 | 2.3839
74 | 149 | PEE DEE | 808PD | 1913 | 2.3837
75 | 123 | CROWDER | 105CD | 885 | 2.3751
76 | 91 | WALDEN | 564WD | 5320 | 2.3716
77 | 79 | PANSY | 185PS | 625 | 2.3712
78 | 193 | HUMPHREY | 108HM | 37 | 2.3514
79 | 224 | WYNTEX | 634WT | 1218 | 2.3415
80 | 72 | TEMCO | 628TE | 349 | 2.3266
81 | 110 | LINDBERGH | 42LNB | 1700 | 2.3212
82 | 85 | HANKS | 25HKS | 899 | 2.3092
83 | 354 | APRIL | 591AP | 1502 | 2.3089
84 | 89 | NEW CANEY | 337NC | 544 | 2.2574
85 | 304 | CENTRAL | 131CE | 940 | 2.2479
86 | 173 | MCDONALD | 478MD | 614 | 2.2459
87 | 52 | Alden Bridge | 763AL | 2073 | 2.233
88 | 239 | OAK RIDGE | 744OK | 2429 | 2.1976
89 | 139 | OILLA | 345OI | 1263 | 2.1948
90 | 369 | METRO | 722ME | 845 | 2.1822
91 | 147 | CLEVELAND | 405CV | 1697 | 2.1756
92 | 53 | BRIARCLIFF | 32BRC | 1296 | 2.1582
93 | 216 | SOUR LAKE | 105SL | 1208 | 2.1101
94 | 226 | WALDEN | 563WD | 1633 | 2.1078
95 | 198 | STOWELL | 233ST | 501 | 2.1058
96 | 98 | MANCHESTER | 66MAN | 1931 | 2.0906
97 | 73 | TAMINA | 317TA | 1081 | 2.0611
98 | 61 | CALDWELL INDUSTRIAL | 138CI | 676 | 2.0429
99 | 349 | LINCOLN | 15LCN | 275 | 2.0182
100 | 102 | KOUNTZE BULK | 435KT | 47 | 2
101 | 283 | BRIDGE CITY | 362BD | 1264 | 1.9818
102 | 218 | HANKAMER | 206HA | 580 | 1.9759
103 | 146 | NAVASOTA | 904NA | 1213 | 1.9588
104 | 80 | DAISETTA | 743DA | 335 | 1.9463
105 | 321 | FEDERAL | 801FE | 222 | 1.9324
106 | 74 | VIDOR | 163VD | 2906 | 1.9174
107 | 225 | LOEB | 17LOB | 861 | 1.9129
108 | 137 | ROSEDALE | 151RS | 1102 | 1.9074
109 | 364 | Alden Bridge | 769AL | 1007 | 1.9037
110 | 120 | BEVIL | 156BE | 665 | 1.8932
111 | 356 | WESTSIDE | 113WS | 311 | 1.8875
112 | 7 | DOUCETTE | 570DC | 1099 | 1.8799
113 | 258 | DAYTON BULK | 723DY | 898 | 1.8742
114 | 88 | DOBBIN | 920DO | 1538 | 1.8622
115 | 246 | HANKS | 22HKS | 1153 | 1.8552
116 | 12 | BEVIL | 155BE | 3524 | 1.8292
117 | 201 | TYRRELL | 37TYR | 508 | 1.8268
118 | 227 | KOLBS | 34KOL | 1221 | 1.8108
119 | 69 | LACON | 540LA | 1479 | 1.7897
120 | 362 | Alden Bridge | 768AL | 3072 | 1.7786
121 | 249 | TAMINA | 598TA | 704 | 1.7784
122 | 291 | PLANTATION | 545PL | 1044 | 1.7778
123 | 250 | CORDREY | 327CO | 1023 | 1.7478
124 | #N/A | FORT WORTH | 99FTW | 160 | 1.7312
125 | 322 | MCHALE | 111MC | 572 | 1.722
126 | 202 | BAYSHORE | 212BA | 42 | 1.7143
127 | 260 | PORT ACRES BULK | 70PAS | 787 | 1.7128
128 | 255 | ORANGE | 351ON | 380 | 1.6868
129 | 92 | HICKORY RIDGE | 341HI | 1503 | 1.6786
130 | 36 | METRO | 719ME | 1434 | 1.6695
131 | 204 | DAYTON BULK | 726DY | 1472 | 1.6651
132 | 33 | DAYTON BULK | 725DY | 1211 | 1.6606
133 | 236 | PORT ACRES SUB | 68PTA | 1139 | 1.6383
134 | 81 | CENTRAL | 132CE | 1751 | 1.6322
135 | 124 | RAYWOOD | 73RAY | 500 | 1.626
136 | 62 | EASTGATE | 781EG | 1113 | 1.6181
137 | 254 | CROCKETT | 195CR | 1293 | 1.6164
138 | 317 | OAK RIDGE | 740OK | 1256 | 1.5924
139 | 40 | NEW CANEY | 334NC | 4628 | 1.5817
140 | 87 | LACON | 537LA | 1785 | 1.5742
141 | 66 | MCLEWIS | 382MC | 736 | 1.5584
142 | 104 | CONAIR | 512CN | 1238 | 1.5452
143 | 126 | BAYSHORE | 211BA | 964 | 1.5425
144 | 35 | ELIZABETH | 120EL | 1347 | 1.5397
145 | 285 | NAVASOTA | 969NA | 812 | 1.5369
146 | 114 | STONEGATE | 91STG | 1251 | 1.5196
147 | 148 | CROWDER | 103CD | 1386 | 1.518
148 | 197 | GOREE | 681GR | 794 | 1.5038
149 | 181 | Alden Bridge | 766AL | 1637 | 1.5003
150 | 267 | WOODVILLE | 594WD | 1203 | 1.4996
151 | 152 | SPLENDORA | 308SP | 2276 | 1.4917
152 | 144 | BRIARCLIFF | 30BRC | 2345 | 1.4772
153 | 229 | GOREE | 682GR | 1046 | 1.4637
154 | 115 | VIRGINIA | 131VI | 1402 | 1.4593
155 | 158 | HUMPHREY | 107HM | 1962 | 1.4475
156 | 54 | RAYWOOD | 74RAY | 1131 | 1.4439
157 | 365 | GOSLIN | 701GL | 1157 | 1.4287
158 | 241 | VIWAY | 682VI | 1829 | 1.4057
159 | 265 | BEVIL | 154BE | 2166 | 1.4049
160 | 330 | WEST ORANGE | 392WO | 664 | 1.3961
161 | 194 | AMELIA BULK | 181AM | 1663 | 1.3891
162 | 324 | HUMPHREY | 106HM | 1110 | 1.3847
163 | 93 | BATSON | 53BAT | 861 | 1.3624
164 | 103 | TEMCO | 627TE | 1007 | 1.3585
165 | 134 | SILSBEE | 462SI | 757 | 1.3527
166 | 286 | CROWDER | 102CD | 2225 | 1.3524
167 | 333 | WALDEN | 560WD | 625 | 1.3488
168 | 278 | PORT NECHES | 46PTN | 1259 | 1.3423
169 | 184 | GRIMES | 883GR | 831 | 1.3369
170 | 111 | HAMPTON | 158HA | 1101 | 1.3351
171 | 211 | JIROU | 75JRU | 66 | 1.3333
172 | 206 | GROVES-EGSI | 59GRO | 1673 | 1.3293
173 | 38 | SARATOGA | 761SA | 422 | 1.3223
174 | 308 | PARKDALE | 176PR | 532 | 1.3177
175 | 235 | GOSLIN | 702GL | 1715 | 1.3073
176 | 334 | BAYOU FANNETT | 250BY | 33 | 1.303
177 | 208 | JIROU | 78JRU | 406 | 1.2956
178 | 163 | WOODVILLE | 593WD | 729 | 1.2812
179 | 21 | MAGNOLIA AMES | 711MG | 786 | 1.2748
180 | 75 | HANKS | 23HKS | 1288 | 1.2679
181 | 251 | ECHO | 72ECH | 506 | 1.2648
182 | 67 | CALVERT | 4CAL | 2122 | 1.2606
183 | 101 | CROCKETT | 61CRK | 104 | 1.25
184 | 170 | NAVASOTA | 901NA | 336 | 1.244
185 | 82 | LOVELLS LAKE | 142LV | 318 | 1.2358
186 | 269 | CLEVELAND | 403CV | 1475 | 1.2081
187 | 133 | WINFREE | 342WN | 361 | 1.205
188 | 45 | WINSHIRE | 241WS | 1022 | 1.2025
189 | 2 | EGYPT | 552EP | 470 | 1.2021
190 | 247 | YANKEE DOODLE | 25YAN | 176 | 1.1989
191 | 264 | DAYTON BULK | 727DY | 757 | 1.1915
192 | 138 | WYNTEX | 632WT | 865 | 1.1908
193 | 222 | SILSBEE | 463SI | 717 | 1.1897
194 | 165 | VIWAY | 681VI | 951 | 1.1882
195 | 59 | NORTH END | 21NOE | 1822 | 1.1674
196 | 177 | FRONT STREET | 310FR | 515 | 1.1612
197 | 26 | NECHES | 197NE | 145 | 1.1517
198 | 355 | CORRIGAN BULK | 239CR | 492 | 1.1423
199 | 78 | BRIARCLIFF | 31BRC | 869 | 1.1404
200 | 200 | LINCOLN | 16LCN | 338 | 1.1391
201 | 299 | MAPLE | 90MPL | 368 | 1.1304
202 | 71 | CONROE BULK | 577CN | 208 | 1.1298
203 | 174 | WEST END | 86WED | 964 | 1.1234
204 | 245 | Alden Bridge | 765AL | 744 | 1.1102
205 | 343 | SPURLOCK | 98SPU | 520 | 1.0962
206 | 319 | PANSY | 184PS | 415 | 1.094
207 | 90 | HUNTSVILLE | 611HU | 1192 | 1.0864
208 | 252 | AMELIA BULK | 182AM | 875 | 1.0709
209 | 151 | STONEGATE | 93STG | 1658 | 1.0663
210 | 185 | TANGLEWOOD | 134TG | 2323 | 1.0486
211 | 244 | GOSLIN | 709GL | 3595 | 1.035
212 | 287 | ECHO | 73ECH | 788 | 1.0343
213 | 128 | GROVES-EGSI | 63GRO | 1363 | 1.0242
214 | 360 | NORTH END | 27NOE | 162 | 1.0185
215 | 271 | PEE DEE | 806PD | 1339 | 1.0112
216 | 76 | KOLBS | 35KOL | 1105 | 1.0009
217 | 223 | Alden Bridge | 767AL | 2390 | 0.99791
218 | #N/A | JOHNSTOWN | 343JT | 1488 | 0.97849
219 | 127 | TAMINA | 599TA | 395 | 0.97722
220 | 186 | DAISETTA | 744DA | 761 | 0.97635
221 | 118 | KOUNTZE BULK | 432KT | 824 | 0.93689
222 | 237 | DOBBIN | 519DO | 2069 | 0.91832
223 | 183 | NEW CANEY | 336NC | 3576 | 0.91499
224 | 266 | ADAMS BAYOU | 330AD | 144 | 0.90972
225 | 77 | KICKAPOO | 251KP | 1265 | 0.88854
226 | 374 | TRAVIS | 9TRV | 26 | 0.88462
227 | 280 | CRYSTAL | 567CR | 1234 | 0.88169
228 | 337 | PARKDALE | 171PR | 680 | 0.86324
229 | 339 | CORDREY | 321CO | 55 | 0.85455
230 | 275 | FORT WORTH | 7FTW | 1332 | 0.84384
231 | 191 | CONAIR | 514CN | 1939 | 0.84167
232 | 228 | MCHALE | 112MC | 658 | 0.82371
233 | 132 | TANGLEWOOD | 137TG | 1528 | 0.8161
234 | 117 | FLETCHER | 457FL | 1447 | 0.81548
235 | 24 | BRIDGE CITY | 363BD | 1933 | 0.8148
236 | 39 | MCDONALD | 479MD | 955 | 0.80942
237 | 34 | CORDREY | 324CO | 1532 | 0.80744
238 | 178 | NEW CANEY | 304NC | 1222 | 0.80115
239 | 176 | PANORAMA | 525PA | 1315 | 0.79544
240 | 295 | CROCKETT | 64CRK | 1094 | 0.78519
241 | 143 | LOEB | 18LOB | 552 | 0.77174
242 | 145 | APRIL | 590AP | 1505 | 0.7515
243 | 209 | VIDOR | 162VD | 1828 | 0.74945
244 | 215 | CORDREY | 326CO | 1139 | 0.74627
245 | 156 | MCLEWIS | 380MC | 2245 | 0.74031
246 | 293 | SHEAWILL | 535SH | 661 | 0.73374
247 | 248 | LAKEVIEW | 81LAV | 1272 | 0.73192
248 | 94 | NORTH SILSBEE | 472NS | 307 | 0.7101
249 | 95 | CLEVELAND | 404CV | 1669 | 0.70701
250 | 277 | VIRGINIA | 129VI | 630 | 0.7
251 | 272 | ORANGE | 350ON | 869 | 0.69735
252 | 18 | TAMINA | 316TA | 316 | 0.6962
253 | 370 | ROSEDALE | 150RS | 98 | 0.69388
254 | 16 | WINFREE | 341WN | 693 | 0.68543
255 | 289 | STOWELL | 231ST | 903 | 0.6711
256 | 169 | BRIDGE CITY | 361BD | 1072 | 0.66791
257 | 274 | CROCKETT | 60CRK | 217 | 0.65899
258 | 31 | LILLARD | 490LI | 299 | 0.65552
259 | 199 | LUMBERTON | 441LU | 3597 | 0.65026
260 | 263 | ROSEDALE | 152RS | 558 | 0.62724
261 | 17 | HARDIN | 35HDN | 753 | 0.62417
262 | 136 | CORDREY | 325CO | 1349 | 0.6212
263 | 273 | GEORGIA | 670GE | 324 | 0.62037
264 | 268 | CONAIR | 511CN | 1454 | 0.61761
265 | 167 | MCDONALD | 476MD | 1003 | 0.60518
266 | 164 | ELIZABETH | 122EL | 975 | 0.59282
267 | 210 | LACON | 538LA | 1239 | 0.59241
268 | 43 | GRIMES | 982GR | 698 | 0.58739
269 | 353 | WESTSIDE | 112WS | 423 | 0.58629
270 | 83 | MCLEWIS | 381MC | 1151 | 0.58384
271 | 161 | VIDOR | 161VD | 611 | 0.57774
272 | 22 | OAK RIDGE | 745OK | 233 | 0.55365
273 | 60 | FLETCHER | 456FL | 808 | 0.54208
274 | 135 | PORT ACRES SUB | 69PTA | 459 | 0.52288
275 | 47 | ORANGE | 352ON | 928 | 0.52263
276 | 49 | MAYHAW | 671MA | 1720 | 0.51802
277 | 240 | LONGMIRE | 583LM | 1271 | 0.50354
278 | 316 | CENTRAL | 133CE | 1581 | 0.50285
279 | 106 | CONROE BULK | 507CN | 1982 | 0.49445
280 | 253 | Alden Bridge | 762AL | 3807 | 0.48647
281 | 37 | FORT WORTH | 12FTW | 1619 | 0.47498
282 | 56 | DAYTON BULK | 724DY | 2141 | 0.46427
283 | 64 | VIRGINIA | 130VI | 795 | 0.46038
284 | 130 | ECHO | 71ECH | 680 | 0.44853
285 | 203 | VIDOR | 164VD | 855 | 0.44094
286 | 195 | LINDBERGH | 43LNB | 752 | 0.43617
287 | 68 | LONGMIRE | 582LM | 815 | 0.42822
288 | 320 | SOUR LAKE | 104SL | 311 | 0.41801
289 | 257 | CHEEK | 159CH | 536 | 0.41791
290 | 276 | HUNTSVILLE | 610HU | 1872 | 0.41026
291 | 328 | LONGMIRE | 584LM | 1337 | 0.40987
292 | 313 | WEST END | 80WED | 451 | 0.40133
293 | 332 | SILSBEE | 461SI | 513 | 0.39961
294 | 97 | GOSLIN | 703GL | 1662 | 0.39591
295 | 221 | ROSEDALE | 153RS | 881 | 0.38933
296 | 345 | GOSLIN | 707GL | 708 | 0.38842
297 | 310 | GROVES-EGSI | 61GRO | 940 | 0.38723
298 | 159 | YANKEE DOODLE | 23YAN | 633 | 0.38705
299 | 166 | WEST END | 88WED | 769 | 0.38492
300 | 259 | PLANTATION | 546PL | 819 | 0.37363
301 | 48 | METRO | 716ME | 1860 | 0.37151
302 | 318 | GROVES-EGSI | 62GRO | 1505 | 0.37076
303 | 3 | NORTH SILSBEE | 471NS | 1093 | 0.37054
304 | 256 | HUNTSVILLE | 608HU | 3176 | 0.36209
305 | 326 | OAK RIDGE | 741OK | 739 | 0.35589
306 | 336 | VIRGINIA | 132VI | 609 | 0.3399
307 | 86 | WEST END | 85WED | 520 | 0.32885
308 | 150 | LONGMIRE | 581LM | 1846 | 0.30715
309 | 205 | KOUNTZE | 451KT | 1060 | 0.30472
310 | 279 | STONEGATE | 92STG | 1988 | 0.28823
311 | 344 | PORT NECHES | 45PTN | 921 | 0.28773
312 | 359 | CONROE BULK | 576CN | 898 | 0.28285
313 | 338 | GOSLIN | 705GL | 864 | 0.26852
314 | 175 | CORDREY | 320CO | 90 | 0.26667
315 | 63 | ELIZABETH | 121EL | 1149 | 0.26458
316 | 329 | MAPLE | 91MPL | 295 | 0.26441
317 | 188 | TANGLEWOOD | 136TG | 614 | 0.26059
318 | 307 | BRIDGE CITY | 360BD | 1056 | 0.25663
319 | 323 | NORTH END | 29NOE | 361 | 0.25208
320 | 312 | SOMERVILLE | 126SO | 826 | 0.24939
321 | 140 | CONROE BULK | 574CN | 1398 | 0.24821
322 | 212 | CONAIR | 516CN | 418 | 0.24641
323 | 155 | AMELIA BULK | 180AM | 1306 | 0.23507
324 | 217 | TYRRELL | 38TYR | 43 | 0.23256
325 | 179 | TANGLEWOOD | 135TG | 510 | 0.21569
326 | 347 | APRIL | 592AP | 1047 | 0.21299
327 | 376 | WEST END | 87WED | 19 | 0.21053
328 | 262 | SOMERVILLE | 127SO | 428 | 0.21028
329 | 171 | LAKEVIEW | 80LAV | 712 | 0.20365
330 | 281 | KOLBS | 37KOL | 694 | 0.20317
331 | 298 | STONEGATE | 90STG | 1030 | 0.19612
332 | 290 | MCHALE | 110MC | 993 | 0.16818
333 | 116 | CONROE BULK | 505CN | 826 | 0.16102
334 | 363 | Alden Bridge | 764AL | 1433 | 0.15352
335 | 230 | CROCKETT | 198CR | 213 | 0.12676
336 | 342 | TESCO | 36TSC | 81 | 0.12346
337 | 305 | METRO | 718ME | 867 | 0.11419
338 | 292 | BRIARCLIFF | 33BRC | 303 | 0.10891
339 | 112 | ADAMS BAYOU | 331AD | 213 | 0.10798
340 | 331 | FRONT STREET | 308FR | 379 | 0.10554
341 | 302 | JIROU | 76JRU | 199 | 0.1005
342 | 213 | WYNTEX | 633WT | 562 | 0.092527
343 | 108 | GOSLIN | 706GL | 1458 | 0.078189
344 | 192 | DAISETTA | 741DA | 160 | 0.075
345 | 306 | CROCKETT | 63CRK | 29 | 0.068966
346 | 311 | METRO | 723ME | 415 | 0.06747
347 | 375 | WEST END | 83WED | 408 | 0.063725
348 | 361 | MEMORIAL | 280ML | 325 | 0.058462
349 | 352 | JIROU | 77JRU | 345 | 0.057971
350 | 187 | LINDBERGH | 41LNB | 308 | 0.055195
351 | 335 | GOSLIN | 704GL | 1674 | 0.054958
352 | 297 | CONROE BULK | 506CN | 2096 | 0.054866
353 | 189 | SPURLOCK | 99SPU | 613 | 0.053834
354 | 348 | WEST END | 82WED | 353 | 0.048159
355 | 207 | CONROE BULK | 575CN | 598 | 0.038462
356 | 371 | TRAVIS | 13TRV | 31 | 0.032258
357 | 296 | NORTH END | 28NOE | 206 | 0.029126
358 | 327 | WESTSIDE | 111WS | 427 | 0.028103
359 | 314 | BROOKS CREEK | 270BC | 45 | 0.022222
360 | 346 | GOSLIN | 710GL | 857 | 0.0070012
361 | 32 | HEARNE | 29HRN | 322 | 0.0031056
362 | 220 | TRAVIS | 11TRV | 20 | 0
363 | #N/A | SUN WARREN | 139SN | 10 | 0
364 | 372 | Travis | 14TRV | 14 | 0
365 | 219 | NORTH END | 26NOE | 340 | 0
366 | 357 | MEMORIAL | 281ML | 22 | 0
367 | #N/A | JOHNSTOWN | 342JT | 561 | 0
368 | #N/A | Conair | 573CN | 10 | 0
369 | 270 | CEDAR | 698CE | 26 | 0
370 | 373 | TRAVIS | 6TRV | 28 | 0
371 | 113 | SOUTH LIBERTY | 714SL | 126 | 0
372 | 367 | METRO | 717ME | 125 | 0
373 | 351 | Metro | 720ME | 493 | 0
374 | 368 | Metro | 721ME | 527 | 0
375 | #N/A | West End | 81WED | 24 | 0
376 | 350 | SPEEDWAY | 917SW | 27 | 0

## Feeder-SAIDI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System |  |  |  |  | Total Number of Feeders
With More Than 10 Customers |  |  |  |  | 376
Add or Delete Rows as Necessary
Entergy Texas, Inc.
2009 SAIDI Ranking | 2008 SAIDI Ranking | Substation Identification | Feeder Identification | Number of Customers | 2009 SAIDI Value
1 | 89 | NECHES | 193NE | 1032 | 915.1676
2 | 50 | CHEEK | 166CH | 331 | 766.1782
3 | 73 | CHINA | 93CHI | 1215 | 707.7103
4 | #N/A | FORT WORTH | 567FT | 687 | 699.8981
5 | 283 | GRIMES | 981GR | 323 | 698.8111
6 | 119 | HEARNE | 25HRN | 228 | 680.2675
7 | #N/A | HIMEX | 223HI | 2416 | 620.0662
8 | 290 | STOWELL | 234ST | 141 | 593.9645
9 | 5 | PEE DEE | 809PD | 1552 | 566.7874
10 | 366 | HEARNE | 28HRN | 26 | 545.6538
11 | 184 | CRYSTAL | 566CR | 1419 | 545.062
12 | 64 | RIVTRIN | 269RV | 2920 | 544.4675
13 | 307 | HANKS | 24HKS | 840 | 543.3595
14 | 214 | OAK RIDGE | 742OK | 2442 | 518.3726
15 | 55 | SPLENDORA | 309SP | 1206 | 513.1857
16 | 94 | BAYSHORE | 213BA | 1605 | 494.5196
17 | 321 | HIMEX | 222HI | 172 | 479.2558
18 | #N/A | JOHNSTOWN | 544JT | 2360 | 466.7042
19 | 4 | CLEVELAND | 425CV | 1948 | 462.0241
20 | 9 | TRANSCO | 48TCO | 178 | 461.4551
21 | 183 | OAK RIDGE | 743OK | 1659 | 456.8535
22 | 128 | APOLLO | 321AP | 848 | 454.4151
23 | 104 | CALVERT | 6CAL | 1588 | 435.9219
24 | 304 | CROWDER | 104CD | 1573 | 433.7241
25 | 145 | CLEVELAND | 406CV | 1441 | 418.8536
26 | 91 | WARREN | 506WR | 1380 | 414.3536
27 | 331 | FEDERAL | 801FE | 222 | 411.8964
28 | 56 | CHINA | 92CHI | 594 | 405.8519
29 | 133 | HANKAMER | 207HA | 702 | 403.141
30 | 10 | DOUCETTE | 569DC | 184 | 395.5652
31 | 21 | LOVELLS LAKE | 141LV | 717 | 393.8466
32 | 204 | SILSBEE | 463SI | 717 | 387.6123
33 | 32 | CLEVELAND | 426CV | 2840 | 382.394
34 | 134 | PEE DEE | 808PD | 1913 | 381.3607
35 | 53 | STOWELL | 232ST | 1044 | 379.9684
36 | 168 | APOLLO | 320AP | 1417 | 375.9781
37 | 225 | CONAIR | 513CN | 1364 | 371.4553
38 | 357 | WESTSIDE | 112WS | 423 | 348.7045
39 | 54 | NEW CANEY | 337NC | 544 | 348.068
40 | 286 | HIMEX | 221HI | 102 | 345.1078
41 | 191 | NAVASOTA | 901NA | 336 | 339.6994
42 | 7 | CRYSTAL | 570CR | 749 | 334.5808
43 | 216 | MCHALE | 112MC | 658 | 332.1003
44 | 23 | SPLENDORA | 307SP | 1606 | 328.7603
45 | 78 | ADAMS BAYOU | 332AD | 596 | 321.255
46 | 106 | NAVASOTA | 905NA | 2271 | 316.7028
47 | 109 | CORRIGAN BULK | 238CR | 590 | 311.0068
48 | 230 | MCDONALD | 478MD | 614 | 308.9577
49 | 365 | GOSLIN | 701GL | 1157 | 307.1694
50 | 339 | BAYOU FANNETT | 250BY | 33 | 299.5152
51 | 85 | WARREN | 592WR | 2042 | 298.3301
52 | 143 | BAYSHORE | 212BA | 42 | 297.9762
53 | 44 | DOBBIN | 920DO | 1538 | 296.4083
54 | 62 | WINFREE | 340WN | 1026 | 290.9903
55 | 205 | ROSEDALE | 151RS | 1102 | 285.3249
56 | 188 | HAMPTON | 158HA | 1101 | 284.5431
57 | 103 | CLEVELAND | 405CV | 1697 | 284.3854
58 | 98 | HANKS | 25HKS | 899 | 282.564
59 | 121 | HUNTSVILLE | 600HU | 1775 | 275.8242
60 | 72 | WALDEN | 564WD | 5320 | 271.6173
61 | 67 | HICKORY RIDGE | 341HI | 1503 | 270.6693
62 | 141 | ELIZABETH | 120EL | 1347 | 266.804
63 | 79 | MCDONALD | 477MD | 1324 | 265.1601
64 | 144 | DAISETTA | 743DA | 335 | 264.9701
65 | #N/A | JOHNSTOWN | 345JT | 1004 | 264.0827
66 | 101 | TAMINA | 317TA | 1081 | 263.1887
67 | 41 | BATSON | 53BAT | 861 | 262.8269
68 | 152 | SPLENDORA | 308SP | 2276 | 262.7663
69 | 42 | LACON | 537LA | 1785 | 261.9613
70 | 160 | LINDBERGH | 40LNB | 1152 | 259.9679
71 | #N/A | NECHES | 197NE | 145 | 259.0414
72 | 92 | LONGMIRE | 580LM | 1429 | 258.6046
73 | 27 | CONROE BULK | 572CN | 1277 | 254.7565
74 | 122 | LOVELLS LAKE | 142LV | 318 | 254.0409
75 | 47 | NEW CANEY | 334NC | 4628 | 252.842
76 | 112 | HANKAMER | 206HA | 580 | 246.9259
77 | 59 | WALDEN | 563WD | 1633 | 245.0741
78 | 45 | NEW CANEY | 333NC | 5598 | 244.7251
79 | 26 | TEMCO | 628TE | 349 | 244.7077
80 | 31 | DAYTON BULK | 725DY | 1211 | 243.1643
81 | 374 | TRAVIS | 9TRV | 26 | 241.8846
82 | 186 | EGYPT | 550EP | 2143 | 241.56
83 | 288 | PORT ACRES SUB | 67PTA | 577 | 239.6534
84 | 251 | HUMPHREY | 108HM | 37 | 238.5405
85 | 22 | DOUCETTE | 570DC | 1099 | 238.3103
86 | 198 | CROWDER | 105CD | 885 | 235.3424
87 | 35 | CHEEK | 160CH | 1198 | 234.4115
88 | 65 | WINSHIRE | 240WS | 1087 | 232.6762
89 | 20 | BEVIL | 155BE | 3524 | 232.5009
90 | 212 | KOLBS | 36KOL | 1265 | 218.4759
91 | 237 | CROCKETT | 195CR | 1293 | 216.2019
92 | 118 | LACON | 539LA | 1118 | 215.4991
93 | 210 | SILSBEE | 462SI | 757 | 214.9089
94 | 86 | LINDBERGH | 42LNB | 1700 | 214.1076
95 | 151 | MCHALE | 113MC | 626 | 213.0927
96 | 193 | DAYTON BULK | 726DY | 1472 | 212.1753
97 | 172 | FRONT STREET | 307FR | 492 | 211.376
98 | 200 | YANKEE DOODLE | 22YAN | 2381 | 211.142
99 | 107 | TEMCO | 627TE | 1007 | 210.5422
100 | 340 | YANKEE DOODLE | 24YAN | 336 | 209.9613
101 | 322 | CENTRAL | 131CE | 940 | 205.483
102 | 135 | MCLEWIS | 382MC | 736 | 204.3139
103 | 161 | BAYSHORE | 211BA | 964 | 202.8288
104 | 302 | CLEVELAND | 403CV | 1475 | 201.0231
105 | 146 | SOUR LAKE | 105SL | 1208 | 198.1896
106 | 281 | PEE DEE | 806PD | 1339 | 197.885
107 | 43 | VIDOR | 163VD | 2906 | 197.5933
108 | 364 | Alden Bridge | 769AL | 1007 | 196.9692
109 | 49 | BEVIL | 156BE | 665 | 194.7564
110 | 74 | CALVERT | 4CAL | 2122 | 194.59
111 | 51 | CROCKETT | 61CRK | 104 | 191.0865
112 | 245 | TAMINA | 598TA | 704 | 190.0028
113 | 315 | OAK RIDGE | 740OK | 1256 | 183.7436
114 | 139 | MANCHESTER | 67MAN | 1004 | 182.5149
115 | 215 | HANKS | 22HKS | 1153 | 181.9922
116 | 250 | JIROU | 78JRU | 406 | 181.5099
117 | 241 | YANKEE DOODLE | 25YAN | 176 | 178.6477
118 | 178 | STOWELL | 233ST | 501 | 177.3353
119 | #N/A | FORT WORTH | 99FTW | 160 | 176.3562
120 | 88 | DOUCETTE | 568DC | 491 | 176.279
121 | 174 | PORT ACRES SUB | 68PTA | 1139 | 175.986
122 | 14 | NEW CANEY | 335NC | 1588 | 175.7204
123 | 61 | EASTGATE | 781EG | 1113 | 175.6649
124 | 105 | MANCHESTER | 66MAN | 1931 | 174.2346
125 | 24 | TAMINA | 316TA | 316 | 173.481
126 | 81 | BRIARCLIFF | 32BRC | 1296 | 173.4745
127 | 254 | ELIZABETH | 123EL | 2381 | 172.7677
128 | 68 | OILLA | 345OI | 1263 | 170.1188
129 | 207 | DAYTON BULK | 723DY | 898 | 169.3552
130 | 278 | GEORGIA | 670GE | 324 | 167.5926
131 | 147 | PORT ACRES BULK | 70PAS | 787 | 167.2948
132 | 306 | PANSY | 184PS | 415 | 167.1181
133 | 201 | PORT NECHES | 46PTN | 1259 | 166.8872
134 | 48 | RAYWOOD | 74RAY | 1131 | 165.7462
135 | 176 | PANSY | 185PS | 625 | 164.2336
136 | 108 | RAYWOOD | 73RAY | 500 | 161.592
137 | 40 | GOSLIN | 708GL | 2204 | 160.7155
138 | 58 | NORTH END | 21NOE | 1822 | 160.0143
139 | 257 | PLANTATION | 545PL | 1044 | 157.7318
140 | 318 | NAVASOTA | 969NA | 812 | 157.1786
141 | 333 | LINCOLN | 15LCN | 275 | 156.9345
142 | 252 | WEST ORANGE | 393WO | 732 | 153.7186
143 | 213 | GOSLIN | 702GL | 1715 | 153.6163
144 | 182 | GROVES-EGSI | 59GRO | 1673 | 153.1751
145 | 13 | RIVTRIN | 268RV | 2517 | 151.089
146 | 239 | KOLBS | 34KOL | 1221 | 150.9779
147 | 221 | ORANGE | 351ON | 380 | 149.5184
148 | 236 | CHEEK | 165CH | 103 | 149.3786
149 | 33 | SHEAWILL | 536SH | 1176 | 149.2874
150 | 8 | MAGNOLIA AMES | 711MG | 786 | 148.8333
151 | 69 | NAVASOTA | 904NA | 1213 | 147.967
152 | 63 | CALDWELL INDUSTRIAL | 138CI | 676 | 144.4719
153 | 361 | Alden Bridge | 768AL | 3072 | 143.7308
154 | 258 | OAK RIDGE | 744OK | 2429 | 142.0963
155 | 202 | AMELIA BULK | 182AM | 875 | 140.1406
156 | 256 | FORT WORTH | 7FTW | 1332 | 138.9474
157 | 177 | LOEB | 17LOB | 861 | 138.3566
158 | 345 | SPURLOCK | 98SPU | 520 | 138.0135
159 | 316 | CROCKETT | 65CRK | 504 | 137.8988
160 | 154 | GROVES-EGSI | 63GRO | 1363 | 137.1739
161 | 303 | CONAIR | 515CN | 2068 | 136.8665
162 | 39 | GRIMES | 883GR | 831 | 135.3622
163 | 223 | DAISETTA | 744DA | 761 | 135.1261
164 | 271 | Alden Bridge | 767AL | 2390 | 135.0527
165 | 218 | Alden Bridge | 766AL | 1637 | 135.0348
166 | 277 | CRYSTAL | 567CR | 1234 | 134.607
167 | 342 | MCHALE | 111MC | 572 | 134.5157
168 | 328 | HUMPHREY | 106HM | 1110 | 134.4117
169 | 158 | DOBBIN | 519DO | 2069 | 133.4766
170 | 52 | KOUNTZE BULK | 435KT | 47 | 131.9362
171 | 351 | WESTSIDE | 113WS | 311 | 131.5177
172 | 238 | CROWDER | 103CD | 1386 | 127.8449
173 | 354 | CENTRAL | 130CE | 687 | 125.7205
174 | 261 | PLANTATION | 546PL | 819 | 124.4347
175 | 324 | WALDEN | 560WD | 625 | 123.1328
176 | 80 | LACON | 540LA | 1479 | 119.973
177 | 233 | BEVIL | 154BE | 2166 | 119.0679
178 | 140 | LOEB | 18LOB | 552 | 118.9475
179 | 228 | HUNTSVILLE | 607HU | 3321 | 117.741
180 | 253 | VIRGINIA | 129VI | 630 | 117.1937
181 | 248 | CONAIR | 514CN | 1939 | 116.5498
182 | 199 | WYNTEX | 634WT | 1218 | 116.2233
183 | 266 | CORDREY | 327CO | 1023 | 114.653
184 | 124 | KICKAPOO | 251KP | 1265 | 113.487
185 | 127 | STONEGATE | 91STG | 1251 | 111.2038
186 | 175 | TAMINA | 599TA | 395 | 110.0861
187 | 219 | LAKEVIEW | 81LAV | 1272 | 109.5385
188 | 29 | SARATOGA | 761SA | 422 | 107.6161
189 | 229 | ECHO | 70ECH | 1504 | 107.518
190 | 284 | BRIDGE CITY | 362BD | 1264 | 106.8544
191 | 350 | APRIL | 591AP | 1502 | 105.4361
192 | 2 | EGYPT | 552EP | 470 | 105.2574
193 | 148 | CENTRAL | 132CE | 1751 | 103.3198
194 | 84 | GOREE | 681GR | 794 | 102.0743
195 | 159 | NEW CANEY | 336NC | 3576 | 101.7889
196 | 327 | PARKDALE | 171PR | 680 | 101.4294
197 | 117 | HUNTSVILLE | 611HU | 1192 | 98.3859
198 | 76 | Alden Bridge | 763AL | 2073 | 97.6966
199 | 244 | BRIARCLIFF | 30BRC | 2345 | 97.6751
200 | 19 | BRIDGE CITY | 363BD | 1933 | 97.1568
201 | 247 | TYRRELL | 37TYR | 508 | 95.8504
202 | 287 | WOODVILLE | 594WD | 1203 | 95.8146
203 | 369 | METRO | 722ME | 845 | 95.7467
204 | 211 | GOSLIN | 709GL | 3595 | 95.6929
205 | 162 | GOREE | 682GR | 1046 | 94.0163
206 | 99 | FRONT STREET | 310FR | 515 | 93.5922
207 | 83 | BRIARCLIFF | 31BRC | 869 | 90.9816
208 | 294 | CROCKETT | 64CRK | 1094 | 89.3519
209 | 224 | ADAMS BAYOU | 330AD | 144 | 88.3958
210 | 164 | TANGLEWOOD | 134TG | 2323 | 87.1386
211 | 295 | GROVES-EGSI | 61GRO | 940 | 86.6926
212 | 272 | MAPLE | 90MPL | 368 | 85.9891
213 | 197 | LINCOLN | 16LCN | 338 | 85.787
214 | 157 | WINSHIRE | 241WS | 1022 | 83.2456
215 | 243 | DAYTON BULK | 727DY | 757 | 83.1664
216 | 15 | KOUNTZE BULK | 432KT | 824 | 83.0716
217 | 100 | WEST END | 86WED | 964 | 82.8174
218 | 60 | CLEVELAND | 404CV | 1669 | 81.0947
219 | 36 | LILLARD | 490LI | 299 | 80.0167
220 | 87 | GRIMES | 982GR | 698 | 78.3166
221 | 131 | ELIZABETH | 122EL | 975 | 77.9364
222 | 163 | VIDOR | 162VD | 1828 | 77.837
223 | 102 | VIRGINIA | 131VI | 1402 | 75.9351
224 | 165 | HUMPHREY | 107HM | 1962 | 75.6075
225 | 125 | CONAIR | 512CN | 1238 | 74.9063
226 | 181 | VIWAY | 682VI | 1829 | 73.8956
227 | 93 | WINFREE | 342WN | 361 | 73.554
228 | 235 | APRIL | 590AP | 1505 | 73.3774
229 | 270 | AMELIA BULK | 181AM | 1663 | 72.6584
230 | 123 | NORTH SILSBEE | 472NS | 307 | 72.3127
231 | 187 | Alden Bridge | 765AL | 744 | 71.9731
232 | 129 | DAYTON BULK | 724DY | 2141 | 71.8104
233 | #N/A | JOHNSTOWN | 343JT | 1488 | 70.1915
234 | 185 | TANGLEWOOD | 137TG | 1528 | 69.4234
235 | 150 | CHEEK | 159CH | 536 | 69.166
236 | 170 | MCDONALD | 476MD | 1003 | 69.0808
237 | 25 | MCDONALD | 479MD | 955 | 68.1194
238 | 16 | CONROE BULK | 577CN | 208 | 67.9231
239 | 347 | CORRIGAN BULK | 239CR | 492 | 67.3537
240 | 149 | PANORAMA | 525PA | 1315 | 66.7802
241 | 227 | VIDOR | 164VD | 855 | 66.7088
242 | 300 | JIROU | 75JRU | 66 | 66.1667
243 | 308 | STOWELL | 231ST | 903 | 65.9967
244 | 203 | WYNTEX | 632WT | 865 | 65.0532
245 | 138 | VIRGINIA | 130VI | 795 | 63.3849
246 | 113 | AMELIA BULK | 180AM | 1306 | 63.3499
247 | 259 | Alden Bridge | 762AL | 3807 | 62.6953
248 | 111 | PORT ACRES SUB | 69PTA | 459 | 60.3224
249 | 116 | NEW CANEY | 304NC | 1222 | 59.7103
250 | 190 | MCLEWIS | 380MC | 2245 | 59.5216
251 | 153 | FLETCHER | 457FL | 1447 | 59.1824
252 | 11 | FLETCHER | 456FL | 808 | 58.6696
253 | 232 | VIWAY | 681VI | 951 | 57.6141
254 | 209 | CROCKETT | 60CRK | 217 | 56.8433
255 | 279 | SHEAWILL | 535SH | 661 | 56.7716
256 | 173 | LUMBERTON | 441LU | 3597 | 56.4665
257 | 192 | WOODVILLE | 593WD | 729 | 56.2702
258 | 3 | WINFREE | 341WN | 693 | 55.9553
259 | 310 | ECHO | 73ECH | 788 | 55.5406
260 | 276 | CONAIR | 511CN | 1454 | 52.8989
261 | 265 | LONGMIRE | 581LM | 1846 | 52.6029
262 | 130 | MAYHAW | 671MA | 1720 | 52.2483
263 | 222 | LONGMIRE | 583LM | 1271 | 52.2046
264 | 299 | ORANGE | 350ON | 869 | 52.0863
265 | 194 | CORDREY | 325CO | 1349 | 51.9726
266 | 273 | HUNTSVILLE | 610HU | 1872 | 51.5059
267 | 293 | PARKDALE | 176PR | 532 | 51.2011
268 | 126 | CORDREY | 324CO | 1532 | 51.1619
269 | 34 | FORT WORTH | 12FTW | 1619 | 50.1013
270 | 260 | ECHO | 72ECH | 506 | 49.5217
271 | 136 | CONROE BULK | 507CN | 1982 | 49.0499
272 | 28 | HARDIN | 35HDN | 753 | 48.8911
273 | 274 | LINDBERGH | 43LNB | 752 | 48.7008
274 | 338 | WEST ORANGE | 392WO | 664 | 47.9864
275 | 362 | NORTH END | 27NOE | 162 | 47.4074
276 | 220 | BRIDGE CITY | 361BD | 1072 | 47.2584
277 | 268 | WEST END | 88WED | 769 | 47.2276
278 | 155 | ROSEDALE | 153RS | 881 | 46.6901
279 | 12 | LONGMIRE | 582LM | 815 | 46.5951
280 | 334 | VIRGINIA | 132VI | 609 | 46.1757
281 | 66 | HANKS | 23HKS | 1288 | 45.8657
282 | 344 | GOSLIN | 707GL | 708 | 44.7684
283 | 234 | ROSEDALE | 152RS | 558 | 44.2903
284 | 301 | SOUR LAKE | 104SL | 311 | 44.119
285 | 46 | OAK RIDGE | 745OK | 233 | 43.5064
286 | 120 | GOSLIN | 703GL | 1662 | 42.5945
287 | 195 | LACON | 538LA | 1239 | 41.6134
288 | 314 | CENTRAL | 133CE | 1581 | 40.9633
289 | 330 | GOSLIN | 705GL | 864 | 40.3079
290 | 335 | APRIL | 592AP | 1047 | 40.3066
291 | 370 | ROSEDALE | 150RS | 98 | 39.449
292 | 282 | CROWDER | 102CD | 2225 | 38.8364
293 | 97 | MCLEWIS | 381MC | 1151 | 38.6003
294 | 208 | YANKEE DOODLE | 23YAN | 633 | 37.7062
295 | 82 | METRO | 719ME | 1434 | 37.5251
296 | 142 | ELIZABETH | 121EL | 1149 | 37.2811
297 | 285 | STONEGATE | 90STG | 1030 | 37.0534
298 | 6 | NORTH SILSBEE | 471NS | 1093 | 36.5764
299 | 115 | CONROE BULK | 574CN | 1398 | 36.0122
300 | 96 | KOLBS | 35KOL | 1105 | 35.6172
301 | 77 | WEST END | 85WED | 520 | 35.3923
302 | 180 | CORDREY | 326CO | 1139 | 34.9526
303 | 313 | GROVES-EGSI | 62GRO | 1505 | 33.0126
304 | 57 | METRO | 716ME | 1860 | 32.714
305 | 156 | KOUNTZE | 451KT | 1060 | 32.1123
306 | 305 | MAPLE | 91MPL | 295 | 31.3797
307 | 341 | PORT NECHES | 45PTN | 921 | 31.3029
308 | 263 | TANGLEWOOD | 135TG | 510 | 31.149
309 | 269 | STONEGATE | 92STG | 1988 | 31.0644
310 | 311 | OAK RIDGE | 741OK | 739 | 29.9783
311 | 189 | VIDOR | 161VD | 611 | 29.8576
312 | 336 | SILSBEE | 461SI | 513 | 29.4288
313 | 255 | HUNTSVILLE | 608HU | 3176 | 28.9713
314 | 226 | ECHO | 71ECH | 680 | 28.0353
315 | 326 | LONGMIRE | 584LM | 1337 | 27.0307
316 | 37 | ORANGE | 352ON | 928 | 26.1961
317 | 346 | NORTH END | 29NOE | 361 | 25.1053
318 | 90 | TANGLEWOOD | 136TG | 614 | 24.443
319 | 292 | SOMERVILLE | 127SO | 428 | 24.1472
320 | 291 | MCHALE | 110MC | 993 | 24.0262
321 | 231 | WEST END | 80WED | 451 | 23.9911
322 | 171 | LAKEVIEW | 80LAV | 712 | 21.9298
323 | 246 | CORDREY | 320CO | 90 | 21.4778
324 | 359 | CONROE BULK | 576CN | 898 | 20.52
325 | 319 | METRO | 718ME | 867 | 20.2826
326 | 169 | STONEGATE | 93STG | 1658 | 20.146
327 | 349 | CORDREY | 321CO | 55 | 18.8
328 | 206 | CONAIR | 516CN | 418 | 18.2081
329 | 320 | SOMERVILLE | 126SO | 826 | 17.6804
330 | 337 | TESCO | 36TSC | 81 | 16.3704
331 | 363 | Alden Bridge | 764AL | 1433 | 15.7676
332 | 298 | BRIDGE CITY | 360BD | 1056 | 15.6998
333 | 262 | TYRRELL | 38TYR | 43 | 14.8837
334 | 167 | CONROE BULK | 505CN | 826 | 10.7022
335 | 217 | ADAMS BAYOU | 331AD | 213 | 10.662
336 | 196 | BRIARCLIFF | 33BRC | 303 | 10.4356
337 | 289 | KOLBS | 37KOL | 694 | 10.3127
338 | 376 | WEST END | 87WED | 19 | 10.1053
339 | 297 | SPURLOCK | 99SPU | 613 | 9.8564
340 | 249 | CROCKETT | 198CR | 213 | 9.7183
341 | 329 | FRONT STREET | 308FR | 379 | 8.5646
342 | 264 | CONROE BULK | 506CN | 2096 | 8.2347
343 | 242 | LINDBERGH | 41LNB | 308 | 8.013
344 | 240 | DAISETTA | 741DA | 160 | 7.9688
345 | 137 | GOSLIN | 706GL | 1458 | 7.594
346 | 309 | GOSLIN | 704GL | 1674 | 7.1511
347 | 353 | WEST END | 82WED | 353 | 6.0397
348 | 375 | WEST END | 83WED | 408 | 5.8211
349 | 343 | NORTH END | 28NOE | 206 | 5.3786
350 | 312 | JIROU | 76JRU | 199 | 5.1658
351 | 275 | CROCKETT | 63CRK | 29 | 3.931
352 | 323 | WESTSIDE | 111WS | 427 | 3.3162
353 | 179 | WYNTEX | 633WT | 562 | 2.7384
354 | 371 | TRAVIS | 13TRV | 31 | 2.6774
355 | 296 | BROOKS CREEK | 270BC | 45 | 2.3778
356 | 360 | MEMORIAL | 280ML | 325 | 2.2246
357 | 317 | METRO | 723ME | 415 | 2.1928
358 | 280 | CONROE BULK | 575CN | 598 | 1.8445
359 | 348 | GOSLIN | 710GL | 857 | 1.2742
360 | 358 | JIROU | 77JRU | 345 | 1.0029
361 | 17 | HEARNE | 29HRN | 322 | 0.26398
362 | 355 | SPEEDWAY | 917SW | 27 | 0
363 | #N/A | West End | 81WED | 24 | 0
364 | 368 | Metro | 721ME | 527 | 0
365 | 352 | Metro | 720ME | 493 | 0
366 | 367 | METRO | 717ME | 125 | 0
367 | 114 | SOUTH LIBERTY | 714SL | 126 | 0
368 | 373 | TRAVIS | 6TRV | 28 | 0
369 | 267 | CEDAR | 698CE | 26 | 0
370 | #N/A | Conair | 573CN | 10 | 0
371 | #N/A | JOHNSTOWN | 342JT | 561 | 0
372 | 356 | MEMORIAL | 281ML | 22 | 0
373 | 332 | NORTH END | 26NOE | 340 | 0
374 | 372 | Travis | 14TRV | 14 | 0
375 | #N/A | SUN WARREN | 139SN | 10 | 0
376 | 325 | TRAVIS | 11TRV | 20 | 0

## Causes
Entergy Texas, Inc.
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
2009 Reporting Year
| Causes of Forced Interruptions |  | Percentage
|  | Weather (Including Lightning) | 16.9%
|  | Vegetation | 18.81%
|  | Animals and Birds | 3.978%
|  | People (Including cars and farm equip) | 14.74%
|  | Utility-owned Equipment | 32.34%
|  | Other | 6.706%
|  | Unknown | 6.527%
100%