Public Utility Commission 
of Texas

Texas Technical Reference Manual

Version 8.0

Volume 3: Nonresidential Measures

Program Year 2021

Last Revision Date:

October 2020

Table of Contents

1.	Introduction	12

2.	Nonresidential Measures	13

2.1	Nonresidential: Lighting	13

2.1.1	Lamps and Fixtures Measure Overview	13

2.1.2	Lighting Controls Measure Overview	48

2.1.3	Light Emitting Diode (LED) Traffic Signals Measure Overview	53

2.2	Nonresidential: HVAC	58

2.2.1	Air Conditioner or Heat Pump Tune-ups Measure Overview	58

2.2.2	Split System/Single Packaged Air Conditioners and Heat Pumps Measure Overview	64

2.2.3	HVAC Chillers Measure Overview	87

2.2.4	Packaged Terminal Air Conditioners, Heat Pumps, and Room Air Conditioners Measure Overview	104

2.2.5	HVAC Variable Frequency Drive (VFD) Measure Overview	116

2.2.6	Condenser Air Evaporative Pre-Cooling Measure Overview	129

2.2.7	Computer Room Air Conditioners Measure Overview	138

2.2.8	High-Volume Low-Speed (HVLS) Fans Measure Overview	144

2.2.9	Computer Room Air Handler (CRAH) Motor Efficiency Measure Overview	149

2.3	Nonresidential: Building Envelope	153

2.3.1	Cool Roofs Measure Overview	153

2.3.2	Window Treatments Measure Overview	165

2.3.3	Entrance and Exit Door Air Infiltration	169

2.4	Nonresidential: Food Service Equipment	177

2.4.1	ENERGY STAR® Combination Ovens Measure Overview	177

2.4.2	ENERGY STAR® Electric Convection Ovens Measure Overview	183

2.4.3	ENERGY STAR® Commercial Dishwashers Measure Overview	188

2.4.4	ENERGY STAR® Hot Food Holding Cabinets Measure Overview	195

2.4.5	ENERGY STAR® Electric Fryers Measure Overview	199

2.4.6	Pre-Rinse Spray Valves Measure Overview	204

2.4.7	ENERGY STAR® Electric Steam Cookers Measure Overview	208

2.4.8	Demand Controlled Kitchen Ventilation	213

2.4.9	Commercial Ice Makers Measure Overview	219

2.4.10	Vacuum-Sealing & Packaging Machines Measure Overview	224

2.5	Nonresidential: Refrigeration	227

2.5.1	Door Heater Controls Measure Overview	227

2.5.2	ECM Evaporator Fan Motors Measure Overview	234

2.5.3	Electronic Defrost Controls Measure Overview	240

2.5.4	Evaporator Fan Controls Measure Overview	244

2.5.5	Night Covers for Open Refrigerated Display Cases Measure Overview	247

2.5.6	Solid and Glass Door Reach-Ins Measure Overview	254

2.5.7	Strip Curtains for Walk-In Refrigerated Storage Measure Overview	259

2.5.8	Zero-Energy Doors for Refrigerated Cases Measure Overview	261

2.5.9	Door Gaskets for Walk-In and Reach-In Coolers and Freezers	267

2.6	Nonresidential: Miscellaneous	272

2.6.1	Vending Machine Controls Measure Overview	272

2.6.2	Lodging Guest Room Occupancy Sensor Controls Measure Overview	275

2.6.3	Pump-Off Controllers Measure Overview	280

2.6.4	ENERGY STAR® Pool Pumps Measure Overview	285

2.6.5	Computer Power Management Measure Overview	292

2.6.6	Premium Efficiency Motors Measure Overview	298

2.6.7	Central Domestic Hot Water (DHW) Controls Measure Overview	313

2.6.8	High Speed Doors for Cold Storage	319

2.6.9	Showerhead Temperature Sensitive Restrictor Valves Measure Overview	325

2.6.10	Tub Spout and Showerhead Temperature Sensitive Restrictor Valves Measure Overview 	331

2.6.11	ENERGY STAR® Electric Vehicle Supply Equipment (EVSE)	339

2.6.12	ENERGY STAR® Electric Vehicle Supply Equipment (EVSE)	344

APPENDIX A:	Measure Life Calculations for Dual Baseline Measures	349

List of Figures

Figure 1: Non-Qualifying LED Process for Lighting Projects	17

Figure 2: Building Type Decision Making	40

Figure 3: Comparison of Projected Annual Energy Savings to Cooling Degree Days for All 16 California Climate Zones for Reach-in Display Cases (Coolers)	269

Figure 4: Comparison of Projected Annual Energy Savings to Cooling Degree Days for All 16 California Climate Zones for Reach-in Display Cases (Freezers)	269

Figure 5: Survival Function for Premium Efficiency Motors	306

Figure 6: Showerhead TSRVs – Shower, Bath, and Sink Hot Water Use Profile	329

Figure 7: Tub Spout/Showerhead TSRVs – Shower, Bath, and Sink Hot Water Use Profile	337

List of Tables

Table 1: Adjusted Baseline Wattages for T12 Equipment	19

Table 2: EISA 2007 Baseline Adjustment for GSILs	20

Table 3: New Construction LPDs for Interior Space Types by Building Type	25

Table 4: New Construction LPDs for Exterior Space Types	26

Table 5: New Construction Baseline Wattages for Athletic Field/Court LEDs	26

Table 6: Commercial Lighting Building Type Descriptions and Examples	29

Table 7: Operating Hours by Building Type	34

Table 8: Summer Peak Coincidence Factors by Building Type	36

Table 9: Winter Peak Coincidence Factors by Building Type	38

Table 10: Deemed Energy and Demand Interactive HVAC Factors	41

Table 11: Midstream Assumptions by Lamp Type	42

Table 12: Permitted Baseline Wattage by Reflector Lamp Type and Diameter,	43

Table 13: Lighting Controls Definitions	50

Table 14: Lighting Controls Energy and Power Adjustment Factors	50

Table 15: Federal Standard Maximum Wattages and Nominal Wattages	54

Table 16: Incandescent and LED Traffic Signal Savings Assumptions	55

Table 17: LED Traffic Signal Deemed Savings per Fixture	56

Table 18: Incandescent and LED Traffic Signal EULs by Fixture Type	56

Table 19: Default EER and HSPF per Size Category	59

Table 20: ER Baseline Full-load Efficiency for ACs	66

Table 21: ER Baseline Part-load Efficiency for ACs	66

Table 22: ER Baseline Full-load Cooling Efficiency for HPs	67

Table 23: ER Baseline Part-load Cooling Efficiency for HPs	67

Table 24: ER Baseline Heating Efficiency for HPs	67

Table 25: Baseline Efficiency Levels for ROB and NC Air Conditioners and Heat Pumps	69

Table 26: Commercial HVAC Building Type Descriptions and Examples	73

Table 27: Commercial HVAC Floor Area and Floor Assumptions by Building Type	76

Table 28: DF and EFLH Values for Amarillo (Climate Zone 1)	77

Table 29: DF and EFLH Values for Dallas (Climate Zone 2)	78

Table 30: DF and EFLH Values for Houston (Climate Zone 3)	79

Table 31: DF and EFLH Values for Corpus Christi (Climate Zone 4)	80

Table 32: DF and EFLH Values for El Paso (Climate Zone 5)	81

Table 33: Remaining Useful Life Early Retirement Systems	83

Table 34: ER Baseline Full-load Efficiency of All Path A Air-cooled Chillers	88

Table 35: ER Baseline Full-load Efficiency of All Path B Air-cooled Chillers	89

Table 36: ER Baseline Part-load Efficiency (IPLV) of All Path A Air-cooled Chillers	89

Table 37: ER Baseline Part-load Efficiency (IPLV) of All Path B Air-cooled Chillers	89

Table 38: ER Baseline Full-load Efficiency of Centrifugal Path A Water-cooled Chillers	90

Table 39: ER Baseline Full-load Efficiency of Centrifugal Path B Water-cooled Chillers	90

Table 40: ER Baseline Part-load Efficiency (IPLV) of Centrifugal Path A Water-cooled Chillers	90

Table 41: ER Baseline Part-load Efficiency (IPLV) of Centrifugal Path B Water-cooled Chillers	91

Table 42: ER Baseline Full-load Efficiency of Screw/Scroll/Recip. Path A Water-cooled Chillers	91

Table 43: ER Baseline Full-load Efficiency of Screw/Scroll/Recip. Path B Water-cooled Chillers	91

Table 44: ER Baseline Part-load Efficiency (IPLV) of Screw/Scroll/Recip. Path A Water-cooled Chillers	92

Table 45: ER Baseline Part-load Efficiency (IPLV) of Screw/Scroll/Recip. Path B Water-cooled Chillers	92

Table 46: Baseline Efficiencies for ROB and NC Air-cooled and Water-cooled Chillers	93

Table 47: DF and EFLH for Amarillo (Climate Zone 1)	96

Table 48: DF and EFLH for Dallas (Climate Zone 2)	97

Table 49: DF and EFLH for Houston (Climate Zone 3)	97

Table 50: DF and EFLH for Corpus Christi (Climate Zone 4)	98

Table 51: DF and EFLH for El Paso (Climate Zone 5)	98

Table 52: Remaining Useful Life of Early Retirement Systems	99

Table 53: ER Baseline Efficiency Levels for Standard Size PTAC/PTHP Units	105

Table 54: Minimum Efficiency Levels for PTAC/PTHP ROB and NC Units,	105

Table 55: Minimum Efficiency Levels for Room Air Conditioners ROB and NC Units	106

Table 56: PTAC/PTHP or RAC Equipment: DF and EFLH Values for Amarillo (CZ 1)	109

Table 57: PTAC/PTHP or RAC Equipment: DF and EFLH Values for Dallas (CZ 2)	109

Table 58: PTAC/PTHP or RAC Equipment: DF and EFLH Values for Houston (CZ 3)	110

Table 59: PTAC/PTHP or RAC Equipment: DF and EFLH Values for Corpus Christi (CZ 4)	110

Table 60: PTAC/PTHP or RAC Equipment: DF and EFLH Values for El Paso (CZ 5)	111

Table 61: Remaining Useful Life of ER PTAC/PTHP Systems,	112

Table 62: AHU Supply Fan VFD %CFM Inputs	117

Table 63: Chilled Water Pump VFD %CFM Inputs	118

Table 64: Hot Water Pump VFD %CFM Inputs	119

Table 65: Yearly Motor Operation Hours by Building Type	122

Table 66: AHU Supply Fan Outlet Damper Baseline Savings per Motor HP	123

Table 67: AHU Supply Fan Inlet Damper Baseline Savings per Motor HP	124

Table 68: AHU Supply Fan Inlet Guide Vane Baseline Savings per Motor HP	124

Table 69: AHU Supply Fan No Control Baseline Savings per Motor HP	125

Table 70: Chilled Water Pump Savings per Motor HP	125

Table 71: Hot Water Pump Savings per Motor HP	126

Table 72: Average Weather during Peak Conditions	129

Table 73: DRF and EFLH Reduction Values for Amarillo (Climate Zone 1)	131

Table 74: DRF and EFLH Reduction Values for Fort Worth (Climate Zone 2)	132

Table 75: DRF and EFLH Reduction Values for Houston (Climate Zone 3)	133

Table 76: DRF and EFLH Reduction Values for Corpus Christi (Climate Zone 4)	134

Table 77: DRF and EFLH Reduction Values for El Paso (Climate Zone 5)	135

Table 78: Baseline Efficiency Levels for ROB and NC CRACs	138

Table 79: Commercial CRAC Building Type Descriptions and Examples	140

Table 80: DF and EFLH Values for All Climate Zones	140

Table 81: Hours of Circulating Fan Operation by Barn Type	146

Table 82. Cool Roofs – Assumed Cooling and Heating Efficiencies (COP)	154

Table 83. Cool Roofs – ENERGY STAR® Specification	154

Table 84. Cool Roofs – Estimated R-value based on Year of Construction	155

Table 85. Cool Roofs – Savings Factors for Amarillo (Climate Zone 1)	155

Table 86. Cool Roofs – Savings Factors for Dallas (Climate Zone 2)	157

Table 87. Cool Roofs – Savings Factors for Houston (Climate Zone 3)	158

Table 88. Cool Roofs – Savings Factors for Corpus Christi (Climate Zone 4)	160

Table 89. Cool Roofs – Savings Factors for El Paso (Climate Zone 5)	161

Table 90: Window Treatments – Solar Heat Gain Factors	166

Table 91: Window Treatments – Recommended Clear Glass SHGCpre by Window Thickness	166

Table 92: Window Treatments – Recommended COP by HVAC System Type	166

Table 93: Average Monthly Ambient Temperatures (°F)	171

Table 94: Daytime and Nighttime Design Temperatures	171

Table 95: Deemed Cooling Energy Savings per Linear Foot of Weather Stripping/Door Sweep	173

Table 96: Deemed ER Heating Energy Savings per Linear Foot of Weather Stripping/Door Sweep	174

Table 97: Deemed HP Heating Energy Savings per Linear Foot of Weather Stripping/Door Sweep	174

Table 98: Deemed Summer Demand Savings per Linear Foot of Weather Stripping/Door Sweep	174

Table 99: Deemed ER Winter Demand Savings per Linear Foot of Weather Stripping/Door Sweep	174

Table 100: Deemed HP Winter Demand Savings per Linear Foot of Weather Stripping/Door Sweep	175

Table 101: Cooking Energy Efficiency and Idle Energy Rate Requirements	177

Table 102: Deemed Variables for Energy and Demand Savings Calculations	179

Table 103: Deemed Energy and Demand Savings Values	179

Table 104: Convection Oven Cooking Energy Efficiency and Idle Energy Requirements	183

Table 105: Deemed Variables for Energy and Demand Savings Calculations	184

Table 106: Deemed Energy and Demand Savings Values	185

Table 107: Nonresidential ENERGY STAR® Commercial Dishwashers Descriptions	188

Table 108: High-efficiency Requirements for Commercial Dishwashers	189

Table 109: Deemed Variables for Energy and Demand Savings Calculations	191

Table 110: Deemed Energy and Peak Demand Savings Values by Dishwasher	192

Table 111: Equipment Lifetime per Dishwasher Category	192

Table 112: Maximum Idle Energy Rate Requirements ENERGY STAR® Qualification	195

Table 113: Deemed Variables for Energy and Demand Savings Calculations	196

Table 114: Deemed Energy and Demand Savings Values by HFHC Size	196

Table 115: High-efficiency Requirements for Electric Fryers	199

Table 116: Deemed Variables for Energy and Demand Savings Calculations	201

Table 117: Deemed Energy and Demand Savings Values by Fryer Type	201

Table 118: Pre-rinse Spray Valve Flow Rate Limits	203

Table 119: Assumed Variables for Energy and Demand Savings Calculations	205

Table 120: ENERGY STAR® Energy Efficiency and Idle Rate Requirements for Electric Steam Cookers	208

Table 121: Deemed Variables for Energy and Demand Savings Calculations	210

Table 122: Annual Energy Consumption and Daily Food Cooked	210

Table 123: Demand Controlled Kitchen Ventilation – Default Assumptions	214

Table 124: Demand Controlled Kitchen Ventilation – Population-Adjusted Interactive HVAC Savings per hp	214

Table 125: Demand Controlled Kitchen Ventilation – Probability Weighted Peak Load Share	215

Table 126: Demand Controlled Kitchen Ventilation – Deemed Annual Energy Savings per horsepower	215

Table 127: Demand Controlled Kitchen Ventilation – Deemed Summer and Winter Peak Demand Savings per horsepower	216

Table 128: Ice Maker Baseline Efficiency	219

Table 129: ENERGY STAR® Criteria - Automatic Ice Makers	220

Table 130: Probability-weighted Peak Load Share - Ice Makers	221

Table 131: Vacuum-sealing & Packaging Machines – Deemed Energy and Demand Savings	224

Table 132: Coefficients by Climate Zone	230

Table 133: Deemed Energy and Demand Savings Values by Location and Refrigeration Temperature	231

Table 134: Deemed Variables for Energy and Demand Savings Calculations	236

Table 135: Motor Sizes, Efficiencies, and Input Watts	237

Table 136: Compressor Coefficient of Performance Based on Climate and Refrigeration Type (COPcooler or COPfreezer)	237

Table 137: Deemed Variables for Energy and Demand Savings Calculations	241

Table 138: Deemed Variables for Energy and Demand Savings Calculations	244

Table 139: Summer Design Dry Bulb Temperatures by Climate Zone 	248

Table 140: Modeled Deemed Savings for Night Covers for Texas (per Linear Foot)	251

Table 141: Baseline Energy Consumption,	254

Table 142: Efficient Energy Consumption Requirements	254

Table 143: Deemed Energy and Demand Savings	256

Table 144: Deemed Energy and Demand Savings for Freezers and Coolers	259

Table 145: Coefficients by Climate Zone	263

Table 146: Deemed Energy and Demand Savings Values by Climate Zone and Refrigeration Temperature	265

Table 147: Energy Savings Achievable for New Gaskets Replacing Baseline Gaskets of Various Efficacies (per Linear Foot of Installed Door Gasket)	267

Table 148: Energy Savings Achievable for New Gaskets Replacing Baseline Gaskets of Various Efficacies (per Linear Foot of Installed Door Gasket)	269

Table 149: Deemed Energy and Demand Savings per Linear Foot of Installed Door Gasket	270

Table 150: Vending Machine Controls – Refrigerated Cold Drink Unit Deemed Savings	272

Table 151: Vending Machine Controls – Refrigerated Reach-in Unit Deemed Savings	272

Table 152: Vending Machine Controls – Non-refrigerated Snack Unit Deemed Savings	273

Table 153: Deemed Energy and Demand Savings for Motel per Guest Room, by Region	276

Table 154: Deemed Energy and Demand Savings for Hotel per Guest Room, by Region	276

Table 155: Deemed Energy and Demand Savings for Dormitories per Room, by Region	277

Table 156: Deemed Variables for Energy and Demand Savings Calculations	281

Table 157: NEMA Premium Efficiency Motor Efficiencies	282

Table 158: Conventional Pool Pumps Assumptions	286

Table 159: ENERGY STAR® Pool Pumps Assumptions	287

Table 160: Demand Factors	287

Table 161: ENERGY STAR® Variable Speed Pool Pump Energy Savings	288

Table 162: ENERGY STAR® Variable Speed Pool Pump Summer Demand Savings	288

Table 163: ENERGY STAR® Variable Speed Pool Pump Winter Demand Savings	289

Table 164: ENERGY STAR® Variable Speed Pool Pump Claimed Demand Savings	289

Table 165: Computer Power Management - Equipment Wattages	293

Table 166: Computer Power Management – Operating Hours	293

Table 167: Computer Power Management – Probability Weighted Peak Load Share, All Activity Types	293

Table 168: Computer Power Management - Deemed Energy Savings Values, All Climate Zones	294

Table 169: Computer Power Management - Deemed Demand Savings Values, Office or School	295

Table 170: Premium Efficiency Motors – HVAC Assumptions by Building Type	301

Table 171: Premium Efficiency Motors – Industrial Assumptions by Building Type	302

Table 172: Rewound Motor Efficiency Reduction Factors	302

Table 173: Premium Efficiency Motors – New Construction and Replace-on-Burnout Baseline Efficiencies by Motor Size409,	303

Table 174: Remaining Useful Life (RUL) of Replaced Motor	304

Table 175: Premium Efficiency Motors – Early Retirement Baseline Efficiencies by Motor Size for 1-200 hp Motors Manufactured Prior to December 19, 2010	309

Table 176: Premium Efficiency Motors – Early Retirement Baseline Efficiencies by Motor Size for 250-500 hp Motors Manufactured Prior to June 1, 2016	309

Table 177: Central DHW Controls - Probability Weighted Peak Load Share	313

Table 178: Central DHW Controls - Reference kWh by Water Heater and Building Type	314

Table 179: Central DHW Controls - HDD Adjustment Factors	314

Table 180: Central DHW Controls – Annual kWh Circulation Pump Savings	315

Table 181: Central DHW Controls - Annual kWh Thermal Distribution Savings per Dwelling Unit	315

Table 182: Central DHW Controls - Peak Demand kW Circulation Pump Savings	315

Table 183: Central DHW Controls - Peak Demand kW Thermal Savings per Dwelling Unit	316

Table 184: High Speed Doors – Energy Factors for Door to Unconditioned Area	320

Table 185: High Speed Doors – Energy Factors for Door to Conditioned Area	321

Table 186: High Speed Doors – Summer and Winter Demand Factors for Door to Conditioned Area	321

Table 187: High Speed Doors – Summer Demand Factors for Door to Unconditioned Area	321

Table 188: High Speed Doors – Winter Demand Factors for Door to Unconditioned Area	321

Table 189: High Speed Doors – qsA, Sensible Heat Load of Infiltration Air	321

Table 190: High Speed Doors – Rs, Sensible Heat Ratio of Infiltration Air	322

Table 191: Showerhead TSRVs – Hot Water Usage Reduction	326

Table 192: Showerhead TSRVs – Water Mains Temperatures	328

Table 193: Showerhead TSRVs – Peak Coincidence Factors	328

Table 194: Tub Spout/Showerhead TSRVs – Hot Water Usage Reduction	333

Table 195: Tub Spout/Showerhead TSRVs – Water Mains Temperatures	335

Table 196: Tub Spout/Showerhead TSRVs – Peak Coincidence Factors	335

Table 197: EVSE Peak Demand Probability Factors	340

Table 198: EVSE Annual Energy Savings	340

Table 199: EVSE Peak Demand Savings	341

Table 200: EVSE Peak Demand Probability Factors	345

Table 201: EVSE Annual Energy Savings	345

Table 202: EVSE Peak Demand Savings	346

Acknowledgments

The Technical Reference Manual is maintained by the Public Utility Commission of Texas’ independent Evaluation, Measurement, and Verification (EM&V) team led by Tetra Tech. This version of the Texas Technical Reference Manual (TRM) was primarily developed from program documentation and measure savings calculators used by the Texas Electric Utilities and their Energy Efficiency Services Providers (EESPs) to support their energy efficiency efforts, and original source material from petitions filed with the Public Utility Commission of Texas by the utilities, their consultants, and EESPs, such as Frontier Energy (TXu 1-904-705), ICF, CLEAResult, and Nexant. Portions of the Technical Reference Manual are copyrighted 2001-2017 by the Electric Utility Marketing Managers of Texas (EUMMOT), while other portions are copyrighted 2001-2018 by Frontier Energy. Certain technical content and updates were added by the EM&V team to provide further explanation and direction as well as a consistent structure and level of information.

TRM Technical Support

Technical support and questions can be emailed to the EM&V project manager (lark.lee@tetratech.com) and PUCT staff (therese.harris@puc.texas.gov).

# Introduction

This volume of the TRM contains the deemed savings for nonresidential measures that have been approved for use in Texas by the PUCT. This volume includes instructions regarding various savings calculators and reference sources of the information. The TRM serves as a centralized source of deemed savings values; where appropriate, Measurement & Verification (M&V) methods by measure category are noted for informational purposes only regarding the basis of projected and claimed savings.

Table 1-1 provides an overview of the nonresidential measures contained within Volume 3 and the types of deemed savings estimates available for each one. There are four types of deemed savings estimates identified:

- Point estimates that provide a single deemed savings value that correspond to a single measure or type of technology.

- Deemed saving tables that provide energy and peak savings as a function of size, capacity; building type, efficiency level, or other inputs.

- Savings algorithms that require user defined inputs that must be gathered on site and the identification of default inputs where primary data could not be collected. In many cases, these algorithms are provided as references to deemed savings tables, point estimates, or calculator explanations.

- Calculators are used by different utilities and implementers to calculate energy savings for different measures. In many cases, there are several different calculators available for a single measure. Sometimes their background calculators are similar, and in other cases, estimates can vary greatly between each calculator.

- M&V methods are also used for some measures to calculate savings in the event that standard equipment is not used, or the specified building types do not apply. For some of these measures, both a simplified M&V approach and a full M&V approach may be allowed by the utility. M&V methods as a source of claimed and projected savings are noted for informational purposes only. Standardized M&V approaches that have been reviewed by the EM&V team are incorporated into Volume 4: Measurement & Verification Protocols of this TRM.

Please consult Volume I: Overview and User Guide, Section 4: Structure and Content, for details on the organization of the measure templates presented in this volume.

Table 1: Nonresidential Deemed Savings by Measure Category

| Measure Category |  | Measure Description | Point Estimates | Deemed Savings Tables | Savings Algorithm | Calculator | M&V | 8.0 Update |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Lighting |  | Lighting: Lamps and Fixtures | -- | -- | X | X | X | General reference checks and text edits. Updated EUL for new construction projects to apply to whole project. Updated dusk-to-dawn operating hours. Minor formula corrections. Updated DLC references to refer to v3.0 or later rather than explicit versions. Removed 10% nonqualified fixture threshold. Established lumens/watt assumptions for new construction baselines. |
|  |  | Lighting Controls | -- | -- | X | X | X | General reference checks and text edits. |
|  |  | LED Traffic Signals | -- | -- | X | X | X | General reference checks and text edits. |
| HVAC HVAC |  | AC Tune-up | -- | -- | X | -- | X | General reference checks and text edits. |
|  |  | Package and Split-System (AC and Heat Pumps) | -- | -- | X | X | X | General reference checks and text edits. Clarified use of post capacity for ROB baselines. Verify M&V plan requirement for VRF and documentation requirements. Added unknown age defaults for early retirement. |
|  |  | Chillers | -- | -- | X | X | X | General reference checks and text edits. Clarified use of post capacity for ROB baselines. Added unknown age defaults for early retirement.. |
|  |  | Package Terminal Units and Room Air Conditioners (AC and Heat Pumps) | -- | -- | X | X | X | General reference checks and text edits. Clarified use of post capacity for ROB baselines. Added unknown age defaults for early retirement. |
|  |  | Variable Frequency Drives | -- | X | X | -- | -- | General reference checks and text edits. Added motor efficiency default assumptions. |
|  |  | Condenser Air Evaporative Pre-cooling | -- | -- | X | -- | X | General reference checks and text edits. |
|  |  | Computer Room Air Conditioners | -- | -- | X | X | -- | General reference checks and text edits. Removed text referring to building types other than data centers. |
|  |  | High-volume Low-speed Fans | -- | -- | X | -- | -- | General reference checks and text edits. |
|  |  | Computer Room Air Handler Motor Efficiency | -- | -- | X | X | -- | TRM v8.0 origin. |
| Building Envelope |  | ENERGY STAR® Roofs | X | -- | X | X | -- | General reference checks and text edits. Removed EStar qualification requirement and defers to meeting criteria. |
|  |  | Window Treatments | X | -- | X | X | -- | General reference checks and text edits. Updated peak demand values for climate zones and PDPF values. |
|  |  | Entrance and Exit Door Air Infiltration | -- | X | X | -- | -- | General reference checks and text edits. Degradation factor added to deemed savings values..Guidance clarified for measuring gap sizes. |
| Food Service |  | ENERGY STAR® Combination Ovens Measure Overview | -- | X | X | -- | -- | General reference checks and text edits. Removed EStar qualification requirement and defers to meeting criteria. |
|  |  | ENERGY STAR® Electric Convection Ovens | -- | X | X | -- | -- | General reference checks and text edits. Removed EStar qualification requirement and defers to meeting criteria. |
|  |  | ENERGY STAR® Commercial Dishwashers | -- | X | X | -- | -- | General reference checks and text edits. Removed EStar qualification requirement and defers to meeting criteria. |
|  |  | ENERGY STAR® Commercial Electric Hot Food Holding Cabinets | -- | X | X | -- | -- | General reference checks and text edits. Removed EStar qualification requirement and defers to meeting criteria. |
|  |  | ENERGY STAR® Kitchen Electric Fryers | -- | X | X | -- | -- | General reference checks and text edits. Removed EStar qualification requirement and defers to meeting criteria. |
|  |  | Pre-rinse Spray Valves | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | ENERGY STAR® Electric Steam Cookers | -- | X | X | -- | -- | General reference checks and text edits. Removed EStar qualification requirement and defers to meeting criteria. |
|  |  | Demand Controlled Kitchen Ventilation | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | Commercial Ice Makers | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | Vacuum-Sealing and Packaging Machines | -- | X | -- | -- | -- | TRM v8.0 origin |
| Refrigeration |  | Door Heater Controls | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | ECM Evaporator Fan Motors | -- | -- | X | -- | -- | General reference checks and text edits. |
|  |  | Electronic Defrost Control | -- | -- | X | -- | -- | General reference checks and text edits. |
|  |  | Evaporator Fan Controls | -- | -- | X | -- | -- | General reference checks and text edits. |
|  |  | Night Covers for Open Refrigerated Cases | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | High-efficiency Solid and Glass Door Reach-in Cases | -- | -- | X | -- | -- | General reference checks and text edits. |
|  |  | Strip Curtains for Walk-in Cooler/ Freezer | -- | X | -- | -- | -- | General reference checks and text edits. |
|  |  | Zero Energy Glass Doors | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | Door Gaskets for Walk-in and Reach-in Coolers and Freezers | -- | X | X | -- | -- | General reference checks and text edits. |
| Miscellaneous |  | Vending Machine Controllers | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | Lodging Guest Room Occupancy Sensor Control | -- | X | -- | -- | -- | General reference checks and text edits. |
|  |  | Pump-Off Controller | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | ENERGY STAR® Pool Pumps | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | Computer Power Management | -- | X | X | -- | -- | General reference checks and text edits. Incorporated version 2 baseline adjustments and revised savings. |
|  |  | Premium Efficiency Motors | -- | -- | X | -- | -- | General reference checks and text edits. Replace-on-burnout and Early Retirement clarifications. |
|  |  | Central DHW Controls | -- | X | X | -- | -- | General reference checks and text edits. |
|  |  | Showerhead Temperature Sensitive Restrictor Valves | -- | -- | X | -- | -- | TRM v8.0 origin. |
|  |  | Tub Spout and Showerhead Temperature Sensitivie Restrictor Valves | -- | -- | X | -- | -- | TRM v8.0 origin. |
|  |  | ENERGY STAR® Electric Vehicle Supply Equipment | -- | X | X | -- | -- | TRM v8.0 origin. |

# Nonresidential Measures

## Nonresidential: Lighting

### Lamps and Fixtures Measure Overview

TRM Measure ID: NR-LT-LF

Market Sector: Commercial

Measure Category: Lighting

Applicable Building Types: All commercial, multifamily common areas

Fuels Affected: Electricity (interactive HVAC effects: electric/gas space heating)

Decision/Action Types: Retrofit, new construction

Program Delivery Type: Prescriptive, custom, direct install

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This section provides estimates of the energy and peak savings resulting from the installation of energy efficient lamps and/or ballasts. The installation can be the result of new construction or the replacement of existing lamps and/or ballasts. This TRM Measure ID covers the following lighting technologies:

- Linear fluorescent T5s; high performance or reduced watt T8s. Linear fluorescent measures may also involve delamping with or without the use of reflectors.

- Fluorescent electrodeless induction lamps and fixtures

- Compact fluorescent lamp (CFL) screw-based lamps and hard-wired pin-based fixtures

- Pulse-start (PSMH) and ceramic metal halide (CMH) lamps; high-intensity discharge (HID) lamps

- Light emitting diode (LED) screw-based lamps; hard-wired LED fixtures.

Energy and demand savings are based on operating hours, coincident-load factors, and changes in pre-existing and post-installation lighting loads, as determined using an approved lighting Standard Fixture Wattage table (see Fixture Codes tab in the latest version of the Lighting Survey Form). The Lighting Survey Form (LSF) is one example of a calculator that is used to determine energy and demand savings. Pre- and post-retrofit lighting inventories are entered and used with the pre-loaded stipulated values and algorithms needed to calculate energy and demand savings. Components of the calculator include:

- Instructions and project information.

- Pre- and post-retrofit lighting inventories. A tab for exempt fixtures and a description of the exemptions is also present in the calculator.

- Fixture wattages and descriptions are defined in a Standard Fixture Wattage table.

- Factor tables that contain stipulated operating hours, coincidence factors, interactive HVAC factors, control adjustment factors, and new construction lighting power density factors.

- A summary tab displaying the final energy and demand calculations. The data from this tab is entered into the utility program tracking data as the claimed savings values.

Although the generic Lighting Survey Form calculator is available publicly on the Texas Energy Efficiency website, several utilities have their own versions.

##### Eligibility Criteria

This section describes the system information and certified wattage values that must be used to estimate energy and peak savings from lighting systems installed as part of the Texas utility energy efficiency programs. The fixture codes and the demand values listed in the Table of Standard Fixture Wattages are used to calculate energy and demand savings for lighting efficiency projects.

Existing lighting fixtures must be removed or demolished in place after retrofit to count towards reduced pre-install wattage.  Existing lighting fixtures that remain operable after retrofit should be listed in both the pre- and post-retrofit lighting inventory.

In addition, LED and linear fluorescent T8s need to be qualified, as follows:

- High-performance (HP) and reduced-watt (RW) T8 linear fluorescent lamps need to be qualified by the Consortium for Energy Efficiency (CEE). Their respective ballasts need to be qualified by NEMA. See the High-efficiency Condition section for additional details.

- LED lamps and fixtures must have their input power (wattage) and an L70 rated life (hours) verified through some combination of the following references: DesignLights ConsortiumTM (DLC), ENERGY STAR®, or independent lab testing (e.g., LM-79, LM-80, TM-21, ISTMT). Rated life for LED fixtures should be greater than or equal to 50,000 hours and greater than or equal to 10,000 hours for integrated-ballast LED lamps.

Exempt lighting for new construction. Some types of new construction lighting fixtures are exempt from inclusion in the interior lighting demand savings calculation, but they are still included in the total installed lighting power calculations for a project. Exempt fixtures are those that do not provide general/ambient/area lighting, have separate control devices, and are installed in one of the following applications:

- The connected power associated with the following lighting equipment is not included in calculating total connected lighting power

  - Professional sports arena playing-field lighting

  - Sleeping-unit lighting in hotels, motels, boarding houses, or similar buildings

  - Emergency lighting automatically off during normal building operation

  - Lighting in spaces specifically designed for use by occupants with special lighting needs including visual impairment and other medical and age-related issues

  - Lighting in interior spaces that have been specifically designated as a registered interior historic landmark

  - Casino gaming areas

  - Mirror lighting in dressing rooms

- Lighting equipment used for the following shall be exempt provided that it is in addition to general lighting and is controlled by an independent control device

  - Task lighting for medical and dental purposes

  - Display lighting for exhibits in galleries, museums, and monuments

- Lighting for theatrical purposes, including performance, stage, film production, and video production

- Lighting for photographic processes

- Lighting integral to equipment or instrumentation and installed by the manufacturer

- Task lighting for plant growth or maintenance

- Advertising signage or directional signage

- In restaurant building and areas, lighting for food warming or integral to food preparation equipment

- Lighting equipment that is for sale

- Lighting demonstration equipment in education facilities

- Lighting approved because of safety or emergency considerations, inclusive of exit lights

- Lighting integral to both open and glass-enclosed refrigerator and freezer cases

- Lighting in retail display windows, provided the display area is enclosed by ceiling-height partitions

- Furniture-mounted supplemental task lighting that is controlled by automatic shut off

- Exit signs

Non-qualifying LEDs. This section provides guidance to assess and calculate nonresidential lighting project savings that include non-qualifying LEDs.Figure 1 summarizes the recommended protocol for lighting system projects with non-qualifying LEDs when square footage cannot be isolated. Additional explanations and criteria for use follow.

Figure 1: Non-Qualifying LED Process for Lighting Projects

Step 1: Qualify New Construction Projects. Calculate non-qualifying LED project percentage:

- Based as a percentage of demand (percent NQwattage = wattage of non-qualifying fixtures / wattage of total fixtures)

Step 2: New Construction Projects Only. Adjust baseline wattage to account for non-qualifying fixtures.

- List non-qualifying LEDs on separate lines (e.g., separate on lighting inventory worksheet of deemed savings calculator). Non-qualifying fixtures are identified by a unique fixture code.

- Adjust code allowable baseline wattage so that non-qualifying fixture wattage is not included as part of the lighting power density (LPD) code limit requirements. To do so, calculate the sum of the qualifying fixture wattage and the sum of the total installed fixture wattage. Take the ratio of qualifying fixture wattage to total fixture wattage and multiply the resulting ratio against the total treated square footage for space. The adjusted square footage is included as part of the overall LPD calculation and will decrease the total allowable baseline wattage for the project.

- Fixture Isolation Method. If non-qualifying fixtures are isolated to a section of the building whose square footage can be easily segmented from the total building square footage, the non-qualifying fixtures and affected square footage can be excluded from the lighting inventory. Excluded fixtures must be documented when using the fixture isolation method.

Step 3: Retrofit Projects. List non-qualifying LEDs on separate lines (e.g., separate on lighting inventory worksheet of deemed savings calculator).

- Include unique identifiers/markers for the non-qualifying LEDs within the inventory (e.g., fixture code, description, or another designator within the deemed savings tool).

- Adjust non-qualifying LED wattages, so their demand and energy savings are not included as part of the project savings. Demand and energy savings for non-qualifying LEDs shall result in zero-project savings.

- Adjust non-qualifying LED quantities so they are not included as part of the project incentive. Incentives shall not be paid on non-qualifying LEDs.

- Provide clear visibility for all changes within the savings calculation (e.g., deemed savings calculator), including changes to all input assumptions and calculation methodologies to implement the above procedure.

- All other savings procedures and requirements, as specified within the TRM for lighting measures apply to all fixtures of a lighting project.

##### Baseline Condition

The baseline condition or assumed baseline efficiency used in the savings calculations depends on the decision-type used for the measure. For new construction, the baseline will be based on a lighting power density (LPD) in watts per square foot by building type, as specified by the relevant energy code/standard applied to a specific project. For retrofit applications, the baseline efficiency would typically reflect the in-situ, pre-existing equipment, with the exception of linear fluorescent T12s and first-generation T8s, as explained below. Fixture wattages used for the savings calculations are determined from the Table of Standard Fixture Wattages.

Major renovation projects should use a new construction baseline (for the building type after the improvement) if either of the following conditions are met:

- Building type changes in combination with the renovation

- Renovation scope includes removing drywall and gutting existing building to the studs

##### Linear Fluorescent T12 Special Conditions

The U.S. Energy Policy Act of 1992 (EPACT) set energy efficiency standards that preclude certain lamps and ballasts from being manufactured or imported into the U.S. The latest standards covering general service linear fluorescents went into full effect July 2014. Under this provision, almost all 4-foot and some 8-foot T12 lamps, as well as first-generation 4-foot, 700 series T8 lamps were prohibited from manufacture. Because all lighting equipment for Texas energy efficiency programs must be EPACT compliant, including existing or baseline equipment, adjustments were made to the T12 fixtures in the Standard Fixture Wattage table. Certain T12 lamp/ballast combinations which are non-EPACT compliant are assigned EPACT demand values.

As such, 4-foot and 8-foot T12s are no longer an approved baseline technology for Texas energy efficiency programs. 4-foot and 8-foot T12s are still eligible for lighting retrofit projects, but an assumed electronic T8 baseline will be used for estimating the energy and demand savings instead of the existing T12 equipment. T12 fixtures will remain in the Standard Fixture Wattage list, but the label for these records will be changed to “T12 (T8 baseline)” and the fixture wattage for these records will be adjusted to use the adjusted fixture wattages shown in Table 1.

Table 1: Adjusted Baseline Wattages for T12 Equipment

| T12 Length | Lamp Count | Revised Lamp Wattage | Revised System Wattage |
| --- | --- | --- | --- |
| 48 inch—Std, HO, and VHO (4 feet) | 1 | 32 | 31 |
|  | 2 | 32 | 58 |
|  | 3 | 32 | 85 |
|  | 4 | 32 | 112 |
|  | 6 | 32 | 170 |
|  | 8 | 32 | 224 |
| 96 inch—Std (8 feet) 60/75W | 1 | 59 | 69 |
|  | 2 | 59 | 110 |
|  | 3 | 59 | 179 |
|  | 4 | 59 | 219 |
|  | 6 | 59 | 330 |
|  | 8 | 59 | 438* |
| 96 inch-HO and VHO (8 feet) 95/110W | 1 | 86 | 101 |
|  | 2 | 86 | 160 |
|  | 3 | 86 | 261 |
|  | 4 | 86 | 319 |
|  | 6 | 86 | 481 |
|  | 8 | 86 | 638 |
| 2-foot U-Tube | 1 | 32 | 32 |
|  | 2 | 32 | 60 |
|  | 3 | 32 | 89 |
| * 8 lamp fixture wattage approximated by doubling 4 lamp fixture wattage. |  |  |  |
| Key: HO = high output, VHO—very high output. |  |  |  |

##### General Service Lamps

The baseline is assumed to be the first-tier Energy Independence and Security Act of 2007 (EISA)-mandated maximum wattage for a general service or standard incandescent or halogen lamp (see Table 2). Baseline wattages should be adjusted as EISA regulations dictate higher efficiency standards. A potential second-tier EISA baseline adjustment was scheduled to go into effect beginning January 2020. At that time, general service lamps would need to comply with a 45 lumen-per-watt efficacy standard. However, the Department of Energy (DOE) issued a definition for general service lamps on September 5, 2019, concluding that “no backstop energy conservation has been imposed.” Therefore, no additional baseline adjustment will be imposed starting in 2020. However, standard practice must also be considered in determining an appropriate baseline for this measure. To account for a rapidly changing market, measure life assumptions have been reduced as described later in this measure.

Table 2: EISA 2007 Baseline Adjustment for GSILs

| Minimum Lumens | Maximum Lumens | Incandescent Equivalent Wattage Pre-EISA 2007 | 1st Tier EISA 2007 Baseline Wattage |
| --- | --- | --- | --- |
| 310 | 749 | 40 | 29 |
| 750 | 1,049 | 60 | 43 |
| 1,050 | 1,489 | 75 | 53 |
| 1,490 | 2,600 | 100 | 72 |

##### High-efficiency Condition

Acceptable efficient fixture types are specified in the Table of Standard Fixture Wattages. In addition, some technologies such as LEDs must meet the additional requirements specified under Eligibility Criteria.

##### High-efficiency/Performance Linear Fluorescent T8s

All 4-foot T8 post-retrofit technologies and new construction projects must use electronic ballasts manufactured after November 2014, and high-performance T8 lamps that are on the T8 Replacement Lamp products list developed by the Consortium for Energy Efficiency (CEE) as published on its website.

If CEE does not have efficiency guidelines for a T8 system (such as for 8-foot, 3-foot, 2-foot, and U-bend T8 products), the product must have higher light output or reduced wattage than its standard equivalent product (minimum efficacy of 75 mean lumens per watt), while also providing a CRI (color rendering index) greater than 80 and an average rated life of 24,000 hours at three hours per start. In addition, 2-foot and 3-foot ballasts must also use electronic ballasts manufactured after November 2014.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

This section describes the deemed savings methodology for both energy and demand savings for all lighting projects. Savings are calculated using separate methods for retrofit and new construction projects.

Retrofit,

Energy Savings=kWpre×Hourspre×EAFpre-kWinstalled×Hoursinstalled×HVACenergy

Equation 1

Peak Summer Demand Savings=kWpre×CFpre×PAFpre-kWinstalled×CFinstalled×HVACdemand

Equation 2

New Construction

Energy Savings=LPD×FloorArea1000-kWinstalled×Hours×HVACenergy

Equation 3

Peak Summer Demand Savings=LPD×FloorArea1000-kWinstalled×CF×HVACdemand

Equation 4

Where:

kWpre	=	Total kW of existing measure(s) (Approved baseline fixture code wattage from deemed savings tool divided by 1000 and multiplied by fixture/lamp quantity)

kWinstalled	=	Total kW of retrofit measure(s) (Verified installed fixture code wattage from deemed savings tool divided by 1000 and multiplied by fixture/lamp quantity)

Note: wattage for installed LED fixtures may be rounded up or down to the nearest half watt; all other wattages should be rounded to the nearest watt.

LPD	=	Acceptable Lighting Power Density based on building type from efficiency codes from Table 3 [W/ft2]

Floor Area	=	Floor area of the treated space where the lights were installed

Hours	=	Hours by building type from

Table 7

EAF	=	Energy Adjustment Factor from Lighting Controls measure (set equal to 1 if no controls are installed on the existing fixture)

CF	= 	Coincidence factor by building type from

Table 8 or Table 9

PAF	=	Power Adjustment Factor from Lighting Controls measure (set equal to 1 if no controls are installed on the existing fixture)

HVACenergy	=	Energy Interactive HVAC factor by building type

HVACdemand	= 	Demand Interactive HVAC factor by building type

ISR	=	In-Service Rate, the percentage of incentivized units that are installed and in use (rather than removed, stored, or burnt out) to account for units incentivized but not operating = 1.0 unless otherwise specified for midstream applications (see Table 11)

Each of the parameters in these equations, and the approach or their stipulated values, are discussed in detail below.

Lamp and Fixture Wattages (kWpre, kWinstalled)

Existing construction: standard fixture wattage table. One example of a Table of Standard Fixture Wattages can be found in the Fixture Codes tab of the latest version of the Lighting Survey Form maintained on the Texas Energy Efficiency website. This table is used to assign identification codes and demand values (watts) to common fixture types (e.g., fluorescent, incandescent, HID, LED) used in commercial applications. The table is subdivided into lamp types (e.g., linear fluorescent, compact fluorescent, mercury vapor) with each subdivision sorted by fixture code. Each record (or row) in the table contains a fixture code, serving as a unique identifier. A legend explains the rules behind the fixture codes.

Each record also includes a description of the fixture, the number of lamps, the number of ballasts if applicable, and the fixture wattage. The table wattage values for each fixture type are averages of various manufacturers’ laboratory tests performed to ANSI test standards. By using standardized demand values for each fixture type, the Table simplifies the accounting procedures for lighting equipment retrofits. The table is updated periodically as new fixtures are added.

The fixture codes and the demand values listed in the watt/fixture column in the Table of Standard Fixture Wattages are used to calculate energy and demand savings for any lighting efficiency project.

For implementers interested in adding new fixtures to Frontier’s lighting table, a request should be submitted to Frontier. The request should include all information required to uniquely identify the fixture type and to fix its demand, as well as other contextual information needed for the table. If possible, the request should also be supported by manufacturer’s ANSI test data. Frontier periodically releases updated versions of the LSF with new fixture codes.

New construction: lighting power density table. For new construction projects, the post-retrofit lighting wattages are determined as they are for the existing construction projects, from the Standard Fixture Wattage table. However, the baseline wattage is determined from the treated floor area and a lighting power density (LPD) value, which are the allowable watts per square foot of lit floor area as specified by the relevant energy code. The applicable baseline is the code that was in effect at the time of building permit issuance. The current Commercial code for the state of Texas is IECC 2015. These values for interior space types are presented in Table 3.

In Table 4 the zones used for exterior space types are:

- Zone 1: Developed areas of national parks, state parks, forest lands, and rural areas

- Zone 2: Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited night-time use, and residential mixed-use areas

- Zone 3: All other areas

- Zone 4: High-activity commercial districts in major metropolitan areas as designated by the local land use planning authority.

Table 3: New Construction LPDs for Interior Space Types by Building Type

| Facility Type | Lighting Power Density (W/ft2) | Facility Type | Lighting Power Density (W/ft2) |
| --- | --- | --- | --- |
| Automotive facility | 0.80 | Multifamily | 0.51 |
| Convention center | 1.01 | Museum | 1.02 |
| Courthouse | 1.01 | Office | 0.82 |
| Dining: bar/lounge/leisure | 1.01 | Parking garage | 0.21 |
| Dining: cafeteria/fast food | 0.90 | Penitentiary | 0.81 |
| Dining: family | 0.95 | Performing arts | 1.39 |
| Dormitory | 0.57 | Police stations | 0.87 |
| Exercise center | 0.84 | Post office | 0.87 |
| Fire station | 0.67 | Religious buildings | 1.00 |
| Gymnasium | 0.94 | Retail | 1.26 |
| Health care/clinic | 0.90 | School/university | 0.87 |
| Hospital | 1.05 | Sports arena | 0.91 |
| Hotel/motel | 0.87 | Town hall | 0.89 |
| Library | 1.19 | Transportation | 0.70 |
| Manufacturing facility | 1.17 | Warehouse | 0.66 |
| Motion picture theater | 0.76 | Workshop | 1.19 |

The total exterior lighting power allowance for all exterior building applications is the sum of the base site allowance plus the individual allowances for areas that are to be illuminated and are permitted in Table 4.

Table 4: New Construction LPDs for Exterior Space Types

| Facility Type | Lighting Power Density (W/ft2) |  |  |  |
| --- | --- | --- | --- | --- |
|  | Zone 1 | Zone 2 | Zone 3 | Zone 4 |
| Base Site Allowance | 500 W | 600 W | 750 W | 1,300 W |
| Uncovered Parking: Parking Areas and Drives | 0.04 | 0.06 | 0.10 | 0.13 |
| Building Grounds: Walkways > 10 ft. Wide, Plaza Areas, and Special Feature Areas | 0.14 | 0.14 | 0.16 | 0.20 |
| Building Grounds: Stairways | 0.75 | 1.00 | 1.00 | 1.00 |
| Building Grounds: Pedestrian Tunnels | 0.15 | 0.15 | 0.20 | 0.30 |
| Building Grounds: Landscaping (ASHRAE 90.1-2013 only) | 0.04 | 0.05 | 0.05 | 0.05 |
| Building Entrances and Exits: Entry Canopies | 0.25 | 0.25 | 0.40 | 0.40 |
| Building Entrances, Exits, and Loading Docks: Loading Docks (ASHRAE 90.1-2013 specific) | 0.50 | 0.50 | 0.50 | 0.50 |
| Sales Canopies: Free-Standing and Attached | 0.60 | 0.60 | 0.80 | 1.00 |
| Outdoor Sales: Open Areas | 0.25 | 0.25 | 0.50 | 0.70 |
| Building Facades | -- | 0.075 | 0.113 | 0.150 |
| Entrances and Gatehouse Inspection Stations | 0.75 | 0.75 | 0.75 | 0.75 |
| Loading Areas for Emergency Vehicles | 0.50 | 0.50 | 0.50 | 0.50 |

The following default metal halide baseline wattage assumptions have been approved for exterior athletic fields and courts, which are not included in the above LPD table. These baseline wattages were derived based on a review of reported lumen range for available LED products and their reported equivalent metal halide (MH) wattage.

Table 5: New Construction Baseline Wattages for Athletic Field/Court LEDs

| Equivalent MH Wattage | # of Lamps | LED Rated Lumen Range |
| --- | --- | --- |
| 175 | 1 | < 7,500 |
| 250 | 1 | 7,500-12,499 |
| 400 | 1 | 12,500-19,999 |
| 400 | 2 | 20,000-39,999 |
| 1,000 | 1 | 40,000-59,000 |
| 1,500 | 1 | 60,000-75,000 |
| 1,000 | 2 | 75,000-99,999 |
| 1,000 | 3 | 100,000-124,999 |
| 1,000 | 4 | 125,000-149,999 |
| 1,000 | 5 | 150,000-199,999 |
| 1,000 | 6 plus 1 additional lamp for every 50,000 lumens above 200,000 (rounded down) | > 200,000 |

Operating Hours (Hours) and Coincidence Factors (CFs)

Operating hours and peak demand coincidence factors are assigned by building type, as shown in

Table 7 through Table 9. The building types used in this table are based on Commercial Buildings Energy Consumption Survey (CBECS) building types but have been modified for Texas. Refer to Volume 1, Appendix B for a description of the Texas peak demand methodology. Winter peak coincidence factors are only specified for outdoor fixtures, including for the “Parking Garage” building type.

The “Manufacturing” building type is specified with 1, 2, and 3 shift options:

- Shift 1: typical operation of 9.5-11.5 hours per day and 4-6 days per week (< 70 hours per week)

- Shift 2: typical operation of 18-20 hours per day and 5-6 days per week (70-120 hours per week)

- Shift 3: typical operation of 24 hours per day and 5-6 days per week (> 120 hours per week).

“Outdoor Dusk-to-Dawn” applies to outdoor fixtures controlled by a photocell or timer with dusk-to-dawn operation throughout the entire year. Outdoor fixtures controlled by timers with less than dusk-to-dawn operation (excluding for athletic fields and courts) may be claimed separately using the “Outdoor Less than Dusk-to-Dawn” building type or using a custom timer schedule.

These tables also include an “Other” building type, which can be used for business types that are not explicitly listed. The hours and CF values used for other are the most conservative values from the explicitly listed building types (with the exception of the CF values specified for “Education: K-12 without Summer Session” and “Lodging: Hotel/Motel/Dorm, Common Areas”, which are associated with very specific operating schedules that experience low coincidence with the summer peak period). When the Other building type is used, a description of the actual building type, the primary business activity, the business hours, and the lighting schedule must be collected for the project site and stored in the utility tracking data system.

The operating hours and coincidence factors specified in this section have been calculated at the facility level and should be applied to the entire facility. Outdoor fixtures that are not associated with the typical building lighting schedule may be claimed separately. These can include parking lot, walkway, wall pack, or another lighting, while building-mounted lighting with an operating schedule that more closely approximates the interior lighting schedule typically should not be claimed separately.

Table 6: Commercial Lighting Building Type Descriptions and Examples

| Building Type | Principal Building Activity | Definition |  | Detailed Business Type Examples |
| --- | --- | --- | --- | --- |
| Agriculture | Dairy Buildings | Buildings used to house dairy livestock and collect milk from dairy cows. |  | 1) Dairy Buildings |
|  | Grow House | Buildings used to grow herbs, fruits, or vegetables under artificial lighting. |  | 1) 24-hour Grow House 2) Non-24-hour Grow House |
| Data Center | Data Center | Buildings used to house computer systems and associated components. |  | 1) Data Center |
| Education | College/University | Buildings used for academic or technical classroom instruction, such as elementary, middle, or high schools, and classroom buildings on college or university campuses. Buildings on education campuses for which the main use is not classroom are included in the category relating to their use. For example, administration buildings are part of "Office," dormitories are "Lodging," and libraries are "Public Assembly." |  | 1) College or University 2) Career or Vocational Training 3) Adult Education |
|  | Primary School |  |  | 1) Elementary or Middle School 2) Preschool or Daycare |
|  | Secondary School |  |  | 1) High School 2) Religious Education |
| Food Sales | Convenience | Buildings used for retail or wholesale of food. |  | 1) Gas Station with a Convenience Store 2) Convenience Store |
|  | Supermarket |  |  | 1) Grocery Store or Food Market |
| Food Service | Full-service Restaurant | Buildings used for the preparation and sale of food and beverages for consumption. |  | 1) Restaurant or Cafeteria |
|  | Quick-service Restaurant |  |  | 1) Fast Food |
| Healthcare | Hospital | Buildings used as diagnostic and treatment facilities for inpatient care. |  | 1) Hospital 2) Inpatient Rehabilitation |
|  | Outpatient Healthcare | Buildings used as diagnostic and treatment facilities for outpatient care. Medical offices are included here if they use any type of diagnostic medical equipment (if they do not, they are categorized as an office building). |  | 1) Medical Office 2) Clinic or Outpatient Health Care 3) Veterinarian |
| Multifamily | Common Area | Buildings containing multifamily dwelling units, having multiple stories and equipped with elevators. |  | 1) Common Area |
| Lodging | Large Hotel | Buildings used to offer multiple accommodations for short-term or long-term residents. |  | 1) Motel or Inn 2) Hotel 3) Dormitory, Fraternity, or Sorority 4) Retirement Home, Nursing Home, Assisted Living, or other Residential Care 5) Convent or Monastery |
|  | Nursing Home |  |  |  |
|  | Small Hotel/Motel |  |  |  |
| Manufacturing | 1 Shift (<70 hr/week) | Buildings used for manufacturing/industrial applications. |  | 1) Apparel 2) Beverage, Food, and Tobacco Products 3) Chemicals 4) Computer and Electronic Products 5) Appliances and Components 6) Fabricated Metal Products 7) Furniture 8) Leather and Allied Products 9) Machinery 10) Nonmetallic Mineral Products 11) Paper 12) Petroleum and Coal Products 13) Plastics and Rubber Products 14) Primary Metals 15) Printing and Related Support 16) Textile Mills 17) Transportation Equipment 18) Wood Products |
|  | 2 Shift (70-120 hr/week) |  |  |  |
|  | 3 Shift (>120 hr/week) |  |  |  |
| Mercantile | Stand-alone Retail | Buildings used for the sale and display of goods other than food. |  | 1) Retail Store 2) Beer, Wine, or Liquor Store 3) Rental Center 4) Dealership or Showroom for Vehicles or Boats 5) Studio or Gallery |
|  | Strip Mall/Enclosed Mall | Shopping malls comprised of multiple connected establishments. |  | 1) Strip Shopping Center 2) Enclosed Malls |
| Office | Large Office | Buildings used for general office space, professional office, or administrative offices. Medical offices are included here if they do not use any type of diagnostic medical equipment (if they do, they are categorized as an outpatient health care building). |  | 1) Administrative or Professional Office 2) Government Office 3) Mixed-Use Office 4) Bank or Other Financial Institution 5) Medical Office 6) Sales Office 7) Contractor’s Office (e.g., Construction, Plumbing, HVAC) 8) Non-Profit or Social Services 9) Research and Development 10) City Hall or City Center 11) Religious Office 12) Call Center |
|  | Medium Office |  |  |  |
|  | Small Office |  |  |  |
| Parking | Parking Garage | Buildings used for parking applications. |  | No sub-categories collected. |
| Public Assembly | Public Assembly | Buildings in which people gather for social or recreational activities, whether in private or non-private meeting halls. |  | 1) Social or Meeting (e.g., Community Center, Lodge, Meeting Hall, Convention Center, Senior Center) 2) Recreation (e.g., Gymnasium, Health Club, Bowling Alley, Ice Rink, Field House, Indoor Racquet Sports) 3) Entertainment or Culture (e.g., Museum, Theater, Cinema, Sports Arena, Casino, Night Club) 4) Library 5) Funeral Home 6) Student Activities Center 7) Armory 8) Exhibition Hall 9) Broadcasting Studio 10) Transportation Terminal |
| Public Order and Safety | Jail and Prison | Government establishments engaged in justice, public order, and safety. |  | 1) Correctional Institutions 2) Prison Administration and Operation |
|  | Other |  |  | 1) Police Protection 2) Legal Counsel and Prosecution 3) Fire Protection 4) Public Order and Safety, Not Elsewhere Classified |
| Religious Worship | Religious Worship | Buildings in which people gather for religious activities (such as chapels, churches, mosques, synagogues, and temples). |  | No sub-categories collected. |
| Service | Service | Buildings in which some type of service is provided, other than food service or retail sales of goods. |  | 1) Vehicle Service or Vehicle Repair Shop 2) Vehicle Storage/Maintenance 3) Repair Shop 4) Dry Cleaner or Laundromat 5) Post Office or Postal Center 6) Car Wash 7) Gas Station with no Convenience Store 8) Photo Processing Shop 9) Beauty Parlor or Barber Shop 10) Tanning Salon 11) Copy Center or Printing Shop 12) Kennel |
| Warehouse | Warehouse | Buildings used to store goods, manufactured products, merchandise, raw materials, or personal belongings (such as self-storage). |  | 1) Refrigerated Warehouse 2) Non-refrigerated warehouse 3) Distribution or Shipping Center |
| Other | Other |  | For building types not explicitly listed. | Values used for Other are the most conservative values from the explicitly listed building types. |

Table 7: Operating Hours by Building Type

| Building Type | Operating Hours |
| --- | --- |
| Agriculture: Long-Day Lighting | 6,209 |
| Agriculture: Non-24 Hour Grow Lighting | 5,479 |
| Data Center | 4,008 |
| Education: K-12 with Summer Session, College, University, Vocational, and Day Care | 3,577 |
| Education: K-12 with Partial Summer Session | 3,177 |
| Education: K-12 without Summer Session | 2,777 |
| Food Sales: Non-24 Hour Supermarket or Convenience Store | 4,706 |
| Food Service: Full-service Restaurant | 4,368 |
| Food Service: Quick-service Restaurant | 6,188 |
| Food Service: 24 Hour Restaurant | 7,311 |
| Health Care: Inpatient | 5,730 |
| Health Care: Outpatient | 3,386 |
| Health Care: Resident Care and Nursing Home | 4,271 |
| Lodging: Hotel/Motel/Dorm, Common Area | 6,630 |
| Lodging: Hotel/Motel/Dorm, Room | 3,055 |
| Manufacturing: 1 Shift (<70 hr/week) | 2,786 |
| Manufacturing: 2 Shift (70-120 hr/week) | 5,188 |
| Manufacturing: 3 Shift (>120 hr/week) | 6,414 |
| Mercantile: Non-24 Hour Stand-alone Retail | 3,668 |
| Mercantile: Enclosed Mall | 4,813 |
| Mercantile: Strip Center and Non-Enclosed Mall | 3,965 |
| Mercantile/Food Sales: 24 Hour Stand-alone Retail, Supermarket, or Convenience Store | 6,900 |
| Multifamily: Common Area | 4,772 |
| Office | 3,737 |
| Outdoor: Athletic Field and Court | 767 |
| Outdoor: Billboard | 3,470 |
| Outdoor: Dusk-to-Dawn | 4,161 |
| Outdoor: Less than Dusk-to-Dawn | 1,998 |
| Parking Garage | 7,884 |
| Public Assembly | 2,638 |
| Public Order and Safety: Jail and Prison | 7,264 |
| Public Order and Safety: Other | 3,472 |
| Religious Worship | 1,824 |
| Service: Excluding Food | 3,406 |
| Warehouse: Non-refrigerated | 3,501 |
| Warehouse: Refrigerated | 3,798 |
| Other | 2,638 |

Table 8: Summer Peak Coincidence Factors by Building Type

| Building Type | Summer Peak CF |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Climate Zone 1 | Climate Zone 2 | Climate Zone 3 | Climate Zone 4 | Climate Zone 5 |
| Agriculture: Long-Day Lighting | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Agriculture: Non-24 Hour Grow Lighting | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Data Center | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 |
| Education: K-12 with Summer Session, College, University, Vocational, and Day Care | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Education: K-12 with partial Summer Session | 0.42 | 0.39 | 0.90 | 0.90 | 0.57 |
| Education: K-12 without Summer Session | 0.39 | 0.39 | 0.90 | 0.87 | 0.40 |
| Food Sales: Non-24 Hour Supermarket or Convenience Store | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Food Service: Full-service Restaurant | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Food Service: Quick-service Restaurant | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Food Service: 24 Hour Restaurant | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Health Care: Inpatient | 0.80 | 0.83 | 0.81 | 0.80 | 0.90 |
| Health Care: Outpatient | 0.70 | 0.75 | 0.72 | 0.71 | 0.90 |
| Health Care: Resident Care and Nursing Home | 0.70 | 0.75 | 0.72 | 0.71 | 0.90 |
| Lodging: Hotel/Motel/Dorm, Common Area | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Lodging: Hotel/Motel/Dorm, Room | 0.30 | 0.30 | 0.30 | 0.30 | 0.30 |
| Manufacturing: 1 Shift (<70 hr/week) | 0.83 | 0.84 | 0.83 | 0.85 | 0.85 |
| Manufacturing: 2 Shift (70-120 hr/week) | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 |
| Manufacturing: 3 Shift (>120 hr/week) | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 |
| Multifamily: Common Area | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Office | 0.87 | 0.88 | 0.86 | 0.90 | 0.90 |
| Outdoor: Athletic Field and Court | -- | -- | -- | -- | -- |
| Outdoor: Billboard | -- | -- | -- | -- | -- |
| Outdoor: Dusk-to-Dawn | -- | -- | -- | -- | -- |
| Outdoor: Less than Dusk-to-Dawn | -- | -- | -- | -- | -- |
| Parking Garage | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Public Assembly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 |
| Public Order and Safety: Jail and Prison | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Public Order and Safety: Other | 0.70 | 0.75 | 0.72 | 0.71 | 0.90 |
| Religious Worship | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 |
| Retail: All Non-24 Hour Retail Excluding Mall and Strip | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Retail: Enclosed Mall | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Retail: Strip Center and Non-Enclosed Mall | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Retail/Food Sales: 24 Hour Retail or Supermarket | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Service: Excluding Food | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| Warehouse: Non-refrigerated | 0.79 | 0.81 | 0.79 | 0.80 | 0.85 |
| Warehouse: Refrigerated | 0.79 | 0.81 | 0.79 | 0.80 | 0.85 |
| Other | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 |

Table 9: Winter Peak Coincidence Factors by Building Type

| Space Type | Winter Peak CF |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Climate Zone 1 | Climate Zone 2 | Climate Zone 3 | Climate Zone 4 | Climate Zone 5 |
| Outdoor: Athletic Field and Court | 0.26 | 0.27 | 0.24 | 0.29 | 0.38 |
| Outdoor: Billboards | 0.59 | 0.62 | 0.53 | 0.65 | 0.87 |
| Outdoor: Dusk-to-Dawn | 0.67 | 0.71 | 0.61 | 0.75 | 1.00 |
| Outdoor: Less than Dusk-to-Dawn | 0.67 | 0.71 | 0.61 | 0.75 | 1.00 |
| Parking Garage | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |

Lighting Calculator Building Type

This section provides additional guidance on Recommendation #1b in the 2013 Statewide Annual Portfolio Evaluation Report.

The deemed lighting hours of use (HOU) and peak summer coincidence factors (CF) for utilities to use in calculating savings associated with lighting are broken down by building type and use.  If the building type changes in combination with the retrofit, the selected building type should be consistent with the space condition after improvement. These values are provided in

Table 7 through Table 9. For the majority of the building types listed in this table, the HOU and CFs were created based on weighted averages of lighting usage across all activity areas of the building. Therefore, the deemed HOU and CFs are representative of an entire building type, across all activity areas that are in a “typical” building for this type.

The following flow chart, Figure 2, has been provided to assist utilities in understanding how they can use the deemed methods to calculate lighting savings based on HOU and CF provided in the TRM. Additionally, it provides guidance on how to treat lodging facilities and outdoor lighting projects as well as unique building types.

Figure 2: Building Type Decision Making

Lodging sites. Lodging facilities (Hotel/Motel/Dormitories) have been identified in the TRM by Common and Rooms, both with different HOU and CF. As two different values have been provided for these areas, it is acceptable for the utilities to use either or both of these building types for a single project.

Outdoor Lighting Projects that involve outdoor lighting should be claimed in a separate calculator. The exception to this is walkway lighting that is more consistent with building operation. In this application, the utilities should use the primary building type as their HOU and CFs have been rolled up into the overall building type calculations (e.g., walkway lighting between two buildings that operates during business hours).

In situations where multiple TRM building types seem plausible, or a predominant TRM building type is unclear, the utilities have two choices:

- Deemed approach. The deemed approach is a simplified method where utilities should choose a TRM building type based on the “best fit” for the facility. This is determined by the largest interior area for the potential building types. Although, if that is not best fit, the utilities will use their best judgment to make this decision and provide sufficient, defensible documentation for their decision.

- Custom approach. In more unique situations, utilities should consider projects “custom” where 1) the deemed building types in the TRM may not represent the project’s facility type, 2) the facility may represent multiple TRM building types without a clear predominant building type, or 3) the use of a predominant building type may be too conservative in the estimate of savings. The deemed methods are only applicable to specific scenarios and cannot be developed for all unique situations. Utilities should provide sufficient, defensible documentation for their HOU and CF values used in their savings calculations that can be reviewed by the EM&V team.

Interactive HVAC Factors (HVAC Energy, Demand)

Basic lighting savings are adjusted to account for the lighting system interaction with HVAC systems in conditioned or refrigerated spaces. A reduced lighting load reduces the internal heat gain to the building, which reduces the air conditioning/cooling load while increasing the heating load. Currently, the TRM only considers additional cooling savings, and the heating penalty or increase in usage is ignored.

As Table 10 shows, four conditioned space types are used for the Texas programs: single air-conditioned space type, two options for commercial refrigeration, and refrigerated warehouses: medium and low temperature. Utility procedures state that if the actual application falls between these values, the higher temperature value should be used. The final space type is unconditioned (or more explicitly uncooled as the focus is on cooling). In the lighting calculators, these values are typically assigned at the line-item level based on the conditioning type for the space in which the fixtures are located.

Table 10: Deemed Energy and Demand Interactive HVAC Factors

| Space Conditioning Type | Energy Interactive HVAC Factor | Demand Interactive HVAC Factor |
| --- | --- | --- |
| Refrigerated Air | 1.05 | 1.10 |
| Evaporative Cooling | 1.02 | 1.04 |
| Med. Temperature Refrigeration (33 to 41ºF) | 1.25 | 1.25 |
| Low Temperature Refrigeration (-10 to 10ºF) | 1.30 | 1.30 |
| None (Unconditioned/Uncooled) | 1.00 | 1.00 |

##### Midstream Lighting

This section provides guidance on calculating and allocating savings at the sector-level for midstream lighting programs. The assumptions below are to be used for midstream lighting programs’ claimed savings starting with PY2020.

An increased number of utilities are offering or planning to offer midstream lighting programs in Texas. It is important that savings are calculated and reported consistently across utilities and in agreement with industry-standard practice and the Energy Efficiency Rule 16 TAC § 25.181.

Midstream Program Assumptions

For midstream program delivery, use the following AOH and CF assumptions specified by lamp type. Assumed AOH and CF values have been weighted based on building type survey data from 2012 CBECS and 2014 MECS as well as lamp density and lamp type distribution survey data from the DOE 2015 U.S. Lighting Market Characterization (LMC).

Table 11: Midstream Assumptions by Lamp Type

| Lamp Type | AOH | Coincidence Factors |  |  |  |  | ISR |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |  |
| General Service Lamp < 100W equivalent | 1,245 | 0.15 | 0.15 | 0.16 | 0.16 | 0.13 | 0.98 |
| General Service Lamp > 100W equivalent | 3,748 | 0.69 | 0.69 | 0.73 | 0.73 | 0.71 | 0.98 |
| Pin-based Lamp | 3,744 | 0.67 | 0.67 | 0.72 | 0.72 | 0.68 | 0.98 |
| Directional/Reflector < 100W equivalent | 1,249 | 0.17 | 0.16 | 0.17 | 0.17 | 0.15 | 1.00 |
| Directional/Reflector > 100W equivalent | 3,774 | 0.78 | 0.79 | 0.78 | 0.79 | 0.82 | 1.00 |
| LED Tube | 3,522 | 0.74 | 0.75 | 0.84 | 0.84 | 0.76 | 1.00 |
| High Bay Fixture | 3,796 | 0.78 | 0.79 | 0.83 | 0.84 | 0.80 | 1.00 |
| Garage | 7,884 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Outdoor | 3,996 | 0.67 | 0.71 | 0.61 | 0.75 | 1.00 | 1.00 |

Additionally, baseline wattage for directional/reflector lamps should be calculated as follows:

Wbase=375.1-4.355D-227,800-937.9D-0.9903D2-1,479BA-12.02D×BA+14.69BA2-16,720×ln(CBCP)

Equation 5

Where:

D	=	Bulb diameter (e.g., 16 for PAR16, MR16, or MRX16)

BA	=	Beam angle (from ENERGY STAR® certification)

CBCP	=	Center beam candle power (from ENERGY STAR® certification)

Note: Round DOWN to nearest wattage from the table below:

Table 12: Permitted Baseline Wattage by Reflector Lamp Type and Diameter,

| Reflector Type | D | Permitted Wattage |
| --- | --- | --- |
| MR16 | 16 | 20, 35, 40, 45, 50, 60, 75 |
| MRX16 | 16 | 50 |
| PAR16 | 16 | 40, 45, 50, 60, 75 |
| PAR20 | 20 | 50, 75 |
| PAR30S | 30 | 40, 45, 50, 55, 60, 65, 75, 85, 90, 100, 120, 150, 250 |
| PAR30L | 30 | 20, 30, 35, 37, 40, 42, 45, 50, 65, 75 |
| PAR38 | 38 | 20, 35, 40, 45, 50, 60, 75 |

##### Deemed Energy and Demand Savings Tables

This section is not applicable as these calculations are entirely dependent on site-specific parameters related to lighting system operation.

##### Claimed Peak Demand Savings

Refer to Volume 1 for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

The estimated useful life (EUL) values are defined for the following lamp/fixture types. A separate new construction EUL has been established to account for the whole-building baseline.

- Halogen Lamps: 1.5 years

- High-intensity Discharge Lamps: 15 years

- Integrated-ballast CCFL Lamps: 4.5 years

- Integrated-ballast CFL Lamps: 2.5 years

- Integral LED Lamps: 9 years

- LED Fixtures: 15 years

- LED Corn Cob Lamps: 15 years

- LED Tubes: 15 years

- Modular CFL and CCFL Fixtures: 15 years

- T8 and T5 Linear Fluorescents: 15 years

- New Construction Interior Fixtures/Controls: 14 years

- New Construction Exterior Fixtures: 15 years

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Decision/action type: retrofit or NC

- Building or space type

- Optional: building or space funding source (state or private)

- For new construction only: light power density factor

- For new construction only: interior and/or exterior space square footage

- For new construction only: if applicable, verify if SECO compliance certification forms were filed

- Conditioned space type: cooling equipment type, refrigerated space temperature range, heating fuel type, percent heated/cooled for NC Only (specified per control)

- Baseline fixture configuration

- Baseline lamp wattage

- Baseline ballast type

- Baseline lighting controls

- Baseline counts of operating fixtures

- Baseline counts of inoperable fixtures

- Post-retrofit fixture configuration

- Post-retrofit lamp wattage

- Post-retrofit lamp specifications sheets: Post retrofit lamp product qualification information from DLC, ENERGY STAR®, or independent lab testing

- Post-retrofit ballast type

- Post-retrofit lighting controls

- Post-retrofit counts of operating fixtures

- For field adjustable light output fixtures only: isolate these fixtures by setting type and location within reported project inventories and track field adjustment settings

- For field adjustable light output fixtures only: post-retrofit lumen readings for inspection sample

- Equipment operating hours

- Lighting measure group (from ).

- For retrofit only: Proof of purchase: invoice showing model number; a photo of the model number on product packaging and installed fixture; OR an evaluator pre-approved inspection approach

- For new construction only: Proof of purchase: invoice showing model number; a photo of the model number on product packaging and installed fixture; as-built design drawings; lighting specifications package that provides detailed make and model information on installed lighting; OR an evaluator pre-approved inspection approach

- For midstream only: Qualified product list

##### Lighting Measure Groups to be Used for Measure Summary Reports

The lighting measure groups below must be used for reporting summarized savings of lighting measures. Higher-level groupings of lighting technologies, such as “Non-LED” lighting, will not provide enough resolution for evaluation and cost-effectiveness analysis. These lighting groups are consistent with the EULs defined for lighting technologies and will ensure that the correct, approved EUL can be associated with reported lighting savings.

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 36779—Describes Effective Useful Life (EUL)

- PUCT Docket 39146—Describes deemed values for energy and demand savings

- PUCT Docket 38023—Describes LED Installation and Efficiency Standards for nonresidential LED products.

##### Relevant Standards and Reference Sources

- 2015 International Energy Conservation Code. (Commercial Buildings)

- ANSI/ASHRAE/IESNA Standard 90.1-2013. Energy Standard for Buildings Except Low-Rise Residential Buildings. (Public/State buildings)

- ENERGY STAR® requirements for Commercial LED Lighting. http://www.energystar.gov/‌index.cfm?fuseaction=find_a_product.showProductGroup&pgw_code=LTG. Accessed 08/21/2017.

- Design Lights Consortium. www.designlights.org. Accessed 08/21/2017.

- Consortium for Energy Efficiency. Commercial Lighting Qualifying Products List (for 4-foot lamps). http://library.cee1.org/content/Commercial-lighting-qualifying-products-lists Accessed 02/09/2016.

- National Electrical Manufacturers Association. NEMA Premium Electronic Ballast Program. https://www.nema.org/Technical/Pages/NEMA-Premium.aspx Accessed 08/21/2017.

- U.S. Lighting Market Characterization report, September 2002, http://apps1.eere.energy.gov/‌buildings/publications/pdfs/ssl/lmc_vol1_final.pdf. Accessed 09/19/2013.

- United Illuminating Company and Connecticut Light and Power. Final Report, 2005 Coincidence Factor Study. https://library.cee1.org/content/united-illuminating-company-and-connecticut-light-power-final-report-2005-coincidence-factor. Accessed 09/19/2013.

- COMNET Appendix C—Schedules (Rev 3) https://comnet.org/appendix-c-schedules updated 07/25/2016.

### Lighting Controls Measure Overview

TRM Measure ID: NR-LT-LC

Market Sector: Commercial

Measure Category: Lighting

Applicable Building Types: All commercial, multifamily common areas

Fuels Affected: Electricity (interactive HVAC effects: electric/gas space heating)

Decision/Action Types: Retrofit, new construction

Program Delivery Type: Prescriptive, custom, direct install

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This measure promotes the installation of lighting controls in both new construction and retrofit applications. For retrofit applications, lighting controls are typically installed where there is no control other than a manual switch (wall or circuit panel). For new construction lighting systems, controls would be added where they are not already required by existing energy or building codes. Promoted technologies include occupancy sensors and daylight dimming controls. Energy and peak demand savings are calculated for these technologies with an energy adjustment factor (EAF) for kWh and a power adjustment factor (PAF) for kW.

##### Eligibility Criteria

Measures installed through utility programs must be one of the occupancy sensor, daylighting, and tuning controls that are described in Table 13.

##### Baseline Condition

The baseline condition assumes no existing or code required (for new construction) automatic lighting controls are installed on the existing lighting fixtures (i.e., they are only manually switched).

##### High-efficiency Condition

The energy-efficient condition is properly installed (not bypassed or overridden) and calibrated lighting controls that control overhead lighting in a facility based on occupancy, daylighting, or tuning sensors.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

The equations for lighting controls are similar to those used for lighting lamps and fixtures, with the addition of the EAF and PAF multipliers, as shown below. Additionally, the pre/post kW difference is replaced by a single kW value (the total fixture wattage controlled by the device).

Energy Savings= kWcontrolled×EAF×Hours×HVACenergy

Equation 6

Peak Summer Demand Savings=kWcontrolled×PAF×CF×HVACdemand

Equation 7

Where:

kWcontrolled	=	Total kW of controlled fixtures (Fixture wattage from Standard wattage table multiplied by quantity of fixtures)

Hours		=	Hours by building type from Table 7

EAF	= 	Lighting control Energy Adjustment Factor, see Table 14

PAF	= 	Lighting control Power Adjustment Factor, see Table 14

CF		= 	Coincidence factor by building type, see Table 8 or Table 9

HVACenergy	=	Energy Interactive HVAC factor by building type, see Table 10

HVACdemand	= 	Demand Interactive HVAC factor by building type, see Table 10

See Section 2.1.1 of this volume for a full explanation of the non-control variables and their corresponding values. The lighting controls EAFs and PAFs for different building types are presented in Table 14. The EAF and PAF represent the reduction in energy and demand usage. For example, a factor of 0.24 would equate to 24 percent energy and demand savings. The same values from the referenced LBNL study are used for both EAF and PAF factors due to the lack of published data for demand factors.

Table 13: Lighting Controls Definitions

| Control Type | Description |
| --- | --- |
| None | No control |
| Occupancy | Adjusting light levels according to the presence of occupants - Wall or ceiling-mounted occupancy sensors - Integrated fixture occupancy sensors - Time clocks - Energy management systems |
| Daylighting (indoor) | Adjusting light levels automatically in response to the presence of natural light - Photosensors |
| Outdoor | Outdoor on/off photosensor/time clock controls; no savings attributed because already required by code |
| Personal tuning | Adjusting individual light levels by occupants according to their personal preference; applies to private offices, workstation-specific lighting in open-plan offices, and classrooms - Dimmers - Wireless ON/OFF switches - Personal computer-based controls - Pre-set scene selection |
| Institutional tuning | Adjustment of light levels through commissioning or provision of switches or controls for areas or groups of occupants - Dimmable ballasts - ON/OFF or dimmer switches for non-personal tuning |
| Multiple types | Any combination of the types described above |

Table 14: Lighting Controls Energy and Power Adjustment Factors

| Control Type | Sub-Category | Control Codes | EAF | PAF |
| --- | --- | --- | --- | --- |
| None | Not applicable. | None | 0.00 | 0.00 |
| Occupancy | Not applicable. | OS | 0.24 | 0.24 |
| Daylighting (indoor) | Continuous dimming | DL-Cont | 0.28 | 0.28 |
|  | Multiple-step dimming | DL-Step |  |  |
|  | ON/OFF | DL-ON/OFF |  |  |
| Outdoor | Not applicable. | Outdoor | 0.00 | 0.00 |
| Personal tuning | Not applicable. | PT | 0.31 | 0.31 |
| Institutional tuning | Not applicable. | IT | 0.36 | 0.36 |
| Multiple/combined types | Various combinations | Multiple | 0.47 | 0.47 |

##### Deemed Energy and Demand Savings Tables

This section is not applicable.

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

Lighting controls savings for interior new construction projects should be claimed at the project level (combined fixture and controls savings) using a 14-year estimated useful life (EUL). Lighting controls savings are not eligible for exterior new construction applications.

For retrofit applications, the EUL for lighting controls is provided by the 2007 GDS Associates Report.

- Occupancy Sensor: 10 years

- Daylighting Control: 10 years

- Time Clock: 10 years

- Tuning Control: 10 years

#### Program Tracking Data and Evaluation Requirements

Primary inputs and contextual data that should be specified and tracked by the program database to inform the evaluation and apply the savings properly are:

- Building type

- Decision/action type: RET or NC

- Conditioned Space Type: cooling equipment type, refrigerated space temperature range (specified per control)

- Location of controlled lighting: interior or exterior (specified per control)

- Baseline & iinstalled lighting control type codes (Table 14)

- Lighting control mount type: wall, ceiling, integrated fixture, etc.

- Lighting control specification sheets

- Controlled fixture/lamp type

- Controlled fixture wattage

- For retrofit only: Proof of purchase: invoice showing model number; a photo of the model number on product packaging and installed fixture; OR an evaluator pre-approved inspection approach

- For new construction only: Proof of purchase: invoice showing model number; a photo of the model number on product packaging and installed fixture; as-built design drawings; lighting specifications package that provides detailed make and model information on installed lighting; OR an evaluator pre-approved inspection approach

#### References and Efficiency Standards

##### Petitions and Rulings

- “A Meta-Analysis of Energy Savings from Lighting Controls in Commercial Buildings.” Williams, Alison, Atkinson, Barbara, Barbesi, Karina, and Rubinstein, Francis, Lawrence Berkeley National Laboratory (LBNL). September 2011. Table 6, p. 14. Weighted average by the number of “reviewed” and “non-reviewed” papers.

- PUCT Docket 40668—Describes deemed values to be used in energy and demand savings calculations.

- PUCT Docket 36779—Describes Effective Useful Life.

##### Relevant Standards and Reference Sources

- 2015 International Energy Conservation Code (Commercial Buildings)

- ANSI/ASHRAE/IESNA Standard 90.1-2013. Energy Standard for Buildings Except Low-Rise Residential Buildings. (Public/State buildings.)

### Light Emitting Diode (LED) Traffic Signals Measure Overview

TRM Measure ID: NR-LT-TS

Market Sector: Commercial

Measure Category: Lighting

Applicable Building Types: Outdoor

Fuels Affected: Electricity

Decision/Action Type(s): Retrofit

Program Delivery Type(s): Prescriptive, custom, direct install

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This measure is for the installation of LED traffic signals (typically available in red, yellow, green, and pedestrian formats) at traffic lights serving any intersection, in retrofit applications.

##### Eligibility Criteria

New construction applications are not eligible for this measure, as incandescent traffic signals are not compliant with the current federal standard, effective January 1, 2006.

##### Baseline Condition

For all retrofit applications, the baseline is a fixture with incandescent lamps.

##### High-efficiency Condition

Due to the increased federal standard for traffic signals, the ENERGY STAR® Traffic Signal specification was suspended effective May 1, 2007. ENERGY STAR® chose to suspend the specification rather than revise it due to minimal additional savings that would result from a revised specification. Because the ENERGY STAR® specification no longer exists, the efficiency standard is an equivalent LED fixture for the same application. The equivalent LED fixture must be compliant with the current federal standard except for yellow “ball” or “arrow” fixtures where there is no federal standard.

Table 15: Federal Standard Maximum Wattages and Nominal Wattages

| Module Type | Maximum Wattage | Nominal Wattage |
| --- | --- | --- |
| 12” Red Ball | 17 | 11 |
| 8” Red Ball | 13 | 8 |
| 12” Red Arrow | 12 | 9 |
| 12” Green Ball | 15 | 15 |
| 8” Green Ball | 12 | 12 |
| 12” Green Arrow | 11 | 11 |
| Combination Walking Man/Hand | 16 | 13 |
| Walking Man | 12 | 9 |
| Orange Hand | 16 | 13 |

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

This section describes the deemed savings methodology for both energy and demand savings for all LED traffic signal projects.

Energy Savings=kWpre-kWinstalled×Hours

Equation 8

Peak Summer Demand Savings=kWpre-kWinstalled×CF

Equation 9

Where:

kWpre	=	Total kW of existing measure (fixture wattage multiplied by quantity)

kWinstalled	=	Total kW of retrofit measure (fixture wattage multiplied by quantity)

Hours	=	Annual operating hours from Table 16

CF	= 	Coincidence factor from Table 16

Table 16: Incandescent and LED Traffic Signal Savings Assumptions

| Fixture Type | Incand. Wattage | LED Wattage | AOH | CF |
| --- | --- | --- | --- | --- |
| 8” Red Ball | 86 | 8 | 4,746 | 0.54 |
| 8” Green Ball |  | 10 | 3,751 | 0.43 |
| 8” Yellow Ball |  | 13 | 263 | 0.03 |
| 12” Red Ball | 149 | 11 | 4,746 | 0.54 |
| 12” Green Ball |  | 12 | 3,751 | 0.43 |
| 12” Yellow Ball |  | 10 | 263 | 0.03 |
| 8” Red Arrow | 69 | 8 | 6,570 | 0.75 |
| 8” Green Arrow |  | 8 | 1,825 | 0.21 |
| 8” Yellow Arrow | 128 | 10 | 263 | 0.03 |
| 12” Red Arrow |  | 7.5 | 7,771 | 0.89 |
| 12” Green Arrow |  | 10 | 726 | 0.08 |
| 12” Yellow Arrow |  | 10 | 263 | 0.03 |
| Large (16”x18”) Pedestrian Signal | 149 | 9 | 8,642 | 0.99 |
| Small (12”x12”) Pedestrian Signal | 107 | 9 | 8,642 | 0.99 |

##### Deemed Energy and Demand Savings Tables

Table 17: LED Traffic Signal Deemed Savings per Fixture

| Fixture Type | kW Savings | kWh Savings |
| --- | --- | --- |
| 8” Red Ball | 0.042 | 370 |
| 8” Green Ball | 0.033 | 285 |
| 8” Yellow Ball | 0.002 | 19 |
| 12” Red Ball | 0.075 | 655 |
| 12” Green Ball | 0.059 | 514 |
| 12” Yellow Ball | 0.004 | 37 |
| 8” Red Arrow | 0.046 | 401 |
| 8” Green Arrow | 0.013 | 111 |
| 8” Yellow Arrow | 0.004 | 31 |
| 12” Red Arrow | 0.107 | 936 |
| 12” Green Arrow | 0.010 | 86 |
| 12” Yellow Arrow | 0.004 | 31 |
| Large (16”x18”) Pedestrian Signal | 0.138 | 1,210 |
| Small (12”x12”) Pedestrian Signal | 0.097 | 847 |

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

According to the Northwest Power and Conservation Council Regional Technical Forum, the EUL is 5 to 6 years depending on the installed fixture type, as shown in the following table.

Table 18: Incandescent and LED Traffic Signal EULs by Fixture Type

| Fixture Type | EUL (Years) |
| --- | --- |
| 8” and 12” Red, Green, and Yellow Ball | 6 |
| 8” and 12” Red, Green, and Yellow Arrow |  |
| Large (16”x18”) Pedestrian Signal | 5 |
| Small (12”x12”) Pedestrian Signal |  |

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Decision/Action Type: retrofit or NC (NC not eligible)

- Fixture type

- Quantity of installed fixtures

- Proof of purchase: invoice showing model number; a photo of the model number on product packaging and installed fixture; OR an evaluator pre-approved inspection approach

#### References and Efficiency Standards

##### Petitions and Rulings

##### Relevant Standards and Reference Sources

- Traffic Signal Modules and Pedestrian Modules Federal Standard. https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=12.

- Regional Technical Forum LED Traffic Signals savings workbook. https://rtf.nwcouncil.org/measure/led-traffic-signals?id=114&decisionid=37.

## Nonresidential: HVAC

### Air Conditioner or Heat Pump Tune-ups Measure Overview

TRM Measure ID: NR-HV-TU

Market Sector: Commercial

Measure Category: HVAC

Applicable Building Types: See Table 26 through Table 32

Fuels Affected: Electricity

Decision/Action Type(s): Retrofit

Program Delivery Type(s): Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This measure applies to direct expansion central air conditioners (AC) and heat pumps (HP) of any configuration where all applicable actions from the checklist below are completed. An AC tune-up involves checking, cleaning, adjusting, and resetting the equipment to factory conditions to restore operating efficiencies closer to as-new performance. This measure applies to all commercial applications.

For this measure, the service technician must complete the following tasks according to industry best practices. To properly assess and adjust the refrigerant charge level, the unit must be operating under significant (normal) cooling load conditions. Therefore, this measure may only be performed for energy savings reporting purposes when the outdoor ambient dry bulb temperature is above 75˚F and the indoor return air dry bulb temperature is above 70˚F.

##### Air Conditioner Inspection and Tune-up Checklist:

- Tighten all electrical connections; measure motor voltage and current

- Lubricate all moving parts, including motor and fan bearings

- Inspect and clean condensate drain

- Inspect controls of the system to ensure proper and safe operation; check startup/shutdown cycle of the equipment to assure the system starts, operates, and shuts off properly

- Clean evaporator and condenser coils

- Clean indoor blower fan components

- Inspect and clean (or change) air filters; replacement preferred best practice

- Measure airflow via static pressure across the cooling coil and adjust to manufacturers specifications

- Check refrigerant level and adjust to manufacturer specifications

- Check capacitor functionality and capacitance; compare to OEM specifications

##### Eligibility Criteria

All commercial customers are eligible for this measure if they have direct expansion refrigerated air conditioning that has not been serviced in the last 5 years. This measure does not apply to chillers.

##### Baseline Condition

The baseline is a system with all or some of the following issues:

- Dirty condenser coil

- Dirty evaporator coil

- Dirty blower wheel

- Dirty filter

- Improper airflow

- Incorrect refrigerant charge

The baseline system efficiency should be calculated using the following formulas:

EERpre=(1-EL)×EERpost

Equation 10

HSPFpre=(1-EL)×HSPFpost

Equation 11

Where:

EERpre 	=	Efficiency of the cooling equipment before tune-up

EL 	=	Efficiency loss due to dirty coils, blower, filter, improper airflow, and/or incorrect refrigerant charge = 0.05

EERpost 	=	Deemed cooling efficiency of the equipment after tune-up. See Table 19.

HSPFpre 	= 	Heating efficiency of the air source heat pump before tune-up

HSPFpost 	= 	Deemed heating efficiency of air source heat pumps after tune-up. See Table 19.

Table 19: Default EER and HSPF per Size Category

| Size Category (Btuh/hr) | AC Only Default EER | Heat Pump Default EER | Default HSPF |
| --- | --- | --- | --- |
| < 65,000 | 11.2 | 11.2 | 7.7 |
| ≥ 65,000 and < 135,000 | 10.1 | 9.9 | 10.9 |
| ≥ 135,000 and < 240,000 | 9.5 | 9.1 | 10.6 |
| ≥ 240,000 and < 760,000 | 9.3 | 8.8 | 10.6 |
| ≥ 760,000 | 9.0 | 8.8 | 10.6 |

##### High-efficiency Condition

After the tune-up, the equipment must be clean with airflows and refrigerant charges adjusted as appropriate and set forth above. Additionally, refrigerant charge adjustments must be within ± 3 degrees of target sub-cooling for units with thermal expansion valves (TXV) and ± 5 degrees of target super heat for units with fixed orifices or capillary tubes.

The efficiency standard, or efficiency after the tune-up, is deemed to be the manufacturer specified energy efficiency ratio (EER) of the existing central air conditioner or heat pump, which has been determined using the following logic and standards. The useful life of an AC unit is 19 years. The useful life of a heat pump is 16 years. Therefore, it is conservatively thought that the majority of existing, functioning units were installed under the federal standard in place between January 23, 2006 and January 1, 2015 for units less than 65,000 Btuh, which set a baseline of 13 SEER and 7.7 HSPF, and prior to January 1, 2010 for units greater than 65,000 Btuh. A 13 SEER is equivalent to approximately 11.2 EER using the conversion developed by Lawrence Berkeley Lab and US DOE: EER = -0.02 x SEER2 + 1.12 x SEER. A 3.2 and 3.1 COP is equivalent to approximately 10.9 and 10.6 HSPF, respectively, using the conversion of HSPF = 3.412 x COP.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Savings are based on an assumed efficiency loss factor of five percent due to dirty coils, dirty filters, improper airflow, and/or incorrect refrigerant charge.

Heating energy savings are only applicable to heat pumps.

Energy Savings kWhsavings=kWhSavings,C+kWhSavings,H

Equation 12

Energy Cooling kWhSavings,C=Capacity×1EERpre-1EERpost×EFLHC×1 kW1,000 W

Equation 13

Energy Heating kWhSavings,H=Capacity×1HSPFpre-1HSPFpost×EFLHH×1 kW1,000 W

Equation 14

Where:

Capacity	=	Rated cooling capacity of the equipment based on model number [Btuh] (1 ton = 12,000 Btuh)

EERpre	= 	Cooling efficiency of the equipment pre-tune-up using Table 19 [Btuh/W]

EERpost	=	Cooling efficiency of the equipment after the tune-up [Btuh/W]

HSPFpre	= 	Heating efficiency of the equipment pre-tune-up using Table 19 [Btuh/W]

HSPFpost	=	Heating efficiency of the equipment after the tune-up [Btuh/W]

Summer Peak Demand kWSavings,C=Capacity×1EERpre-1EERpost×DFC×1 kW1,000 W

Equation 15

Winter Peak Demand kWSavings,H=Capacity×1HSPFpre-1HSPFpost×DFH×1 kW1,000 W

Equation 16

Where:

EFLHC/H	=	Cooling/heating equivalent full-load hours for appropriate climate zone [hours]. See Table 28 through Table 32 in Section 2.2.2.

##### Demand Savings Algorithms

Summer and winter demand savings are determined by applying a coincidence factor for each season. Winter peak demand savings are only applicable to heat pumps.

Where:

DFC	=	Cooling Demand factor. See Table 28 through Table 32 in Section 2.2.2.

DFH	= 	Heating Demand factor. See Table 28 through Table 32 in Section 2.2.2.

##### Deemed Energy Savings Tables

There are no lookup tables available for this measure. See engineering algorithms in the previous section for calculating energy and demand savings.

##### Deemed Summer Demand Savings Tables

There are no lookup tables available for this measure. See engineering algorithms in the previous section for calculating energy and demand savings.

##### Deemed Winter Demand Savings Tables

There are no lookup tables available for this measure. See engineering algorithms in the previous section for calculating energy and demand savings.

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Additional Calculators and Tools

This section is not applicable.

##### Measure Life and Lifetime Savings

The estimated useful life (EUL) for a tune-up is 5 years.

According to the 2014 California Database for Energy Efficiency Resources (DEER), the estimated useful life of cleaning condenser and evaporator coils is 3 years, and the estimated useful life of refrigerant charge adjustment is 10 years. The other parts of the tune-up checklist are not listed in DEER. Therefore, 5 years is used as the best representation of the entire tune-up, as referenced by the Measure Life Report.

#### Program Tracking Data and Evaluation Requirements

Primary inputs and contextual data that should be specified and tracked by the program database to inform the evaluation and apply the savings properly are:

- Manufacturer

- Model number

- Cooling capacity of the installed unit (tons)

- Climate zone or county of the site

- Type of unit

  - Air conditioner

  - Air source heat pump

- Recommended

  - Serial number

  - Refrigerant type

  - Target superheat or subcooling

  - Post-tune-up superheat or subcooling

  - Amount of refrigerant added or removed

  - Static pressures before and after a tune-up

  - Return and supply dry bulb and wet bulb temperatures

  - Before and after tune-up pictures of components illustrating condition change due to cleanings (Note: pictures that include well-placed familiar objects like hand tools often provide a sense of scale and a reference for color/shading comparisons. Pictures of equipment nameplates are useful).

#### References and Efficiency Standards

This section is not applicable.

### Split System/Single Packaged Air Conditioners and Heat Pumps Measure Overview

TRM Measure ID: NR-HV-SP

Market Sector: Commercial

Measure Category: HVAC

Applicable Building Types: See Table 26 through Table 32

Fuels Affected: Electricity

Decision/Action Type: Replace-on-burnout, early retirement, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Energy modeling, engineering algorithms, and estimates

#### Measure Description

This section summarizes the deemed savings methodology for the installation of air-cooled split system and single packaged air conditioning (AC) and heat pump (HP) systems. This document covers assumptions made for baseline equipment efficiencies for early retirement (ER) based on the age of the replaced equipment and for replace-on-burnout (ROB) and new construction (NC) situations based on efficiency standards. Savings calculations incorporate the use of both full-load and part-load efficiency values. For ER, the actual age of the baseline system should be determined from the equipment nameplate or other physical documentation whenever possible. Default values are provided for when the actual age of the unit is unknown.

Applicable efficient measure types include:

- Packaged and split air conditioners (DX or air-cooled)

- Packaged and split heat pumps (air-cooled)

- System Type Conversions. Retrofits involving a change from a chiller-based system to a packaged/split system are also covered under this measure. If this type of retrofit is performed, reference the tables from the HVAC Chillers measure.

##### Eligibility Criteria

For a measure to be eligible to use this deemed savings approach, the following conditions must be met:

- The existing and proposed cooling equipment is electric.

- The building falls into one of the categories listed in Table 28 through Table 32. Building type descriptions and examples are provided in Table 26 and Table 27.

- For early retirement projects: ER projects involve the replacement of a working system. Additionally, the ER approach cannot be used for projects involving a renovation where a major structural change or internal space remodel has occurred. A ROB approach should be used for these scenarios.

- If these conditions are not met, the deemed savings approach cannot be used, and the Simplified M&V Methodology or the Full M&V Methodology must be used.

Manufacturer datasheets for installed equipment or documentation of AHRI or DOE CCMS certification must be provided.,

##### Baseline Condition

The baseline conditions related to efficiency and system capacity for early retirement and replace-on-burnout/new construction are as follows:

Early Retirement

Early retirement systems involve the replacement of a working system, prior to natural burnout. The ER baseline cannot be used for projects involving a renovation where a major structural change or internal space remodel has occurred.

Two baseline condition efficiency values are required for an ER scenario, one for the ER (RUL) period and one for the ROB (EUL-RUL) period. For the ROB period, the baseline efficiency is the same as ROB/NC scenario. For the ER period, the baseline efficiency should be estimated using the values from Table 20 through Table 24 according to the capacity, system type, and age (based on year manufactured) of the replaced system. When the system age can be determined (e.g., from nameplate, building prints, equipment inventory list), the baseline efficiency levels provided in Table 20 through Table 24 should be used. If individual system components were installed at different times, use the condenser age as a proxy for the entire system. When the system age is unknown, assume an age of 15 years. A default RUL may be used exclusively if applied consistently for all projects. Otherwise, the default should only be used when a project is reported and documented as having a nameplate that is illegible.

PUCT Docket 40885 provided baseline efficiencies for split and packaged systems replaced via ER.

ER baseline efficiency values represent the code-specified efficiency in effect at the time the system was installed. Prior to 2002, code-specified efficiencies from ASHRAE 90.1-1989 were in effect. Code-specified efficiencies increased in 2002, approximating the effective date of ASHRAE 90.1-1999, which went into effect on October 29, 2001. Code-specified efficiencies increased again in 2010 and 2018, coinciding with the IECC 2009 and IECC 2015 code increases. The baseline efficiency levels shown in Table 20 through Table 24 are based on assumptions of the predominant heating types expected in the state. For air conditioners, baseline cooling efficiencies are displayed for a natural gas furnace heating section type. For heat pumps, baseline cooling efficiencies are displayed for electric resistance supplemental heating section type. For all other heating section types, or for no heating section type, the baseline efficiencies may need to be adjusted as specified by the footnotes in the tables.

Table 20: ER Baseline Full-load Efficiency for ACs

| Year Installed (Replaced System) | Split Systems < 5.4 tons [EER] | Package System < 5.4 tons [EER] | All Systems 5.4 to < 11.3 tons [EER] | All Systems 11.3 to < 20 tons [EER]53 | All Systems 20 to < 63.3 tons [EER]53 | All Systems > 63.3 tons [EER]53 |
| --- | --- | --- | --- | --- | --- | --- |
| ≤ 2005 | 9.2 | 9.0 | 10.1 | 9.5 | 9.3 | 9.0 |
| 2006–2009 | 11.2 | 11.2 | 10.1 | 9.5 | 9.3 | 9.0 |
| 2010–2017 | 11.2 | 11.2 | 11.0 | 10.8 | 9.8 | 9.5 |
| ≥ 2018 | 11.2 | 11.8 | 11.0 | 10.8 | 9.8 | 9.5 |

Table 21: ER Baseline Part-load Efficiency for ACs

| Year Installed (Replaced System) | Split Systems < 5.4 tons [SEER] | Package System < 5.4 tons [SEER] | All Systems 5.4 to < 11.3 tons [IEER] | All Systems 11.3 to < 20 tons [IEER] | All Systems 20 to < 63.3 tons [IEER] | All Systems > 63.3 tons [IEER]55 |
| --- | --- | --- | --- | --- | --- | --- |
| ≤ 2005 | 10.0 | 9.7 | 10.3 | 9.7 | 9.4 | 9.1 |
| 2006–2009 | 13.0 | 13.0 | 10.3 | 9.7 | 9.4 | 9.1 |
| 2010–2017 | 13.0 | 13.0 | 11.2 | 11.0 | 9.9 | 9.6 |
| ≥ 2018 | 13.0 | 14.0 | 12.6 | 12.2 | 11.4 | 11.0 |

Table 22: ER Baseline Full-load Cooling Efficiency for HPs

| Year Installed (Replaced System) | Split Systems < 5.4 tons [EER] | Package System < 5.4 tons [EER] | All Systems 5.4 to < 11.3 tons [EER] | All Systems 11.3 to < 20 tons [EER]58 | All Systems 20 to < 63.3 tons [EER]58 | All Systems > 63.3 tons [EER]58 |
| --- | --- | --- | --- | --- | --- | --- |
| ≤ 2005 | 9.2 | 9.0 | 10.1 | 9.3 | 9.0 | 9.0 |
| 2006–2009 | 11.2 | 11.2 | 10.1 | 9.3 | 9.0 | 9.0 |
| 2010–2017 | 11.2 | 11.2 | 11.0 | 10.6 | 9.5 | 9.5 |
| ≥ 2018 | 11.8 | 11.8 | 11.0 | 10.6 | 9.5 | 9.5 |

Table 23: ER Baseline Part-load Cooling Efficiency for HPs

| Year Installed (Replaced System) | Split Systems < 5.4 tons [SEER] | Package System < 5.4 tons [SEER] | All Systems 5.4 to < 11.3 tons [IEER] | All Systems 11.3 to < 20 tons [IEER]60 | All Systems 20 to < 63.3 tons [IEER]60 | All Systems > 63.3 tons [IEER]60 |
| --- | --- | --- | --- | --- | --- | --- |
| ≤ 2005 | 10.0 | 9.7 | 10.3 | 9.5 | 9.1 | 9.1 |
| 2006–2009 | 13.0 | 13.0 | 10.3 | 9.5 | 9.1 | 9.1 |
| 2010–2017 | 13.0 | 13.0 | 11.2 | 10.7 | 9.6 | 9.6 |
| ≥ 2018 | 14.0 | 14.0 | 12.0 | 11.6 | 10.6 | 10.6 |

Table 24: ER Baseline Heating Efficiency for HPs

| Year Installed (Replaced System) | Split Systems < 5.4 tons [HSPF] | Package System < 5.4 tons [HSPF] | All Systems 5.4 to < 11.3 tons [COP] | All Systems > 11.3 tons [COP] |
| --- | --- | --- | --- | --- |
| ≤ 2005 | 6.8 | 6.6 | 3.2 | 3.1 |
| 2006–2009 | 7.7 | 7.7 | 3.2 | 3.1 |
| 2010–2017 | 7.7 | 7.7 | 3.3 | 3.2 |
| ≥ 2018 | 8.2 | 8.0 | 3.3 | 3.2 |

Replace-on-Burnout (ROB) and New Construction (NC)

Baseline efficiency levels for package and split DX air conditioners and heat pumps are provided in Table 25. These baseline efficiency levels reflect the latest minimum efficiency requirements from the current federal manufacturing standard and IECC 2015.

Table 25: Baseline Efficiency Levels for ROB and NC Air Conditioners and Heat Pumps

| System Type | Capacity [Tons] | Heating Section Type | Baseline Efficiencies | Source |
| --- | --- | --- | --- | --- |
| Air Conditioner | < 5.4 | All | 11.2 EER 13.0 SEER (split) 11.8 EER 14.0 SEER (packaged) | DOE Standards/ IECC 2015 |
|  | 5.4 to < 11.3 | None or Electric Resistance | 11.2 EER 12.8 IEER |  |
|  |  | All Other | 11.0 EER 12.6 IEER |  |
|  | 11.3 to < 20 | None or Electric Resistance | 11.0 EER 12.4 IEER |  |
|  |  | All Other | 10.8 EER 12.2 IEER |  |
|  | 20 to < 63.3 | None or Electric Resistance | 10.0 EER 11.6 IEER |  |
|  |  | All Other | 9.8 EER 11.4 IEER |  |
|  | > 63.3 | None or Electric Resistance | 9.7 EER 11.2 IEER | IECC 2015 |
|  |  | All Other | 9.5 EER 11.0 IEER |  |
| Heat Pump (cooling) | < 5.4 | Heat Pump | 11.8 EER 14.0 SEER | DOE Standards/ IECC 2015 |
|  | 5.4 to < 11.3 |  | 11.0 EER 12.0 IEER |  |
|  | 11.3 to < 20 |  | 10.6 EER 11.6 IEER |  |
|  | > 20 |  | 9.5 EER 10.6 IEER |  |
| Heat Pump (heating) | < 5.4 | Heat Pump | 8.2 HSPF (split) 8.0 HSPF (packaged) | DOE Standards/IECC 2015 |
|  | 5.4 to < 11.25 |  | 3.3 COP |  |
|  | > 11.3 |  | 3.2 COP |  |

##### High-efficiency Condition

Package and split-systems must exceed the minimum efficiencies specified in Table 25. Split system efficiencies are driven primarily by the efficiency of the condenser unit. If the paired outdoor and indoor units are not listed on the AHRI certification listing and only provide DOE CCMS testing results, then the capacity and efficiency of the high efficient condition shall not exceed the average of the AHRI certification listing pairing for the matching condenser. The DOE CCMS listing provides documentation of the results that are on the AHRI certification listing and can be downloaded and filtered based on listing using a similar condenser and various indoor units.

For reference, both ENERGY STAR® and the Consortium for Energy Efficiency (CEE) offer suggested guidelines for high-efficiency equipment. Additional conditions for replace-on-burnout, early retirement and new construction are as follows:

New Construction and Replace-on-Burnout

This scenario includes equipment used for new construction and retrofit/replacements that are not covered by early retirement, such as units that are replaced after natural failure.

Early Retirement

The high-efficiency retrofits must meet the following criteria:

- For ER projects only, the installed equipment cooling capacity must be within 80 percent to 120 percent of the replaced electric cooling capacity. For scenarios involving the replacement of a combination of systems by an alternate combination of systems of varying capacities, ER savings can still be claimed if the overall pre- and post-capacities for the total combination of systems are within ± 20%. In these cases, a custom calculation should be performed to establish the following weighted savings factors to be applied over the ER portion of the savings calculation: manufacturer year, EUL, RUL, full and part-load baseline efficiency, demand factor, and EFLH. These factors should be weighted based on contribution to overall capacity.

- No additional measures are being installed that directly affect the operation of the cooling equipment (e.g., control sequences, cooling towers, and condensers).

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Energy Savings kWhsavings=kWhSavings,C+kWhSavings,H

Peak Demand (Summer) [kWSavings,C]=CapC,preηbaseline,C-CapC,postηinstalled,C×DFC×1 kW1,000 W

Equation 17

Peak Demand (Winter) [kWSavings,H]=CapH,preηbaseline,H-CapH,postηinstalled,H×DFH×1 kW3,412 Btuh

Equation 18

Energy Savings kWhsavings=kWhSavings,C+kWhSavings,H

Equation 19

Energy Cooling kWhSavings,C=CapC,preηbaseline,C-CapC,postηinstalled,C×EFLHC×1 kW1,000 W

Equation 20

Energy Heating kWhSavings,H=CapH,preηbaseline,H-CapH,postηinstalled,H×EFLHH×1 kWh3,412 Btu

Equation 21

Where:

CapC/H,pre	=	For ER, rated equipment cooling/heating capacity of the existing equipment at AHRI standard conditions; for ROB & NC, rated equipment cooling/heating capacity of the new equipment at AHRI standard conditions [Btuh]; 1 ton = 12,000 Btuh

CapC/H,post	=	Rated equipment cooling/heating capacity of the newly installed equipment at AHRI standard conditions [Btuh]; 1 ton = 12,000 Btuh

ηbaseline,C	= 	Cooling efficiency of existing equipment (ER) or standard equipment (ROB/NC) [Btuh/W]

ηinstalled,C	=	Rated cooling efficiency of the newly installed equipment (kW/Ton)—(Must exceed ROB/NC baseline efficiency standards in Table 25) [Btuh/W]

ηbaseline,H	= 	Heating efficiency of existing equipment (ER) or standard equipment (ROB/NC) [COP]

ηinstalled,H	=	Rated heating efficiency of the newly installed equipment (Must exceed baseline efficiency standards in Table 25) [COP]

Note: Use EER for kW savings calculations and SEER/IEER and COP for kWh savings calculations. The COP expressed for units > 5.4 tons is a full-load COP. Heating efficiencies expressed as HSPF will be approximated as a seasonal COP and should be converted using the following equation:

COP=HSPF3.412

Equation 22

DFC/H	=	Seasonal peak demand factor for appropriate climate zone, building type, and equipment type (Table 28 through Table 32)

EFLHC/H	=	Cooling/heating equivalent full-load hours for appropriate climate zone, building type, and equipment type [hours] (Table 28 through Table 32)

Early Retirement Savings

The first-year savings algorithms in the above equations are used for all HVAC projects, across NC, ROB, and ER projects. However, ER projects require weighted savings calculated over both the ER and ROB periods, accounting for both the EUL and RUL. The ER savings are applied over the remaining useful life (RUL) period, and the ROB savings are applied over the remaining period (EUL-RUL). The final reported savings for ER projects are not actually a “first-year” savings, but an “average annual savings over the lifetime (EUL) of the measure.” These savings calculations are explained in Appendix A.

##### Deemed Energy and Demand Savings Tables

Deemed peak demand factor (DF) and equivalent full-load hour (EFLH) values are presented by building type and climate zone. A description of the building types that are used for HVAC systems is presented in Table 26 and Table 27. These building types are derived from the EIA CBECS study.

The DF and EFLH values for packaged and split AC and HP units are presented in Table 28 through Table 32. These tables also include an “Other” building type, which can be used for business types that are not explicitly listed. The DF and EFLH values used for Other are the most conservative values from the explicitly listed building types. When the Other building type is used, a description of the actual building type, the primary business activity, the business hours, and the HVAC schedule must be collected for the project site and stored in the utility tracking data system.

For those combinations of technology, climate zone, and building type where no values are present, a project with that specific combination should use the “Other” building type.

A description of the calculation method used to derive these values can be found in Docket No. 40885, Attachment B.

Table 26: Commercial HVAC Building Type Descriptions and Examples

| Building Type | Principal Building Activity | Definition |  | Detailed Business Type Examples |
| --- | --- | --- | --- | --- |
| Data Center | Data Center | Buildings used to house computer systems and associated components. |  | 1) Data Center |
| Education | College/University | Buildings used for academic or technical classroom instruction, such as elementary, middle, or high schools, and classroom buildings on college or university campuses. Buildings on education campuses for which the main use is not classroom are included in the category relating to their use. For example, administration buildings are part of "Office," dormitories are "Lodging," and libraries are "Public Assembly." |  | 1) College or University 2) Career or Vocational Training 3) Adult Education |
|  | Primary School |  |  | 1) Elementary or Middle School 2) Preschool or Daycare |
|  | Secondary School |  |  | 1) High School 2) Religious Education |
| Food Sales | Convenience | Buildings used for retail or wholesale of food. |  | 1) Gas Station with a Convenience Store 2) Convenience Store |
|  | Supermarket |  |  | 1) Grocery Store or Food Market |
| Food Service | Full-service Restaurant | Buildings used for the preparation and sale of food and beverages for consumption. |  | 1) Restaurant or Cafeteria |
|  | Quick-service Restaurant |  |  | 1) Fast Food |
| Healthcare | Hospital | Buildings used as diagnostic and treatment facilities for inpatient care. |  | 1) Hospital 2) Inpatient Rehabilitation |
|  | Outpatient Healthcare | Buildings used as diagnostic and treatment facilities for outpatient care. Medical offices are included here if they use any type of diagnostic medical equipment (if they do not, they are categorized as an office building). |  | 1) Medical Office 2) Clinic or Outpatient Health Care 3) Veterinarian |
| Large Multifamily | Midrise Apartment | Buildings containing multifamily dwelling units, having multiple stories and equipped with elevators. |  | No sub-categories collected. |
| Lodging | Large Hotel | Buildings used to offer multiple accommodations for short-term or long-term residents, including skilled nursing and other residential care buildings. |  | 1) Motel or Inn 2) Hotel 3) Dormitory, Fraternity, or Sorority 4) Retirement Home, Nursing Home, Assisted Living, or other Residential Care 5) Convent or Monastery |
|  | Nursing Home |  |  |  |
|  | Small Hotel/Motel |  |  |  |
| Mercantile | Stand-alone Retail | Buildings used for the sale and display of goods other than food. |  | 1) Retail Store 2) Beer, Wine, or Liquor Store 3) Rental Center 4) Dealership or Showroom for Vehicles or Boats 5) Studio or Gallery |
|  | Strip Mall | Shopping malls comprised of multiple connected establishments. |  | 1) Strip Shopping Center 2) Enclosed Malls |
| Office | Large Office | Buildings used for general office space, professional office, or administrative offices. Medical offices are included here if they do not use any type of diagnostic medical equipment (if they do, they are categorized as an outpatient health care building). |  | 1) Administrative or Professional Office 2) Government Office 3) Mixed-Use Office 4) Bank or Other Financial Institution 5) Medical Office 6) Sales Office 7) Contractor’s Office (e.g., Construction, Plumbing, HVAC) 8) Non-Profit or Social Services 9) Research and Development 10) City Hall or City Center 11) Religious Office 12) Call Center |
|  | Medium Office |  |  |  |
|  | Small Office |  |  |  |
| Public Assembly | Public Assembly | Buildings in which people gather for social or recreational activities, whether in private or non-private meeting halls. |  | 1) Social or Meeting (e.g., Community Center, Lodge, Meeting Hall, Convention Center, Senior Center) 2) Recreation (e.g., Gymnasium, Health Club, Bowling Alley, Ice Rink, Field House, Indoor Racquet Sports) 3) Entertainment or Culture (e.g., Museum, Theater, Cinema, Sports Arena, Casino, Night Club) 4) Library 5) Funeral Home 6) Student Activities Center 7) Armory 8) Exhibition Hall 9) Broadcasting Studio 10) Transportation Terminal |
| Religious Worship | Religious Worship | Buildings in which people gather for religious activities (such as chapels, churches, mosques, synagogues, and temples). |  | No sub-categories collected. |
| Service | Service | Buildings in which some type of service is provided, other than food service or retail sales of goods. |  | 1) Vehicle Service or Vehicle Repair Shop 2) Vehicle Storage/Maintenance 3) Repair Shop 4) Dry Cleaner or Laundromat 5) Post Office or Postal Center 6) Car Wash 7) Gas Station with no Convenience Store 8) Photo Processing Shop 9) Beauty Parlor or Barber Shop 10) Tanning Salon 11) Copy Center or Printing Shop 12) Kennel |
| Warehouse | Warehouse | Buildings used to store goods, manufactured products, merchandise, raw materials, or personal belongings (such as self-storage). |  | 1) Refrigerated Warehouse 2) Non-refrigerated warehouse 3) Distribution or Shipping Center |
| Other | Other |  | For building types not explicitly listed. | Values used for Other are the most conservative values from the explicitly listed building types. |

Table 27: Commercial HVAC Floor Area and Floor Assumptions by Building Type

| Building Type | Principal Building Activity | Average Floor Area (ft2) | Average # of Floors |
| --- | --- | --- | --- |
| Data Center | Data Center | Not specified | Not specified |
| Education | College/University | Not specified | Not specified |
|  | Primary School | 73,960 | 1 |
|  | Secondary School | 210,887 | 2 |
| Food Sales | Convenience | Not specified | 1 |
|  | Supermarket | 45,000 | 1 |
| Food Service | Full-service Restaurant | 5,500 | 1 |
|  | Quick-service Restaurant | 2,500 | 1 |
| Healthcare | Hospital | 241,351 | 5 |
|  | Outpatient Healthcare | 40,946 | 3 |
| Large Multifamily | Midrise Apartment | 33,740 | 4 |
| Lodging | Large Hotel | 122,120 | 6 |
|  | Nursing Home | Not specified | Not specified |
|  | Small Hotel/Motel | 43,200 | 4 |
| Mercantile | Stand-alone Retail | 24,962 | 1 |
|  | Strip Mall | 22,500 | 1 |
| Office | Large Office | 498,588 | 12 |
|  | Medium Office | 53,628 | 3 |
|  | Small Office | 5,500 | 1 |
| Public Assembly | Public Assembly | Not specified | Not specified |
| Religious Worship | Religious Worship | Not specified | Not specified |
| Service | Service | Not specified | Not specified |
| Warehouse | Warehouse | 52,045 | 1 |

Table 28: DF and EFLH Values for Amarillo (Climate Zone 1)

| Building Type | Principal Building Activity | Package and Split DX |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |
|  |  | DFC | EFLHC | DFC | EFLHC | DFH | EFLHH |
| Data Center | Data Center | 0.89 | 2,048 | 0.89 | 2,048 | -- | -- |
| Education | College/University | 0.69 | 787 | 0.69 | 787 | -- | -- |
|  | Primary School | 0.64 | 740 | 0.64 | 740 | 0.43 | 701 |
|  | Secondary School | 0.69 | 535 | 0.69 | 535 | 0.43 | 736 |
| Food Sales | Convenience | 0.73 | 884 | 0.73 | 884 | -- | -- |
|  | Supermarket | 0.29 | 219 | 0.29 | 219 | -- | -- |
| Food Service | Full-service Restaurant | 0.83 | 1,020 | 0.83 | 1,020 | 0.43 | 1,123 |
|  | 24-hour Full-service | 0.81 | 1,093 | 0.81 | 1,093 | 0.43 | 1,346 |
|  | Quick-service Restaurant | 0.73 | 765 | 0.73 | 765 | 0.48 | 1,029 |
|  | 24-hour Quick-service | 0.74 | 817 | 0.74 | 817 | 0.48 | 1,300 |
| Healthcare | Hospital | 0.72 | 2,185 | 0.72 | 2,185 | -- | -- |
|  | Outpatient Healthcare | 0.71 | 2,036 | 0.71 | 2,036 | 0.27 | 579 |
| Large Multifamily | Midrise Apartment | 0.68 | 674 | 0.68 | 674 | -- | -- |
| Lodging | Large Hotel | 0.58 | 1,345 | 0.58 | 1,345 | 0.86 | 1,095 |
|  | Nursing Home | 0.68 | 685 | 0.68 | 685 | -- | -- |
|  | Small Hotel/Motel | 0.57 | 1,554 | 0.57 | 1,554 | 0.36 | 475 |
| Mercantile | Stand-alone Retail | 0.68 | 623 | 0.68 | 623 | 0.99 | 907 |
|  | 24-hour Stand-alone Retail | 0.80 | 820 | 0.80 | 820 | 0.43 | 1,277 |
|  | Strip Mall | 0.75 | 687 | 0.75 | 687 | 0.39 | 753 |
| Office | Large Office | 0.90 | 2,058 | 0.90 | 2,058 | -- | -- |
|  | Medium Office | 0.64 | 925 | 0.64 | 925 | 0.72 | 576 |
|  | Small Office | 0.72 | 711 | 0.72 | 711 | 0.29 | 340 |
| Public Assembly | Public Assembly | 0.64 | 995 | 0.64 | 995 | -- | -- |
| Religious Worship | Religious Worship | 0.57 | 387 | 0.57 | 387 | -- | -- |
| Service | Service | 0.83 | 790 | 0.83 | 790 | -- | -- |
| Warehouse | Warehouse | 0.34 | 173 | 0.34 | 173 | -- | -- |
| Other | Other | 0.29 | 173 | 0.29 | 173 | 0.27 | 340 |

Table 29: DF and EFLH Values for Dallas (Climate Zone 2)

| Building Type | Principal Building Activity | Package and Split DX |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |
|  |  | DFC | EFLHC | DFC | EFLHC | DFH | EFLHH |
| Data Center | Data Center | 1.08 | 3,401 | 1.08 | 3,401 | -- | -- |
| Education | College/University | 1.02 | 1,595 | 1.02 | 1,595 | -- | -- |
|  | Primary School | 0.88 | 1,208 | 0.88 | 1,208 | 0.66 | 397 |
|  | Secondary School | 1.02 | 1,084 | 1.02 | 1,084 | 0.59 | 489 |
| Food Sales | Convenience | 1.08 | 1,835 | 1.08 | 1,835 | -- | -- |
|  | Supermarket | 0.58 | 615 | 0.58 | 615 | -- | -- |
| Food Service | Full-service Restaurant | 1.09 | 1,823 | 1.09 | 1,823 | 0.50 | 688 |
|  | 24-hour Full-service | 1.09 | 2,061 | 1.09 | 2,061 | 0.49 | 873 |
|  | Quick-service Restaurant | 1.08 | 1,588 | 1.08 | 1,588 | 0.61 | 631 |
|  | 24-hour Quick-service | 1.08 | 1,765 | 1.08 | 1,765 | 0.60 | 794 |
| Healthcare | Hospital | 0.92 | 3,097 | 0.92 | 3,097 | -- | -- |
|  | Outpatient Healthcare | 0.80 | 2,532 | 0.80 | 2,532 | 0.28 | 310 |
| Large Multifamily | Midrise Apartment | 1.04 | 1,709 | 1.04 | 1,709 | -- | -- |
| Lodging | Large Hotel | 0.70 | 2,079 | 0.70 | 2,079 | 0.82 | 464 |
|  | Nursing Home | 1.04 | 1,736 | 1.04 | 1,736 | -- | -- |
|  | Small Hotel/Motel | 0.55 | 2,281 | 0.55 | 2,281 | 0.42 | 249 |
| Mercantile | Stand-alone Retail | 0.95 | 1,157 | 0.95 | 1,157 | 0.55 | 352 |
|  | 24-hour Stand-alone Retail | 1.01 | 1,539 | 1.01 | 1,539 | 0.57 | 632 |
|  | Strip Mall | 0.91 | 1,100 | 0.91 | 1,100 | 0.55 | 376 |
| Office | Large Office | 1.03 | 2,379 | 1.03 | 2,379 | -- | -- |
|  | Medium Office | 0.76 | 1,236 | 0.76 | 1,236 | 0.66 | 262 |
|  | Small Office | 0.92 | 1,203 | 0.92 | 1,203 | 0.40 | 153 |
| Public Assembly | Public Assembly | 0.88 | 1,624 | 0.88 | 1,624 | -- | -- |
| Religious Worship | Religious Worship | 0.55 | 567 | 0.55 | 567 | -- | -- |
| Service | Service | 1.09 | 1,412 | 1.09 | 1,412 | -- | -- |
| Warehouse | Warehouse | 0.84 | 597 | 0.84 | 597 | -- | -- |
| Other | Other | 0.55 | 567 | 0.55 | 567 | 0.28 | 153 |

Table 30: DF and EFLH Values for Houston (Climate Zone 3)

| Building Type | Principal Building Activity | Package and Split DX |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |
|  |  | DFC | EFLHC | DFC | EFLHC | DFH | EFLHH |
| Data Center | Data Center | 1.05 | 4,022 | 1.05 | 4,022 | -- | -- |
| Education | College/University | 0.98 | 1,843 | 0.98 | 1,843 | -- | -- |
|  | Primary School | 0.88 | 1,443 | 0.88 | 1,443 | 0.50 | 239 |
|  | Secondary School | 0.98 | 1,253 | 0.98 | 1,253 | 0.54 | 293 |
| Food Sales | Convenience | 1.03 | 2,142 | 1.03 | 2,142 | -- | -- |
|  | Supermarket | 0.60 | 744 | 0.60 | 744 | -- | -- |
| Food Service | Full-service Restaurant | 1.05 | 2,135 | 1.05 | 2,135 | 0.44 | 429 |
|  | 24-hour Full-service | 1.06 | 2,426 | 1.06 | 2,426 | 0.44 | 559 |
|  | Quick-service Restaurant | 1.03 | 1,853 | 1.03 | 1,853 | 0.51 | 372 |
|  | 24-hour Quick-service | 1.05 | 2,059 | 1.05 | 2,059 | 0.50 | 483 |
| Healthcare | Hospital | 0.90 | 3,490 | 0.90 | 3,490 | -- | -- |
|  | Outpatient Healthcare | 0.80 | 2,844 | 0.80 | 2,844 | 0.29 | 196 |
| Large Multifamily | Midrise Apartment | 1.00 | 2,031 | 1.00 | 2,031 | -- | -- |
| Lodging | Large Hotel | 0.70 | 2,531 | 0.70 | 2,531 | 0.33 | 250 |
|  | Nursing Home | 1.00 | 2,063 | 1.00 | 2,063 | -- | -- |
|  | Small Hotel/Motel | 0.65 | 2,316 | 0.65 | 2,316 | 0.19 | 147 |
| Mercantile | Stand-alone Retail | 0.95 | 1,399 | 0.95 | 1,399 | 0.43 | 204 |
|  | 24-hour Stand-alone Retail | 0.97 | 1,804 | 0.97 | 1,804 | 0.41 | 374 |
|  | Strip Mall | 0.92 | 1,330 | 0.92 | 1,330 | 0.42 | 218 |
| Office | Large Office | 1.00 | 2,619 | 1.00 | 2,619 | -- | -- |
|  | Medium Office | 0.75 | 1,387 | 0.75 | 1,387 | 0.42 | 149 |
|  | Small Office | 0.88 | 1,338 | 0.88 | 1,338 | 0.28 | 69 |
| Public Assembly | Public Assembly | 0.88 | 1,940 | 0.88 | 1,940 | -- | -- |
| Religious Worship | Religious Worship | 0.65 | 576 | 0.65 | 576 | -- | -- |
| Service | Service | 1.05 | 1,653 | 1.05 | 1,653 | -- | -- |
| Warehouse | Warehouse | 0.84 | 633 | 0.84 | 633 | -- | -- |
| Other | Other | 0.60 | 576 | 0.60 | 576 | 0.19 | 69 |

Table 31: DF and EFLH Values for Corpus Christi (Climate Zone 4)

| Building Type | Principal Building Activity | Package and Split DX |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |
|  |  | DFC | EFLHC | DFC | EFLHC | DFH | EFLHH |
| Data Center | Data Center | 0.97 | 4,499 | 0.97 | 4,499 | -- | -- |
| Education | College/University | 0.96 | 2,211 | 0.96 | 2,211 | -- | -- |
|  | Primary School | 0.88 | 1,680 | 0.88 | 1,680 | 0.30 | 156 |
|  | Secondary School | 0.96 | 1,503 | 0.96 | 1,503 | 0.35 | 196 |
| Food Sales | Convenience | 0.94 | 2,510 | 0.94 | 2,510 | -- | -- |
|  | Supermarket | 0.54 | 894 | 0.54 | 894 | -- | -- |
| Food Service | Full-service Restaurant | 0.98 | 2,530 | 0.98 | 2,530 | 0.35 | 292 |
|  | 24-hour Full-service | 0.97 | 2,897 | 0.97 | 2,897 | 0.36 | 377 |
|  | Quick-service Restaurant | 0.94 | 2,172 | 0.94 | 2,172 | 0.34 | 232 |
|  | 24-hour Quick-service | 0.93 | 2,440 | 0.93 | 2,440 | 0.34 | 296 |
| Healthcare | Hospital | 0.86 | 3,819 | 0.86 | 3,819 | -- | -- |
|  | Outpatient Healthcare | 0.78 | 3,092 | 0.78 | 3,092 | 0.08 | 122 |
| Large Multifamily | Midrise Apartment | 0.92 | 2,236 | 0.92 | 2,236 | -- | -- |
| Lodging | Large Hotel | 0.65 | 2,981 | 0.65 | 2,981 | 0.21 | 131 |
|  | Nursing Home | 0.92 | 2,271 | 0.92 | 2,271 | -- | -- |
|  | Small Hotel/Motel | 0.58 | 2,530 | 0.58 | 2,530 | 0.10 | 82 |
| Mercantile | Stand-alone Retail | 0.84 | 1,582 | 0.84 | 1,582 | 0.22 | 131 |
|  | 24-hour Stand-alone Retail | 0.86 | 2,118 | 0.86 | 2,118 | 0.25 | 255 |
|  | Strip Mall | 0.82 | 1,510 | 0.82 | 1,510 | 0.21 | 141 |
| Office | Large Office | 0.91 | 2,778 | 0.91 | 2,778 | -- | -- |
|  | Medium Office | 0.66 | 1,523 | 0.66 | 1,523 | 0.24 | 83 |
|  | Small Office | 0.80 | 1,504 | 0.80 | 1,504 | 0.14 | 39 |
| Public Assembly | Public Assembly | 0.88 | 2,259 | 0.88 | 2,259 | -- | -- |
| Religious Worship | Religious Worship | 0.58 | 629 | 0.58 | 629 | -- | -- |
| Service | Service | 0.98 | 1,959 | 0.98 | 1,959 | -- | -- |
| Warehouse | Warehouse | 0.73 | 665 | 0.73 | 665 | -- | -- |
| Other | Other | 0.54 | 629 | 0.54 | 629 | 0.08 | 39 |

Table 32: DF and EFLH Values for El Paso (Climate Zone 5)

| Building Type | Principal Building Activity | Package and Split DX |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |
|  |  | DFC | EFLHC | DFC | EFLHC | DFH | EFLHH |
| Data Center | Data Center | 0.88 | 2,547 | 0.88 | 2,547 | -- | -- |
| Education | College/University | 0.87 | 1,092 | 0.87 | 1,092 | -- |  |
|  | Primary School | 0.91 | 996 | 0.91 | 996 | 0.37 | 408 |
|  | Secondary School | 0.87 | 742 | 0.87 | 742 | 0.43 | 431 |
| Food Sales | Convenience | 0.76 | 1,251 | 0.76 | 1,251 | -- |  |
|  | Supermarket | 0.38 | 347 | 0.38 | 347 | -- | -- |
| Food Service | Full-service Restaurant | 0.76 | 1,276 | 0.76 | 1,276 | 0.28 | 613 |
|  | 24-hour Full-service | 0.74 | 1,413 | 0.74 | 1,413 | 0.27 | 809 |
|  | Quick-service Restaurant | 0.76 | 1,082 | 0.76 | 1,082 | 0.26 | 522 |
|  | 24-hour Quick-service | 0.77 | 1,171 | 0.77 | 1,171 | 0.26 | 697 |
| Healthcare | Hospital | 0.81 | 2,555 | 0.81 | 2,555 | -- | -- |
|  | Outpatient Healthcare | 0.81 | 2,377 | 0.81 | 2,377 | 0.04 | 320 |
| Large Multifamily | Midrise Apartment | 0.88 | 1,209 | 0.88 | 1,209 | -- | -- |
| Lodging | Large Hotel | 0.63 | 1,701 | 0.63 | 1,701 | 0.21 | 440 |
|  | Nursing Home | 0.88 | 1,228 | 0.88 | 1,228 | -- |  |
|  | Small Hotel/Motel | 0.63 | 1,921 | 0.63 | 1,921 | 0.06 | 185 |
| Mercantile | Stand-alone Retail | 0.80 | 904 | 0.80 | 904 | 0.26 | 384 |
|  | 24-hour Stand-alone Retail | 0.86 | 1,228 | 0.86 | 1,228 | 0.28 | 808 |
|  | Strip Mall | 0.83 | 931 | 0.83 | 931 | 0.27 | 448 |
| Office | Large Office | 0.98 | 2,423 | 0.98 | 2,423 | -- | -- |
|  | Medium Office | 0.77 | 1,173 | 0.77 | 1,173 | 0.27 | 256 |
|  | Small Office | 0.84 | 1,037 | 0.84 | 1,037 | 0.15 | 146 |
| Public Assembly | Public Assembly | 0.91 | 1,339 | 0.91 | 1,339 | -- | -- |
| Religious Worship | Religious Worship | 0.63 | 478 | 0.63 | 478 | -- | -- |
| Service | Service | 0.76 | 988 | 0.76 | 988 | -- | -- |
| Warehouse | Warehouse | 0.75 | 324 | 0.75 | 324 | -- | -- |
| Other | Other | 0.38 | 324 | 0.38 | 324 | 0.04 | 146 |

##### Claimed Peak Demand Savings

A summer peak period value is used for this measure. Refer to Volume 1, Section 4 for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

The EUL and RULs for this HVAC equipment are provided below. The reader should refer to the definitions of effective useful life and remaining useful life in the glossary in Volume 1 for guidance on how to determine the decision type for system installations.

Effective Useful Life (EUL)

The EUL for split and packaged air conditioners and heat pumps is 15 years.

Remaining Useful Life (RUL)

The RUL of replaced systems is provided according to system age in Table 33. If individual system components were installed at different times, use the condenser age as a proxy for the entire system. As previously noted, for ER units of unknown age, a default value of 17 years should be used. Default RUL may be used exclusively if applied consistently for all projects. Otherwise, the default should only be used when a project is reported and documented as having a nameplate that is illegible. Both the RUL and EUL are needed to estimate savings for early retirement projects for two distinct periods: The ER period (RUL) and the ROB period (EUL-RUL). The calculations for early retirement projects are extensive, and as such, are provided in Appendix A.

Table 33: Remaining Useful Life Early Retirement Systems

| Age of Replaced System (Years) | Split/Packaged AC/HP Systems RUL (Years) | Age of Replaced System (Years) | Split/Packaged AC/HP Systems RUL (Years) |
| --- | --- | --- | --- |
| 1 | 14.0 | 10 | 5.7 |
| 2 | 13.0 | 11 | 5.0 |
| 3 | 12.0 | 12 | 4.4 |
| 4 | 11.0 | 13 | 3.8 |
| 5 | 10.0 | 14 | 3.3 |
| 6 | 9.1 | 15 | 2.8 |
| 7 | 8.2 | 16 | 2.0 |
| 8 | 7.3 | 17 | 1.0 |
| 9 | 6.5 | 18 | 0.0 |

#### Program Tracking Data and Evaluation Requirements

The below list of primary inputs and contextual data is recommended to be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Decision/action type: ER, ROB, NC, system type conversion

- Building type

- Climate zone

- Baseline number of units

- Baseline equipment type

- Baseline rated cooling and heating capacities

- For ER only: Baseline age and method of determination (e.g., nameplate, blueprints, customer reported, not available)

- For ER only: Photograph of retired unit nameplate demonstrating model number, serial number, and manufacturer if blueprints are not provided; if photograph of nameplate is unavailable or not legible, provide a photo and/or description documenting the reason why the nameplate photo was unobtainable (alternate forms of documentation can be approved at the evaluator’s discretion)

- Installed number of units

- Installed equipment type

- Installed rated cooling and heating capacities

- Installed cooling and heating efficiency ratings

- Installed manufacturer and model

- Installed unit AHRI/DOE CCMS certificate or reference number

- For retrofit only: Proof of purchase: invoice showing model number; photos of the model number on product packaging or installed unit(s); OR an evaluator pre-approved inspection approach

- For new construction only: Proof of purchase: invoice showing model number; photos of the model number on product packaging or installed unit(s); as-built design drawings; HVAC specifications package that provides detailed make and model information on installed unit(s); OR an evaluator pre-approved inspection approach

- For Other building types only: A description of the actual building type, the primary business activity, the business hours, and the HVAC schedule

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 36779—Provides EUL for HVAC equipment.

- PUCT Docket 40083—Provides incorporation of early retirement savings for existing commercial HVAC SOP designs and updates for baseline equipment efficiency levels for ROB and new construction projects involving package and split systems.

- PUCT Docket 40885—Provides a petition to revise deemed savings values for commercial HVAC replacement measures. Items covered by this petition include the following:

- Updated baseline efficiencies use for estimating deemed savings for commercial PTAC/PTHP’s, room air conditioners, and chilled water systems.

- Approved estimates of RUL of working chilled water systems.

- Updated demand and energy coefficients for all commercial HVAC systems.

- Updated EUL of centrifugal chilled water systems installed in ROB or new construction projects.

- Provide a method for utilizing the early retirement concept developed in the petition in Docket No. 40083 for packaged and split DX systems and applied to chilled water systems when the age of the system being replaced cannot be ascertained.

- PUCT Docket 41070—Provides energy and demand savings coefficients for an additional climate zone, El Paso, Texas. Prior to this filing, savings for the Dallas-Fort Worth area were used for El Paso, but Dallas-Fort Worth has a colder winter, somewhat more moderate summer, more sunshine, and less precipitation than El Paso.

- PUCT Docket 43681—Updated the approach for calculating early replacement energy and demand savings using a Net Present Value (NPV) method. Documented in Appendix A

##### Relevant Standards and Reference Sources

- ANSI/ASHRAE/IES Standard 90.1-2010. Energy Standard for Buildings Except Low-Rise Residential Buildings. Table 6.8.1A through Table 6.8.1D.

- ANSI/ASHRAE/IES Standard 90.1-2010. Energy Standard for Buildings Except Low-Rise Residential Buildings. Table 6.8.1-1 and Table 6.8.1-2.

- 2015 International Energy Conservation Code. Table C403.2.3(1) and Table C403.2.3(2).

- Code of Federal Regulations. Title 10. Part 431—Energy Efficiency Program for Certain Commercial and Industrial Equipment. https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=75&action=viewlive.

### HVAC Chillers Measure Overview

TRM Measure ID: NR-HV-CH

Market Sector: Commercial

Measure Category: HVAC

Applicable Building Types: See Table 47 through Table 51.

Fuels Affected: Electricity

Decision/Action Type: Replace-on-burnout, early retirement, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Energy modeling, engineering algorithms, and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of chillers. This document covers assumptions made for baseline equipment efficiencies for early retirement (ER) based on the age of the replaced equipment and replace-on-burnout (ROB) and new construction (NC) situations based on efficiency standards.

Savings calculations incorporate the use of both full-load and part-load efficiency values. For ER, the actual age of the baseline system should be determined from the equipment nameplate or other physical documentation, whenever possible. Default values are provided for when the actual age of the unit is unknown. Minimum efficiencies are defined in units of kW/ton, the ratio of input power in kW to the cooling capacity in tons, or EER, the ratio of cooling capacity in Btu/h to input power in Watts.

Two paths are currently available for chiller compliance through the IECC and ASHRAE rating standards. Path A requires higher efficiency ratings for full-load operation, with lower ratings for part-load efficiency, and is most applicable to units that are expected to operate at or near full-load conditions. Path B requires higher efficiency ratings for part-load operation, with lower ratings for full-load efficiency, and is most applicable to units that are expected to operate primarily at part-load conditions with variable frequency drives. Either Path can be used for compliance on any particular chiller, but the chiller must meet the minimum requirements for both full and part-load efficiency that are set forth in the following sections.

Applicable efficient measure types include:

- Compressor types: centrifugal or positive-displacement (screw, scroll, or reciprocating)

- Condenser/heat rejection type: air-cooled or water-cooled system type conversions. Retrofits involving a change from a chiller-based system to a packaged/split system are also covered under this measure. If this type of retrofit is performed, reference the tables from the split/single packaged air conditioners and heat pumps measure.

- Chiller type conversions: from an air-cooled chiller system to a water-cooled chiller system is also addressed in this measure. An additional adjustment is made to the basic chiller savings to account for the auxiliary equipment associated with a water-cooled chiller.

##### Eligibility Criteria

For a measure to be eligible for this deemed savings approach, the following conditions must be met:

- The existing and proposed cooling equipment is electric.

- The building falls into one of the categories listed in Table 47 through Table 51. Building type descriptions and examples are provided in Table 26 and Table 27.

- For early retirement projects: ER projects involve the replacement of a working system before natural burnout. Additionally, the ER approach cannot be used for projects involving a renovation where a major structural change or internal space remodel has occurred. A ROB approach should be used for these scenarios.

If one of these conditions is not met, the deemed savings approach cannot be used, and the Simplified M&V Methodology or the Full M&V Methodology must be used.

Manufacturer datasheets for installed equipment or documentation of AHRI or DOE CCMS certification must be provided.,

##### Baseline Condition

Early Retirement

Early retirement systems involve the replacement of a working system prior to natural burnout. The early retirement baseline cannot be used for projects involving a renovation where a major structural change or internal space remodel has occurred.

Two baseline condition efficiency values are required for an ER scenario, one for the ER (RUL) period and one for the ROB (EUL-RUL) period. For the ROB period, the baseline efficiency is the same as for a ROB/NC scenario. For the ER period, the baseline efficiency should be estimated using the values from Table 34 through Table 45 according to the capacity, chiller type, and age (based on year manufactured) of the replaced system.  When the chiller age can be determined (from a nameplate, building prints, equipment inventory list, etc.), the baseline efficiency levels provided in Table 34 through Table 45 should be used. When the system age is unknown, assume 20 years for non-centrifugal chillers and 25 years for centrifugal chillers. A default RUL may be used exclusively if applied consistently for all projects. Otherwise, the default should only be used when a project is reported and documented as having a nameplate that is illegible.

ER baseline efficiency values represent the code-specified efficiency in effect at the time the chiller was installed. Prior to 2002, code-specified efficiencies from ASHRAE 90.1-1989 were in effect. Code-specified efficiencies increased in 2002, approximating the effective date of ASHRAE 90.1-1999, which went into effect on October 29, 2001. Code-specified efficiencies increased again in 2010 and 2018, coinciding with the IECC 2009 and IECC 2015 code increases.

Code-specified efficiencies in effect prior to 2002 were given in COP and have been converted to EER and kW/ton in the tables below using EER = COP x 3.412 and kW/ton = 3.516 ÷ COP. Values in the “< 2001” row of the following tables have been converted and are expressed in italics.

PUCT Docket 40885 provided baseline efficiencies for chillers replaced via early retirement programs and included a category for 1990-2001. However, the common practice for energy efficiency programs in Texas is to allow systems older than 1990 to use the same baseline efficiencies as those listed for 1990-2001. This practice is reflected in the baseline efficiency tables, by showing the Year Installed as ≤ 2001 rather than 1990-2001.

ER Baseline: Air-cooled Chillers

Table 34: ER Baseline Full-load Efficiency of All Path A Air-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [EER] | ≥ 75 to 150 tons [EER] | ≥ 150 to 300 tons [EER] | ≥ 300 to 600 tons [EER] | ≥ 600 tons [EER] |
| --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 9.212 | 9.212 | 8.530 | 8.530 | 8.530 |
| 2002–2009 | 9.562 | 9.562 | 9.562 | 9.562 | 9.562 |
| 2010–2017 | 9.562 | 9.562 | 9.562 | 9.562 | 9.562 |
| ≥ 2018 | 10.100 | 10.100 | 10.100 | 10.100 | 10.100 |

Table 35: ER Baseline Full-load Efficiency of All Path B Air-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [EER] | ≥ 75 to 150 tons [EER] | ≥ 150 to 300 tons [EER] | ≥ 300 to 600 tons [EER] | ≥ 600 tons [EER] |
| --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 9.212 | 9.212 | 8.530 | 8.530 | 8.530 |
| 2002–2009 | 9.562 | 9.562 | 9.562 | 9.562 | 9.562 |
| 2010–2017 | 9.562 | 9.562 | 9.562 | 9.562 | 9.562 |
| ≥ 2018 | 9.700 | 9.700 | 9.700 | 9.700 | 9.700 |

Table 36: ER Baseline Part-load Efficiency (IPLV) of All Path A Air-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [EER] | ≥ 75 to 150 tons [EER] | ≥ 150 to 300 tons [EER] | ≥ 300 to 600 tons [EER] | ≥ 600 tons [EER] |
| --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 9.554 | 9.554 | 8.530 | 8.530 | 8.530 |
| 2002–2009 | 10.416 | 10.416 | 10.416 | 10.416 | 10.416 |
| 2010–2017 | 12.500 | 12.500 | 12.500 | 12.500 | 12.500 |
| ≥ 2018 | 13.700 | 13.700 | 14.000 | 14.000 | 14.000 |

Table 37: ER Baseline Part-load Efficiency (IPLV) of All Path B Air-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [EER] | ≥ 75 to 150 tons [EER] | ≥ 150 to 300 tons [EER] | ≥ 300 to 600 tons [EER] | ≥ 600 tons [EER] |
| --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 9.554 | 9.554 | 8.530 | 8.530 | 8.530 |
| 2002–2009 | 10.416 | 10.416 | 10.416 | 10.416 | 10.416 |
| 2010–2017 | 12.500 | 12.500 | 12.500 | 12.500 | 12.500 |
| ≥ 2018 | 15.800 | 15.800 | 16.100 | 16.100 | 16.100 |

ER Baseline: Centrifugal Water-cooled Chillers

Table 38: ER Baseline Full-load Efficiency of Centrifugal Path A Water-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [kW/ton] | ≥ 75 to 150 tons [kW/ton] | ≥ 150 to 300 tons [kW/ton] | ≥ 300 to 400 tons [kW/ton] | ≥ 400 to < 600 tons [kW/ton] | ≥ 600 tons [kW/ton] |
| --- | --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 0.925 | 0.925 | 0.837 | 0.748 | 0.748 | 0.748 |
| 2002–2009 | 0.703 | 0.703 | 0.634 | 0.576 | 0.576 | 0.576 |
| 2010–2017 | 0.634 | 0.634 | 0.634 | 0.576 | 0.576 | 0.570 |
| ≥ 2018 | 0.610 | 0.610 | 0.610 | 0.560 | 0.560 | 0.560 |

Table 39: ER Baseline Full-load Efficiency of Centrifugal Path B Water-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [kW/ton] | ≥ 75 to 150 tons [kW/ton] | ≥ 150 to 300 tons [kW/ton] | ≥ 300 to 400 tons [kW/ton] | ≥ 400 to < 600 tons [kW/ton] | ≥ 600 tons [kW/ton] |
| --- | --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 0.925 | 0.925 | 0.837 | 0.748 | 0.748 | 0.748 |
| 2002–2009 | 0.703 | 0.703 | 0.634 | 0.576 | 0.576 | 0.576 |
| 2010–2017 | 0.639 | 0.639 | 0.639 | 0.600 | 0.600 | 0.590 |
| ≥ 2018 | 0.695 | 0.695 | 0.635 | 0.595 | 0.585 | 0.585 |

Table 40: ER Baseline Part-load Efficiency (IPLV) of Centrifugal Path A Water-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [kW/ton] | ≥ 75 to 150 tons [kW/ton] | ≥ 150 to 300 tons [kW/ton] | ≥ 300 to 400 tons [kW/ton] | ≥ 400 to < 600 tons [kW/ton] | ≥ 600 tons [kW/ton] |
| --- | --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 0.902 | 0.902 | 0.781 | 0.733 | 0.733 | 0.733 |
| 2002–2009 | 0.670 | 0.670 | 0.596 | 0.549 | 0.549 | 0.549 |
| 2010–2017 | 0.596 | 0.596 | 0.596 | 0.549 | 0.549 | 0.539 |
| ≥ 2018 | 0.550 | 0.550 | 0.550 | 0.520 | 0.500 | 0.500 |

Table 41: ER Baseline Part-load Efficiency (IPLV) of Centrifugal Path B Water-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [kW/ton] | ≥ 75 to 150 tons [kW/ton] | ≥ 150 to 300 tons [kW/ton] | ≥ 300 to 400 tons [kW/ton] | ≥ 400 to < 600 tons [kW/ton] | ≥ 600 tons [kW/ton] |
| --- | --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 0.902 | 0.902 | 0.781 | 0.733 | 0.733 | 0.733 |
| 2002–2009 | 0.670 | 0.670 | 0.596 | 0.549 | 0.549 | 0.549 |
| 2010–2017 | 0.450 | 0.450 | 0.450 | 0.400 | 0.400 | 0.400 |
| ≥ 2018 | 0.440 | 0.440 | 0.400 | 0.390 | 0.380 | 0.380 |

ER Baseline: Positive-Displacement (Screw, Scroll, or Reciprocating) Water-cooled Chillers

Table 42: ER Baseline Full-load Efficiency of Screw/Scroll/Recip. Path A Water-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [kW/ton] | ≥ 75 to <150 tons [kW/ton] | ≥ 150 to <300 tons [kW/ton] | ≥ 300 to <600 tons [kW/ton] | ≥ 600 tons [kW/ton] |
| --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 0.925 | 0.925 | 0.837 | 0.748 | 0.748 |
| 2002–2009 | 0.790 | 0.790 | 0.718 | 0.639 | 0.639 |
| 2010–2017 | 0.780 | 0.775 | 0.680 | 0.620 | 0.620 |
| ≥ 2018 | 0.750 | 0.720 | 0.660 | 0.610 | 0.560 |

Table 43: ER Baseline Full-load Efficiency of Screw/Scroll/Recip. Path B Water-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [kW/ton] | ≥ 75 to <150 tons [kW/ton] | ≥ 150 to <300 tons [kW/ton] | ≥ 300 to <600 tons [kW/ton] | ≥ 600 tons [kW/ton] |
| --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 0.925 | 0.925 | 0.837 | 0.748 | 0.748 |
| 2002–2009 | 0.790 | 0.790 | 0.718 | 0.639 | 0.639 |
| 2010–2017 | 0.800 | 0.790 | 0.718 | 0.639 | 0.639 |
| ≥ 2018 | 0.780 | 0.750 | 0.680 | 0.625 | 0.585 |

Table 44: ER Baseline Part-load Efficiency (IPLV) of Screw/Scroll/Recip. Path A Water-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [kW/ton] | ≥ 75 to 150 tons [kW/ton] | ≥ 150 to 300 tons [kW/ton] | ≥ 300 to 600 tons [kW/ton] | ≥ 600 tons [kW/ton] |
| --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 0.902 | 0.902 | 0.781 | 0.733 | 0.733 |
| 2002–2009 | 0.676 | 0.676 | 0.628 | 0.572 | 0.572 |
| 2010–2017 | 0.630 | 0.615 | 0.580 | 0.540 | 0.540 |
| ≥ 2018 | 0.600 | 0.560 | 0.540 | 0.520 | 0.500 |

Table 45: ER Baseline Part-load Efficiency (IPLV) of Screw/Scroll/Recip. Path B Water-cooled Chillers

| Year Installed (Replaced System) | < 75 tons [kW/ton] | ≥ 75 to 150 tons [kW/ton] | ≥ 150 to 300 tons [kW/ton] | ≥ 300 to 600 tons [kW/ton] | ≥ 600 tons [kW/ton] |
| --- | --- | --- | --- | --- | --- |
| ≤ 2001 | 0.902 | 0.902 | 0.781 | 0.733 | 0.733 |
| 2002–2009 | 0.676 | 0.676 | 0.628 | 0.572 | 0.572 |
| 2010–2017 | 0.600 | 0.586 | 0.540 | 0.490 | 0.490 |
| ≥ 2018 | 0.500 | 0.490 | 0.440 | 0.410 | 0.380 |

Replace-on-Burnout and New Construction

New baseline efficiency levels for chillers are provided in Table 46, which includes both full load and integrated part load value (IPLV) ratings. The IPLV accounts for chiller efficiency at part-load operation for a given duty cycle. These baseline efficiency levels reference standard ASHRAE 90.1-2010. This standard contains two paths for compliance, Path A or Path B. According to ASHRAE 90.1-2007 Addenda M, Path A is intended for applications where significant operating time is expected at full-load conditions, while Path B is an alternative set of efficiency levels for chillers intended for applications where significant time is spent at part-load operation (such as with a VSD chiller). Path A chillers are eligible to claim savings using the full-load efficiency conditions in the energy and demand savings algorithms. Path B chillers are eligible to claim savings using the Path B chiller part-load baseline efficiencies with the demand and energy coefficients defined in this measure.

Table 46: Baseline Efficiencies for ROB and NC Air-cooled and Water-cooled Chillers

| System Type [Efficiency Units] |  | Efficiency Type | Capacity [Tons] | Path A |  | Path B |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Full-load | IPLV | Full-load | IPLV |
| Air-cooled Chiller |  | EER | < 150 | ≥ 10.100 | ≥ 13.700 | ≥ 9.700 | ≥ 15.800 |
|  |  |  | ≥ 150 | ≥ 10.100 | ≥ 14.000 | ≥ 9.700 | ≥ 16.100 |
| Water-cooled Chiller | Screw/ Scroll/ Recip. | kW/ton | < 75 | ≤ 0.750 | ≤ 0.600 | ≤ 0.780 | ≤ 0.500 |
|  |  |  | ≥ 75 and < 150 | ≤ 0.720 | ≤ 0.560 | ≤ 0.750 | ≤ 0.490 |
|  |  |  | ≥ 150 and < 300 | ≤ 0.660 | ≤ 0.540 | ≤ 0.680 | ≤ 0.440 |
|  |  |  | ≥ 300 and < 600 | ≤ 0.610 | ≤ 0.520 | ≤ 0.625 | ≤ 0.410 |
|  |  |  | ≥ 600 | ≤ 0.560 | ≤ 0.500 | ≤ 0.585 | ≤ 0.380 |
|  | Centrifugal |  | < 150 | ≤ 0.610 | ≤ 0.550 | ≤ 0.695 | ≤ 0.440 |
|  |  |  | ≥ 150 and < 300 | ≤ 0.610 | ≤ 0.550 | ≤ 0.635 | ≤ 0.400 |
|  |  |  | ≥ 300 and < 400 | ≤ 0.560 | ≤ 0.520 | ≤ 0.595 | ≤ 0.390 |
|  |  |  | ≥ 400 | ≤ 0.560 | ≤ 0.500 | ≤ 0.585 | ≤ 0.380 |

##### High-efficiency Condition

Chillers must exceed the minimum efficiencies specified in Table 46 for either Path A or Path B. For whichever path is used, the chiller must exceed the minimum baseline efficiency for both full-load and IPLV of that path to qualify. Additional conditions for replace-on-burnout, early retirement, and new construction are as follows:

New Construction and Replace-on-Burnout

This scenario includes chillers used for new construction and retrofit/replacements that are not covered by early retirement, such as units that are replaced after natural failure.

Early Retirement

The high-efficiency retrofits must meet the following criteria:

- For early retirement projects only, the installed equipment cooling capacity must be within 80 percent to 120 percent of the replaced electric cooling capacity. For scenarios involving the replacement of a combination of systems by an alternate combination of systems of varying capacities, early retirement savings can still be claimed if the overall pre- and post-capacities for the total combination of systems are within ± 20%. In these cases, a custom calculation should be performed to establish the following weighted savings factors to be applied over the early retirement portion of the savings calculation: manufacturer year, EUL, RUL, path A/B full and part-load baseline efficiency, demand factor, and EFLH. These factors should be weighted based on contribution to overall capacity.

- No additional measures are being installed that directly affect the operation of the cooling equipment (e.g., control sequences, cooling towers, and condensers).

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Path A and B Air and Water-cooled Chillers

Peak Demand [kWSavings]=CapC,pre×ηbaseline-CapC,post×ηinstalled×DF

Equation 23

Energy Savings [kWhSavings]=CapC,pre×ηbaseline-CapC,post×ηinstalled×EFLHC

Equation 24

Where:

CapC,pre 	=	For ER, rated equipment cooling capacity of the existing equipment at AHRI standard conditions; for ROB & NC, rated equipment cooling capacity of the new equipment at AHRI standard conditions [tons]

CapC,post	=	Rated equipment cooling capacity of the newly installed equipment at AHRI standard conditions [tons]

ηbaseline	= 	Efficiency of existing equipment (ER) or standard equipment (ROB/NC) [kW/ton] – Default values, based on system type, are given in Table 34 through Table 46. For efficiencies given in EER instead of kW/ton, convert to kW/ton using Equation 25. [kW/ton]

ηinstalled	=	Rated efficiency of the newly installed equipment – Must exceed efficiency standards, shown in Table 46. For efficiencies given in EER instead of kW/ton, convert to kW/ton using Equation 25. [kW/ton]

Note: Use full-load efficiency (kW/ton) for kW demand savings calculations and part-load efficiency (IPLV) for kWh energy savings calculations.

kWTon=12EER

Equation 25

DF	=	Summer peak demand factor for appropriate climate zone, building type, and equipment type (Table 47 through Table 51)

EFLHC	=	Cooling equivalent full-load hours for appropriate climate zone, building type, and equipment type [hours] (Table 47 through Table 51)

Air-to Water-cooled Replacement: Adjustments for Auxiliary Equipment

The equipment efficiency for an air-cooled chiller includes condenser fans, but the equipment efficiency for a water-cooled chiller does not include the condenser water pump and cooling tower (auxiliary equipment). Therefore, when an air-cooled chiller is replaced with a water-cooled chiller, the savings must be reduced to account for the impact of the water-cooled system’s additional equipment. This type of retrofit is only applicable for ER situations. The following equations are used:

kWadjust=HPCW pump+HPCT fan×0.7460.86×0.80

Equation 26

kWhadjust=kW×8,760

Equation 27

Where:

HPCW pump 	=	Horsepower of the condenser water pump

HPCT fan	=	Horsepower of the cooling tower fan

0.746	=	Conversion from HP to kW [kW/HP]

0.86	=	Assumed equipment efficiency

0.80	=	Assumed load factor

8,760	=	Annual run-time hours

The energy and demand of the condenser water pump and cooling tower fans are subtracted from the final savings, to reach the net savings:

kWsavings,net=kWChiller-kWadjust

Equation 28

kWhsavings,net=kWhChiller-kWhadjust

Equation 29

Early Retirement Savings

The first-year savings algorithms in the above equations are used for all HVAC projects, across NC, ROB, and ER projects. However, ER projects require weighted savings calculated over both the ER period and the ROB period, accounting for the EUL and the RUL. The final reported savings for ER projects are not actually a “first-year” savings, but an “average annual savings over the lifetime (EUL) of the measure.” These savings calculations are explained in Appendix A.

Table 47 through Table 51 present the demand and energy coefficients as well as the Part Load Factor. These HVAC coefficients vary by climate zone, building type, and equipment type. A description of the calculation method can be found in Docket No. 40885, Attachment B.

##### Claimed Peak Demand Savings

A summer peak period value is used for this measure. Refer to Volume 1, Section 4 for further details on peak demand savings and methodology.

##### Deemed Energy and Demand Savings Tables

Deemed peak demand factor (DF) and equivalent full-load hour (EFLH) values are presented by building type and climate zone. A description of the building types that are used for HVAC systems is presented in Table 26 and Table 27. These building types are derived from the EIA CBECS study.

Deemed peak demand factor (DF) and equivalent full-load hour (EFLH) values are presented by building type and climate zone for chillers in Table 47 through Table 51. These tables also include an “Other” building type, which can be used for business types that are not explicitly listed. The DF and EFLH values used for Other are the most conservative values from the explicitly listed building types. When Other building type is used, a description of the actual building type, the primary business activity, the business operating hours, and the HVAC schedule must be collected for the project site and stored in the utility tracking data system.

For those combinations of technology, climate zone, and building type where no values are present, a project with that specific combination cannot use the deemed approach. A description of the calculation method can be found in Docket No. 40885, Attachment B.

Table 47: DF and EFLH for Amarillo (Climate Zone 1)

| Building Type | Principal Building Activity | Chiller |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Air Cooled |  | Water Cooled |  |
|  |  | DF | EFLHc | DF | EFLHc |
| Data Center | Data Center | 0.56 | 2,807 | 0.73 | 5,100 |
| Education | College | 0.87 | 1,115 | 0.68 | 1,243 |
|  | Primary School | 0.44 | 576 | 0.53 | 971 |
|  | Secondary School | 0.70 | 802 | 0.58 | 1,772 |
| Healthcare | Hospital | 0.70 | 2,006 | 0.65 | 2,711 |
| Large Multifamily | Midrise Apartment | 0.41 | 421 | 0.50 | 1,098 |
| Lodging | Large Hotel | 0.58 | 1,283 | 0.59 | 1,553 |
|  | Nursing Home | 0.41 | 428 | 0.50 | 1,115 |
| Mercantile | Stand-alone Retail | 0.52 | 489 | 0.54 | 719 |
|  | 24-hour Retail | 0.67 | 681 | 0.62 | 974 |
| Office | Large Office | 0.70 | 1,208 | 0.61 | 1,506 |
| Public Assembly | Public Assembly | 0.44 | 774 | 0.53 | 1,306 |
| Religious Worship | Religious Worship | 0.52 | 294 | 0.54 | 433 |
| Other | Other | 0.41 | 294 | 0.50 | 433 |

Table 48: DF and EFLH for Dallas (Climate Zone 2)

| Building Type | Principal Building Activity | Chiller |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Air Cooled |  | Water Cooled |  |
|  |  | DF | EFLHc | DF | EFLHc |
| Data Center | Data Center | 0.54 | 2,791 | 0.77 | 4,906 |
| Education | College | 0.89 | 1,587 | 0.81 | 1,761 |
|  | Primary School | 0.48 | 726 | 0.60 | 1,412 |
|  | Secondary School | 0.84 | 1,170 | 0.54 | 2,234 |
| Healthcare | Hospital | 0.90 | 2,784 | 0.81 | 3,683 |
| Large Multifamily | Midrise Apartment | 0.68 | 1,060 | 0.66 | 2,053 |
| Lodging | Large Hotel | 0.80 | 2,086 | 0.71 | 2,627 |
|  | Nursing Home | 0.68 | 1,077 | 0.66 | 2,085 |
| Mercantile | Stand-alone Retail | 0.79 | 936 | 0.72 | 1,328 |
|  | 24-hour Retail | 0.89 | 1,307 | 0.79 | 1,975 |
| Office | Large Office | 0.92 | 1,711 | 0.70 | 2,062 |
| Public Assembly | Public Assembly | 0.48 | 976 | 0.60 | 1,898 |
| Religious Worship | Religious Worship | 0.79 | 563 | 0.72 | 799 |
| Other | Other | 0.48 | 563 | 0.54 | 799 |

Table 49: DF and EFLH for Houston (Climate Zone 3)

| Building Type | Principal Building Activity | Chiller |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Air Cooled |  | Water Cooled |  |
|  |  | DF | EFLHc | DF | EFLHc |
| Data Center | Data Center | 0.53 | 2,824 | 0.76 | 5,075 |
| Education | College | 0.80 | 1,858 | 0.84 | 2,099 |
|  | Primary School | 0.45 | 818 | 0.60 | 1,627 |
|  | Secondary School | 0.77 | 1,306 | 0.55 | 2,404 |
| Healthcare | Hospital | 0.85 | 3,116 | 0.79 | 4,171 |
| Large Multifamily | Midrise Apartment | 0.65 | 1,295 | 0.66 | 2,467 |
| Lodging | Large Hotel | 0.71 | 2,499 | 0.73 | 3,201 |
|  | Nursing Home | 0.65 | 1,315 | 0.66 | 2,506 |
| Mercantile | Stand-alone Retail | 0.83 | 1,224 | 0.78 | 1,712 |
|  | 24-hour Retail | 0.80 | 1,513 | 0.74 | 2,427 |
| Office | Large Office | 0.92 | 1,820 | 0.71 | 2,312 |
| Public Assembly | Public Assembly | 0.45 | 1,100 | 0.60 | 2,188 |
| Religious Worship | Religious Worship | 0.83 | 737 | 0.78 | 1,031 |
| Other | Other | 0.45 | 737 | 0.55 | 1,031 |

Table 50: DF and EFLH for Corpus Christi (Climate Zone 4)

| Building Type | Principal Building Activity | Chiller |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Air Cooled |  | Water Cooled |  |
|  |  | DF | EFLHc | DF | EFLHc |
| Data Center | Data Center | 0.48 | 2,881 | 0.77 | 5,266 |
| Education | College | 0.80 | 2,340 | 0.87 | 2,583 |
|  | Primary School | 0.45 | 937 | 0.61 | 1,845 |
|  | Secondary School | 0.68 | 1,503 | 0.55 | 2,577 |
| Healthcare | Hospital | 0.79 | 3,455 | 0.82 | 4,637 |
| Large Multifamily | Midrise Apartment | 0.61 | 1,534 | 0.67 | 2,840 |
| Lodging | Large Hotel | 0.74 | 2,908 | 0.73 | 3,713 |
|  | Nursing Home | 0.61 | 1,558 | 0.67 | 2,884 |
| Mercantile | Stand-alone Retail | 0.75 | 1,394 | 0.76 | 1,953 |
|  | 24-hour Retail | 0.70 | 1,725 | 0.73 | 2,768 |
| Office | Large Office | 0.82 | 2,027 | 0.72 | 2,570 |
| Public Assembly | Public Assembly | 0.45 | 1,260 | 0.61 | 2,481 |
| Religious Worship | Religious Worship | 0.75 | 839 | 0.76 | 1,176 |
| Other | Other | 0.45 | 839 | 0.55 | 1,176 |

Table 51: DF and EFLH for El Paso (Climate Zone 5)

| Building Type | Principal Building Activity | Chiller |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Air Cooled |  | Water Cooled |  |
|  |  | DF | EFLHc | DF | EFLHc |
| Data Center | Data Center | 0.56 | 2,950 | 0.71 | 5,137 |
| Education | College | 0.93 | 1,278 | 0.96 | 1,458 |
|  | Primary School | 0.61 | 751 | 0.53 | 1,113 |
|  | Secondary School | 0.77 | 1,039 | 0.54 | 2,196 |
| Healthcare | Hospital | 0.71 | 2,355 | 0.59 | 2,992 |
| Large Multifamily | Midrise Apartment | 0.56 | 841 | 0.52 | 1,553 |
| Lodging | Large Hotel | 0.63 | 1,815 | 0.58 | 2,038 |
|  | Nursing Home | 0.56 | 854 | 0.52 | 1,577 |
| Mercantile | Stand-alone Retail | 0.64 | 722 | 0.55 | 948 |
|  | 24-hour Retail | 0.61 | 884 | 0.60 | 1,371 |
| Office | Large Office | 0.77 | 1,442 | 0.60 | 1,683 |
| Public Assembly | Public Assembly | 0.61 | 1,010 | 0.53 | 1,496 |
| Religious Worship | Religious Worship | 0.64 | 435 | 0.55 | 571 |
| Other | Other | 0.56 | 435 | 0.52 | 571 |

##### Measure Life and Lifetime Savings

Effective Useful Life (EUL)

The EUL of HVAC equipment is provided below:

- Screw/scroll/reciprocating chillers: 20 years

- Centrifugal chillers: 25 years.

Remaining Useful Life (RUL)

The RUL of replaced systems is provided according to system age in Table 52. As previously noted, for ER units of unknown age, a default value of 21 years for non-centrifugal chillers and 26 years for centrifugal chillers should be used. Default RUL may be used exclusively if applied consistently for all projects. Otherwise, the default should only be used when a project is reported and documented as having a nameplate that is illegible. Both the RUL and EUL are needed to estimate savings for early retirement projects for two distinct periods: The ER period (RUL) and the ROB period (EUL-RUL). The calculations for early retirement projects are extensive, and as such, are provided in Appendix A.

Table 52: Remaining Useful Life of Early Retirement Systems

| Age of Replaced System (years) | Non-Centrifugal Chillers RUL (years) | Centrifugal Chillers RUL (years) |  | Age of Replaced System (years) | Non-Centrifugal Chillers RUL (years) | Centrifugal Chillers RUL (years) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 18.7 | 23.9 |  | 17 | 5.0 | 8.7 |
| 2 | 17.7 | 22.9 |  | 18 | 4.5 | 8.1 |
| 3 | 16.7 | 21.9 |  | 19 | 4.0 | 7.5 |
| 4 | 15.7 | 20.9 |  | 20 | 3.6 | 7.1 |
| 5 | 14.7 | 19.9 |  | 21 | 3.0 | 6.6 |
| 6 | 13.7 | 18.9 |  | 22 | 2.0 | 6.3 |
| 7 | 12.7 | 17.9 |  | 23 | 1.0 | 5.9 |
| 8 | 11.8 | 16.9 |  | 24 | 0.0 | 5.6 |
| 9 | 10.9 | 15.9 |  | 25 | N/A | 5.4 |
| 10 | 10.0 | 14.9 |  | 26 | N/A | 5.0 |
| 11 | 9.1 | 13.9 |  | 27 | N/A | 4.0 |
| 12 | 8.3 | 12.9 |  | 28 | N/A | 3.0 |
| 13 | 7.5 | 11.9 |  | 29 | N/A | 2.0 |
| 14 | 6.8 | 10.9 |  | 30 | N/A | 1.0 |
| 15 | 6.2 | 10.1 |  | 31 | N/A | 0.0 |
| 16 | 5.5 | 9.3 |  |  |  |  |

#### Program Tracking Data and Evaluation Requirements

The below list of primary inputs and contextual data is recommended to be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Decision/action type: ER, ROB, NC, system type conversion

- Building type

- Climate zone

- Baseline number of units

- Baseline equipment type (compressor/condenser type)

- Baseline equipment rated cooling capacity

- For ER only: Baseline age of system and method of determination (e.g., nameplate, blueprints, customer reported, not available)

- For ER only: Photograph of retired unit nameplate demonstrating model number, serial number, and manufacturer if blueprints are not provided; if photograph of nameplate is unavailable or not legible, provide a photo and/or description documenting the reason why the nameplate photo was unobtainable (alternate forms of documentation can be approved at the evaluator’s discretion)

- Installed number of units

- Installed equipment type (compressor/condenser type)

- Installed path (Path A or Path B)

- Installed rated cooling capacity

- Installed cooling efficiency rating

- Installed manufacturer and model

- Installed unit AHRI/DOE CCMS certificate or reference number

- For retrofit only: Proof of purchase: invoice showing model number; photos of the model number on product packaging or installed unit(s); OR an evaluator pre-approved inspection approach

- For new construction only: Proof of purchase: invoice showing model number; photos of the model number on product packaging or installed unit(s); as-built design drawings; HVAC specifications package that provides detailed make and model information on installed unit(s); OR an evaluator pre-approved inspection approach

- For chiller type conversion only: Condenser water pump HP and cooling tower fan HP

- For Other building type only: A description of the actual building type, the primary business activity, the business hours, and the HVAC schedule.

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 30331—Established rules for energy efficiency programs, including factors for principal building activities (PBAs). Most PBA values were superseded by Docket 40885; however some values from this Docket remain valid.

- PUCT Docket 36779—Provides EUL for HVAC equipment.

- PUCT Docket 40083–Provides incorporation of early retirement savings for existing commercial HVAC SOP designs and updates for baseline equipment efficiency levels for ROB and new construction projects involving package and split systems.

- PUCT Docket 40885—Provides a petition to revise deemed savings values for commercial HVAC replacement measures. Items covered by this petition include the following:

- Updated baseline efficiencies use for estimating deemed savings for commercial PTAC/PTHP’s, room air conditioners, and chilled water systems.

- Approved estimates of RUL of working chilled water systems.

- Updated demand and energy coefficients for all commercial HVAC systems.

- Updated EUL of centrifugal chilled water systems installed in ROB or new construction projects.

- Provide a method for utilizing the early retirement concept developed in the petition in Docket No. 40083 for packaged and split DX systems and applied to chilled water systems when the age of the system being replaced cannot be ascertained.

- PUCT Docket 41070—Provides energy and demand savings coefficients for an additional climate zone, El Paso, Texas. Previously these savings were taken from the Dallas-Fort Worth area, which has a colder winter, somewhat more moderate summer, more sunshine, and less precipitation than El Paso.

- PUCT Docket 43681—Updated the approach for calculating early replacement energy and demand savings using a Net Present Value (NPV) method. Documented in Appendix A.

##### Relevant Standards and Reference Sources

- ANSI/ASHRAE/IES Standard 90.1-1989. Energy Standard for Buildings Except Low-Rise Residential Buildings. Table 10-7.

- ANSI/ASHRAE/IES Standard 90.1-2004. Energy Standard for Buildings Except Low-Rise Residential Buildings. Table 6.8.1C.

- ANSI/ASHRAE/IES Standard 90.1-2007. Energy Standard for Buildings Except Low-Rise Residential Buildings, Addendum M. Table 6.8.1C.

- ANSI/ASHRAE/IES Standard 90.1-2010. Energy Standard for Buildings Except Low-Rise Residential Buildings. Table 6.8.1A through Table 6.8.1D.

- 2015 International Energy Conservation Code. Table C403.2.3(7).

### Packaged Terminal Air Conditioners, Heat Pumps, and Room Air Conditioners Measure Overview

TRM Measure ID: NR-HV-PT

Market Sector: Commercial

Measure Category: HVAC

Applicable Building Types: See Table 56 through Table 60

Fuels Affected: Electricity

Decision/Action Type: Replace-on-burnout, early retirement, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Energy modeling, engineering algorithms, and estimates

#### Measure Description

This section presents the deemed savings methodology for the installation of packaged terminal air conditioners (PTAC), packaged terminal heat pumps (PTHP), and room AC (RAC) systems. This document covers assumptions made for baseline equipment efficiencies for early retirement (ER) of PTAC/PTHPs, replace-on-burnout (ROB), and new construction (NC) situations based current and previous on efficiency standards. For ER, the actual age of the baseline system should be determined from the equipment nameplate or other physical documentation whenever possible. Default values are provided for when the actual age of the unit is unknown.

Applicable efficient measure types include:

Packaged Terminal Air Conditioners and Heat Pumps. Both standard and non-standard size equipment types are covered. Standard size refers to equipment with wall sleeve dimensions having an external wall opening greater than or equal to 16 inches high or greater than or equal to 42 inches wide and a cross-sectional area greater than 670 in2. Non-standard size refers to equipment with existing wall sleeve dimensions having an external wall opening of less than 16 inches high or less than 42 inches wide and a cross-sectional area less than 670 in2.

Room Air Conditioners include all equipment configurations covered by the federal appliance standards, including with or without a reverse cycle, louvered or non-louvered sides, casement-only, and casement-slide.

##### Eligibility Criteria

For a measure to be eligible for this deemed savings approach, the following conditions will be met:

- The existing and proposed cooling equipment is electric

- The PTAC, PTHP, or RAC must be the primary cooling source for the space.

- For early retirement PTAC/PTHP projects: ER projects involve the replacement of a working system before natural burnout. Additionally, the ER approach cannot be used for projects involving a renovation where a major structural change or internal space remodel has occurred. A ROB approach should be used for these scenarios.

If one of these conditions is not met, the deemed savings approach cannot be used, and the Simplified M&V Methodology or the Full M&V Methodology must be used.

Manufacturer datasheets for installed equipment or documentation of AHRI or DOE CCMS certification must be provided.,

##### Baseline Condition

Early Retirement for PTAC/PTHP Systems

Early retirement systems involve the replacement of a working system prior to natural burnout. The early retirement baseline cannot be used for projects involving a renovation where a major structural change or internal space remodel has occurred. Two baseline condition efficiency values are required for an ER scenario, one for the ER (RUL) period and one for the ROB (EUL-RUL) period. For the ROB period, the baseline efficiency is the same as for a ROB/NC scenario. For the ER period, the baseline efficiency should be estimated according to the capacity, system type (PTAC or PTHP), and age (based on year manufactured) of the replaced system. When the system age can be determined (from a nameplate, building prints, equipment inventory list, etc.), the baseline efficiency levels provided in Table 53, reflecting ASHRAE Standard 90.1-2001 through 90.1-2007, should be used. PTHPs replacing PTACs with built-in electric resistance heat should use a baseline heating efficiency of 1.0 COP.

When the system age is unknown, assume 15 years. A default RUL may be used exclusively if applied consistently for all projects. Otherwise, the default should only be used when a project is reported and documented as having a nameplate that is illegible.

Existing systems manufactured as of February 2013 are not eligible for early retirement.

Table 53: ER Baseline Efficiency Levels for Standard Size PTAC/PTHP Units

| Equipment | Cooling Capacity [Btuh] | Baseline Cooling Efficiency [EER] | Baseline Heating Efficiency [COP] (No Built-in Resistance Heat) | Baseline Heating Efficiency [COP] (With Built-in Resistance Heat) |
| --- | --- | --- | --- | --- |
| PTAC | < 7,000 | 11.0 | -- | 1.0 |
|  | 7,000-15,000 | 12.5-0.213×Cap/1000 |  |  |
|  | > 15,000 | 9.3 |  |  |
| PTHP | < 7,000 | 10.8 | 3.0 | -- |
|  | 7,000-15,000 | 12.3-0.213×Cap/1000 | 3.2-0.026×Cap/1000 |  |
|  | > 15,000 | 9.1 | 2.8 |  |

Replace-on-Burnout and New Construction

Table 54 provides minimum efficiency standards for PTAC/PTHP units and reflects the federal standards for packaged terminal air conditioners and heat pumps effective February 2013 and reflected in 10 CFR 431.

Table 54: Minimum Efficiency Levels for PTAC/PTHP ROB and NC Units,

| Equipment | Category | Cooling Capacity [Btuh] | Minimum Cooling Efficiency [EER] | Minimum Heating Efficiency [COP] |
| --- | --- | --- | --- | --- |
| PTAC | Standard Size | < 7,000 | 11.9 | -- |
|  |  | 7,000-15,000 | 14.0-0.300×Cap/1000 | -- |
|  |  | > 15,000 | 9.5 | -- |
|  | Non-Standard Size | < 7,000 | 9.4 | -- |
|  |  | 7,000-15,000 | 10.9-0.213×Cap/1000 | -- |
|  |  | > 15,000 | 7.7 | -- |
| PTHP | Standard Size | < 7,000 | 11.9 | 3.3 |
|  |  | 7,000-15,000 | 14.0-0.300×Cap/1000 | 3.7-0.052×Cap/1000 |
|  |  | > 15,000 | 9.5 | 2.9 |
|  | Non-Standard Size | < 7,000 | 9.3 | 2.7 |
|  |  | 7,000-15,000 | 10.8-0.213×Cap/1000 | 2.9-0.026×Cap/1000 |
|  |  | > 15,000 | 7.6 | 2.5 |

Table 55 reflects the standards for room air conditioners, specified in 10 CFR 430.32(b).

Table 55: Minimum Efficiency Levels for Room Air Conditioners ROB and NC Units

| Category | Cooling Capacity [Btuh] | Minimum Cooling Efficiency [EER] |
| --- | --- | --- |
| Without reverse cycle, with louvered sides | < 8,000 | 11.0 |
|  | ≥ 8,000 and < 14,000 | 10.9 |
|  | ≥ 14,000 and < 20,000 | 10.7 |
|  | ≥ 20,000 and < 25,000 | 9.4 |
|  | ≥ 25,000 | 9.0 |
| Without reverse cycle, without louvered sides | < 8,000 | 10.0 |
|  | ≥ 8,000 and < 11,000 | 9.6 |
|  | ≥ 11,000 and < 14,000 | 9.5 |
|  | ≥ 14,000 and < 20,000 | 9.3 |
|  | ≥ 20,000 | 9.4 |
| With reverse cycle, with louvered sides | < 20,000 | 9.8 |
|  | ≥ 20,000 | 9.3 |
| With reverse cycle, without louvered sides | < 14,000 | 9.3 |
|  | ≥ 14,000 | 8.7 |
| Casement-only | All capacities | 9.5 |
| Casement-slider | All capacities | 10.4 |

##### High-efficiency Condition

The high-efficiency retrofits must exceed the minimum federal standards found in Table 54 and Table 55.

The high-efficiency retrofits must also meet the following criteria:

- For early retirement projects only, the installed equipment cooling capacity must be within 80 percent to 120 percent of the replaced electric cooling capacity. For scenarios involving the replacement of a combination of systems by an alternate combination of systems of varying capacities, early retirement savings can still be claimed if the overall pre- and post-capacities for the total combination of systems are within ± 20%. In these cases, a custom calculation should be performed to establish the following weighted savings factors to be applied over the early retirement portion of the savings calculation: manufacturer year, EUL, RUL, full and part-load baseline, demand factor, and EFLH. These factors should be weighted based on contribution to overall capacity.

- Non-standard size PTAC/PTHPs cannot be used for new construction

- No additional measures are being installed that directly affect the operation of the cooling equipment (e.g., control sequences)

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Peak Demand (Summer) [kWSavings,C]=CapC,preηbaseline,C-CapC,postηinstalled,C×DFCDF×1 kW1,000 W

Equation 30

Peak Demand (Winter) [kWSavings,H]=CapH,preηbaseline,H-CapH,postηinstalled,H×DFH×1 kW3,412 Btuh

Equation 31

Total Energy [kWhSavings]=kWhSavings,C+kWhSavings,H

Equation 32

Energy Cooling [kWhSavings,C]=CapC,preηbaseline,C-CapC,postηinstalled,C×EFLHC×1 kW1,000 W

Equation 33

Energy Heating [kWhSavings,H]=CapH,preηbaseline,H-CapH,postηinstalled,H×EFLHH×1 kWh3,412 Btu

Equation 34

Where:

CapC/H,pre	=	For ER, rated equipment cooling/heating capacity of the existing equipment at AHRI standard conditions; for ROB & NC, rated equipment cooling/heating capacity of the new equipment at AHRI standard conditions [BTUH]; 1 ton = 12,000 Btuh

CapC/H,post	=	Rated equipment cooling/heating capacity of the newly installed equipment at AHRI standard conditions [Btuh]; 1 ton = 12,000 Btuh

ηbaseline,C	=	Cooling efficiency of existing (ER) or standard (ROB/NC) equipment [EER, Btu/W-h] (Table 53 through Table 55)

ηbaseline,H	=	Heating efficiency of existing (ER) or standard (ROB/NC) equipment [COP] (Table 53 and Table 54)

ηinstalled,C	=	Rated cooling efficiency of the newly installed equipment [EER, Btu/W-h])—(Must exceed minimum federal standards found in Table 54 and Table 55)

ηinstalled,H	=	Rated heating efficiency of the newly installed equipment [COP] (Must exceed minimum federal standards found in Table 54)

DFC/H	=	Seasonal peak demand factor for appropriate climate zone, building type, and equipment type (Table 28 through Table 32)

EFLHC/H	=	Cooling/heating equivalent full-load hours for newly installed equipment based on appropriate climate zone, building type, and equipment type [hours], see Table 56 through Table 60.

The first-year savings algorithms in the above equations are used for all HVAC projects, across NC, ROB, and ER projects. However, ER projects require a weighted savings calculated over both the ER and ROB periods taking the EUL and RUL into account. The ER savings are applied over the remaining useful life (RUL) period, and the ROB savings are applied over the remaining period (EUL-RUL). The final reported savings for ER projects are not actually a “first-year” savings, but an “average annual savings over the lifetime (EUL) of the measure.” These savings calculations are explained in Appendix A.

##### Claimed Peak Demand Savings

A summer peak period value is used for this measure. Refer to Volume 1, Section 4 for further details on peak demand savings and methodology.

##### Deemed Energy and Demand Savings Tables

Table 56 through Table 60 present the deemed peak demand factor (DF) and equivalent full-load hour (EFLH) values for PTAC/PTHPs and RACs. These values are calculated by climate zone, building type, and equipment type.

These tables also include an “Other” building type, which can be used for business types that are not explicitly listed. The DF and EFLH values used for Other are the most conservative values from the explicitly listed building types. When the Other building type is used, a description of the actual building type, the primary business activity, the business hours, and the HVAC schedule must be collected for the project site and stored in the utility tracking data system. For those combinations of technology, climate zone, and building type where no values are present, a project with that specific combination should use the “Other” building type.

A description of the calculation method can also be found in Docket No. 40885, Attachment B.

Table 56: PTAC/PTHP or RAC Equipment: DF and EFLH Values for Amarillo (CZ 1)

| Building Types | Principal Building Activity | Packaged Terminal Unit |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |
|  |  | DFC | EFLHC | DFC | EFLHC | DFH | EFLHH |
| Education | Primary School | 0.56 | 686 | 0.56 | 686 | 0.43 | 322 |
|  | Secondary School | 0.61 | 496 | 0.61 | 496 | 0.43 | 338 |
| Food Sales | Convenience | 0.64 | 820 | 0.64 | 820 | 0.48 | 410 |
| Food Service | Full-service Restaurant | 0.73 | 946 | 0.73 | 946 | 0.43 | 516 |
|  | 24-hour Full-service | 0.71 | 1,014 | 0.71 | 1,014 | 0.43 | 619 |
|  | Quick-service Restaurant | 0.64 | 710 | 0.64 | 710 | 0.48 | 473 |
|  | 24-hour Quick-service | 0.65 | 758 | 0.65 | 758 | 0.48 | 598 |
| Lodging | Large Hotel | 0.51 | 1,248 | 0.51 | 1,248 | 0.86 | 504 |
|  | Nursing Home | 0.60 | 635 | 0.60 | 635 | 0.50 | 256 |
|  | Small Hotel | 0.50 | 1,442 | 0.50 | 1,442 | 0.36 | 218 |
| Mercantile | Strip Mall | 0.66 | 637 | 0.66 | 637 | 0.39 | 346 |
| Office | Small Office | 0.63 | 660 | 0.63 | 660 | 0.29 | 156 |
| Other | Other | 0.50 | 496 | 0.50 | 496 | 0.29 | 156 |

Table 57: PTAC/PTHP or RAC Equipment: DF and EFLH Values for Dallas (CZ 2)

| Building Types | Principal Building Activity | Packaged Terminal Unit |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |  |
|  |  | DFC | EFLHC | DFC | EFLHC | DFH | EFLHH |
| Education | Primary School | 0.85 | 1,016 | 0.85 | 1,016 | 0.66 | 231 |
|  | Secondary School | 0.99 | 912 | 0.99 | 912 | 0.59 | 285 |
| Food Sales | Convenience | 1.05 | 1,544 | 1.05 | 1,544 | 0.61 | 318 |
| Food Service | Full-service Restaurant | 1.06 | 1,534 | 1.06 | 1,534 | 0.50 | 401 |
|  | 24-hour Full-service | 1.06 | 1,734 | 1.06 | 1,734 | 0.49 | 509 |
|  | Quick-service Restaurant | 1.05 | 1,336 | 1.05 | 1,336 | 0.61 | 368 |
|  | 24-hour Quick-service | 1.05 | 1,485 | 1.05 | 1,485 | 0.60 | 463 |
| Lodging | Large Hotel | 0.68 | 1,749 | 0.68 | 1,749 | 0.82 | 270 |
|  | Nursing Home | 1.01 | 1,460 | 1.01 | 1,460 | 0.61 | 226 |
|  | Small Hotel | 0.53 | 1,919 | 0.53 | 1,919 | 0.42 | 145 |
| Mercantile | Strip Mall | 0.88 | 925 | 0.88 | 925 | 0.55 | 219 |
| Office | Small Office | 0.89 | 1,012 | 0.89 | 1,012 | 0.40 | 89 |
| Other | Other | 0.53 | 912 | 0.53 | 312 | 0.40 | 89 |

Table 58: PTAC/PTHP or RAC Equipment: DF and EFLH Values for Houston (CZ 3)

| Building Types | Principal Building Activity | Packaged Terminal Unit |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |  |
|  |  | DFC | EFLHC | DFC | EFLHC | DFH | EFLHH |
| Education | Primary School | 0.71 | 1,186 | 0.71 | 1,186 | 0.50 | 52 |
|  | Secondary School | 0.79 | 1,030 | 0.79 | 1,030 | 0.54 | 63 |
| Food Sales | Convenience | 0.83 | 1,760 | 0.83 | 1,760 | 0.51 | 70 |
| Food Service | Full-service Restaurant | 0.85 | 1,755 | 0.85 | 1,755 | 0.44 | 93 |
|  | 24-hour Full-service | 0.86 | 1,994 | 0.86 | 1,994 | 0.44 | 121 |
|  | Quick-service Restaurant | 0.83 | 1,523 | 0.83 | 1,523 | 0.51 | 80 |
|  | 24-hour Quick-service | 0.85 | 1,692 | 0.85 | 1,692 | 0.50 | 104 |
| Lodging | Large Hotel | 0.57 | 2,080 | 0.57 | 2,080 | 0.33 | 54 |
|  | Nursing Home | 0.81 | 1,695 | 0.81 | 1,695 | 0.24 | 44 |
|  | Small Hotel | 0.53 | 1,903 | 0.53 | 1,903 | 0.19 | 32 |
| Mercantile | Strip Mall | 0.74 | 1,093 | 0.74 | 1,093 | 0.42 | 47 |
| Office | Small Office | 0.71 | 1,100 | 0.71 | 1,100 | 0.28 | 15 |
| Other | Other | 0.53 | 1,030 | 0.53 | 1,030 | 0.28 | 15 |

Table 59: PTAC/PTHP or RAC Equipment: DF and EFLH Values for Corpus Christi (CZ 4)

| Building Types | Principal Building Activity | Packaged Terminal Unit |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |
|  |  | DFc | EFLHC | DFc | EFLHC | DFH | EFLHH |
| Education | Primary School | 0.70 | 1,355 | 0.70 | 1,355 | 0.30 | 73 |
|  | Secondary School | 0.76 | 1,212 | 0.76 | 1,212 | 0.35 | 92 |
| Food Sales | Convenience | 0.74 | 2,025 | 0.74 | 2,025 | 0.34 | 94 |
| Food Service | Full-service Restaurant | 0.77 | 2,041 | 0.77 | 2,041 | 0.35 | 136 |
|  | 24-hour Full-service | 0.77 | 2,337 | 0.77 | 2,337 | 0.36 | 176 |
|  | Quick-service Restaurant | 0.74 | 1,752 | 0.74 | 1,752 | 0.34 | 108 |
|  | 24-hour Quick-service | 0.74 | 1,968 | 0.74 | 1,968 | 0.34 | 138 |
| Lodging | Large Hotel | 0.51 | 2,404 | 0.51 | 2,404 | 0.21 | 61 |
|  | Nursing Home | 0.73 | 1,832 | 0.73 | 1,832 | 0.15 | 47 |
|  | Small Hotel | 0.46 | 2,041 | 0.46 | 2,041 | 0.10 | 38 |
| Mercantile | Strip Mall | 0.65 | 1,218 | 0.65 | 1,218 | 0.21 | 66 |
| Office | Small Office | 0.63 | 1,213 | 0.63 | 1,213 | 0.14 | 18 |
| Other | Other | 0.46 | 1,212 | 0.46 | 1,212 | 0.14 | 18 |

Table 60: PTAC/PTHP or RAC Equipment: DF and EFLH Values for El Paso (CZ 5)

| Building Types | Principal Building Activity | Packaged Terminal Unit |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Air Conditioner |  | Heat Pump |  |  |  |
|  |  | DFc | EFLHC | DFc | EFLHC | DFH | EFLHH |
| Education | Primary School | 0.88 | 1,009 | 0.88 | 1,009 | 0.37 | 271 |
|  | Secondary School | 0.84 | 751 | 0.84 | 751 | 0.43 | 286 |
| Food Sales | Convenience | 0.74 | 1,267 | 0.74 | 1,267 | 0.26 | 300 |
| Food Service | Full-service Restaurant | 0.74 | 1,292 | 0.74 | 1,292 | 0.28 | 407 |
|  | 24-hour Full-service | 0.72 | 1,431 | 0.72 | 1,431 | 0.27 | 538 |
|  | Quick-service Restaurant | 0.74 | 1,096 | 0.74 | 1,096 | 0.26 | 347 |
|  | 24-hour Quick-service | 0.75 | 1,186 | 0.75 | 1,186 | 0.26 | 463 |
| Lodging | Large Hotel | 0.61 | 1,723 | 0.61 | 1,723 | 0.21 | 292 |
|  | Nursing Home | 0.85 | 1,244 | 0.85 | 1,244 | 0.15 | 211 |
|  | Small Hotel | 0.61 | 1,945 | 0.61 | 1,945 | 0.06 | 123 |
| Mercantile | Strip Mall | 0.80 | 943 | 0.80 | 943 | 0.27 | 298 |
| Office | Small Office | 0.81 | 1,050 | 0.81 | 1,050 | 0.15 | 97 |
| Other | Other | 0.61 | 751 | 0.61 | 751 | 0.15 | 97 |

##### Measure Life and Lifetime Savings

Effective Useful Life (EUL)

The EUL of PTAC/PTHP units is 15 years, as specified in DEER 2014.

The EUL of RAC units is 10 years based on current DOE Final Rule standards for room air conditioners. This value is consistent with the EUL reported in the Department of Energy Technical Support Document for Room Air conditioners.

Remaining Useful Life (RUL) for PTAC/PTHP Systems

The RUL of ER replaced systems is provided according to system age in Table 61.

For ER units of unknown age, assume a default value of 15 years, equal to the measure EUL. Default RUL may be used exclusively if applied consistently for all projects. Otherwise, the default should only be used when a project is reported and documented as having a nameplate that is illegible. Both the RUL and EUL are needed to estimate savings for early retirement projects for two distinct periods: The ER period (RUL) and the ROB period (EUL-RUL). The calculations for early retirement projects are extensive, and as such, are provided in Appendix A.

Table 61: Remaining Useful Life of ER PTAC/PTHP Systems,

| Age of Replaced System (Years) | PTAC/PTHP RUL (Years) |  | Age of Replaced System (Years) | PTAC/PTHP RUL (Years) |
| --- | --- | --- | --- | --- |
| 1 | 14.0 |  | 10 | 5.7 |
| 2 | 13.0 |  | 11 | 5.0 |
| 3 | 12.0 |  | 12 | 4.4 |
| 4 | 11.0 |  | 13 | 3.8 |
| 5 | 10.0 |  | 14 | 3.3 |
| 6 | 9.1 |  | 15 | 2.8 |
| 7 | 8.2 |  | 16 | 2.0 |
| 8 | 7.3 |  | 17 | 1.0 |
| 9 | 6.5 |  | 18 | 0.0 |

#### Program Tracking Data and Evaluation Requirements

The below list of primary inputs and contextual data is recommended to be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Decision/action type: ROB, NC, ER, system type conversion

- Building type

- Climate zone

- Baseline number of units

- Baseline equipment type

- Baseline rated cooling and heating capacities

- For ER only: Baseline age and method of determination (e.g., nameplate, blueprints, Customer reported, not available)

- For ER only: Photograph of retired unit nameplate demonstrating model number, serial number, and manufacturer if blueprints are not provided; if photograph of nameplate is unavailable or not legible, provide a photo or description documenting the reason why the nameplate photo was unobtainable (alternate forms of documentation can be approved at the evaluator’s discretion)

- Installed number of units

- Installed equipment type (PTAC, PTHP, RAC)

- Equipment configuration category: Standard/non-standard or room AC

- Installed rated cooling and heating capacities

- Installed cooling and heating efficiency ratings

- Installed manufacturer and model

- Installed unit AHRI/DOE CCMS certificate or reference number

- For retrofit only: Proof of purchase: invoice showing model number; a photo of the model number on product packaging and installed unit(s); OR an evaluator pre-approved inspection approach

- For new construction only: Proof of purchase: invoice showing model number; a photo of the model number on product packaging and installed unit(s); as-built design drawings; HVAC specifications package that provides detailed make and model information on installed unit(s); OR an evaluator pre-approved inspection approach

- For Other building type only: A description of the actual building type, the primary business activity, the business hours, and the HVAC schedule.

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 36779—Provides EUL for HVAC equipment.

- PUCT Docket 40083—Provides incorporation of early retirement savings for existing commercial HVAC SOP designs and updates for baseline equipment efficiency levels for ROB and new construction projects involving package and split systems.

- PUCT Docket 40885—Provides a petition to revise deemed savings values for commercial HVAC replacement measures. This petition updated demand and energy coefficients for all commercial HVAC systems.

##### Relevant Standards and Reference Sources

- ANSI/ASHRAE/IES Standard 90.1-2001 through ASHRAE 90.1-2007. Energy Standard for Buildings Except Low-Rise Residential Buildings. Table 6.8.1D.

- ANSI/ASHRAE/IES Standard 90.1-2010. Energy Standard for Buildings Except Low-Rise Residential Buildings. Table 6.8.1D.

- Code of Federal Regulations. Title 10. Part 431—Energy Efficiency Program for Certain Commercial and Industrial Equipment. https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=46

- Code of Federal Regulations. Title 10. Part 430—Energy Efficiency Program for Certain Commercial and Industrial Equipment. https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=52

- 2015 International Energy Conservation Code. Table C403.2.3(3).

### HVAC Variable Frequency Drive (VFD) Measure Overview

TRM Measure ID: NR-HV-VF

Market Sector: Commercial

Measure Category: HVAC

Applicable Building Types: See Table 65 through Table 71

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This measure involves the installation of a VFD in a commercial HVAC application. Eligible applications include:

- AHU supply fan on a split or packaged HVAC system. The fan is in a variable air volume (VAV) system with terminal VAV boxes or constant air volume (CAV) unit with no control device.

- Hot water distribution pumps

- Chilled water distribution pumps

This measure does not apply to controls installed on the HVAC compressor. This measure accounts for the interactive air conditioning demand savings during the utility defined summer peak period. The savings are on a per-control basis, and the lookup tables show the total savings for eligible scenarios.

##### Eligibility Criteria

Supply fans may not have variable pitch blades. Supply fans must be less than or equal to 100 hp. New construction systems are ineligible. Equipment used for process loads is ineligible.

##### Baseline Condition

The AHU supply fan baseline is a centrifugal supply fan with a single-speed motor on a direct expansion (DX) VAV or CAV air conditioning (AC) unit. The motor is a standard efficiency motor based on ASHRAE Standard 90.1-2013, which are provided by horsepower. The AC unit has standard cooling efficiency based on IECC 2015. The part-load fan control is an outlet damper, inlet damper, inlet guide vane, or no control (constant volume systems).

The HVAC pump baseline is a constant speed pump with a standard-efficiency motor. This measure is applicable to both primary and secondary hot or chilled water pumping systems.

##### High-efficiency Condition

The high-efficiency condition is the installation of a VFD on an AHU supply fan, hot water pump, or chilled water pump.

For AHU supply fans, when applicable, the existing damper or inlet guide vane will be removed or set completely open permanently after installation. The VFD will maintain a constant static pressure by adjusting fan speed and delivering the same amount of air as the baseline condition.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Demand Savings are calculated for each hour over the course of the year:

Step 1: Determine the percent flow rate for each of the year (i)

For AHUs:

%CFMi =m × tdb,i +b

Equation 35

Where:

tdb,i	=	The hourly dry bulb temperature (DBT) using TMY3 data

m	=	The slope of the relationship between DBT and CFM, see Table 62

b	=	The intercept of the relationship between DBT and CFM, see Table 62

The minimum flow rate is set to 60% cfm based on common design practice. Determination of the minimum dry bulb temperature assumes that cooling will only operate above the cooling reference temperature of 65°F dry bulb. The maximum DBT is the ASHRAE dry bulb design temperature.

Table 62: AHU Supply Fan VFD %CFM Inputs

| Climate Zone | Condition | Minimum | Maximum | Slope (m) | Intercept (b) |
| --- | --- | --- | --- | --- | --- |
| Zone 1 | Flow Rate (%CFM) | 60 | 100 | 1.19 | -17.38 |
|  | Dry Bulb T (°F) | 65 | 98.6 |  |  |
| Zone 2 | Flow Rate (%CFM) | 60 | 100 | 1.10 | -11.43 |
|  | Dry Bulb T (°F) | 65 | 101.4 |  |  |
| Zone 3 | Flow Rate (%CFM) | 60 | 100 | 1.23 | -20.00 |
|  | Dry Bulb T (°F) | 65 | 97.5 |  |  |
| Zone 4 | Flow Rate (%CFM) | 60 | 100 | 1.26 | -21.76 |
|  | Dry Bulb T (°F) | 65 | 96.8 |  |  |
| Zone 5 | Flow Rate (%CFM) | 60 | 100 | 1.11 | -12.02 |
|  | Dry Bulb T (°F) | 65 | 101.1 |  |  |

For chilled water pumps:

%GPMi =m × tdb_i +b

Equation 36

Where:

tdb,i	=	The hourly dry bulb temperature (DBT) using TMY3 data

m	=	The slope of the relationship between DBT and GPM, see Table 63

b	=	The intercept of the relationship between DBT and GPM, see Table 63

The minimum flow rate is set to 10% GPM based on the ANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual. Determination of the minimum dry bulb temperature assumes that cooling will only operate above the cooling reference temperature of 65°F dry bulb. The maximum DBT is the ASHRAE dry bulb design temperature.

Table 63: Chilled Water Pump VFD %CFM Inputs

| Climate Zone | Condition | Minimum | Maximum | Slope (m) | Intercept (b) |
| --- | --- | --- | --- | --- | --- |
| Zone 1 | Flow Rate (%GPM) | 10 | 100 | 2.68 | -164.11 |
|  | Dry Bulb T (°F) | 65 | 98.6 |  |  |
| Zone 2 | Flow Rate (%GPM) | 10 | 100 | 2.47 | -150.71 |
|  | Dry Bulb T (°F) | 65 | 101.4 |  |  |
| Zone 3 | Flow Rate (%GPM) | 10 | 100 | 2.77 | -170.00 |
|  | Dry Bulb T (°F) | 65 | 97.5 |  |  |
| Zone 4 | Flow Rate (%GPM) | 10 | 100 | 2.83 | -173.96 |
|  | Dry Bulb T (°F) | 65 | 96.8 |  |  |
| Zone 5 | Flow Rate (%GPM) | 10 | 100 | 2.49 | -152.05 |
|  | Dry Bulb T (°F) | 65 | 101.1 |  |  |

For hot water pumps:

%GPMi =m × tdb_i +b

Equation 37

Where:

tdb,i	=	The hourly dry bulb temperature (DBT) using TMY3 data

m	=	The slope of the relationship between DBT and GPM, see Table 64

b	=	The intercept of the relationship between DBT and GPM, see Table 64

The minimum flow rate is set to 10% GPM based on the ANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual. Determination of the minimum dry bulb temperature assumes that heating will only operate below the heating reference temperature of 65°F dry bulb. The maximum DBT is the ASHRAE dry bulb design temperature.

Table 64: Hot Water Pump VFD %CFM Inputs

| Climate Zone | Condition | Minimum | Maximum | Slope (m) | Intercept (b) |
| --- | --- | --- | --- | --- | --- |
| Zone 1 | Flow Rate (%GPM) | 10 | 100 | -1.64 | 116.56 |
|  | Dry Bulb T (°F) | 65 | 10.1 |  |  |
| Zone 2 | Flow Rate (%GPM) | 10 | 100 | -2.16 | 150.29 |
|  | Dry Bulb T (°F) | 65 | 23.3 |  |  |
| Zone 3 | Flow Rate (%GPM) | 10 | 100 | -2.65 | 182.57 |
|  | Dry Bulb T (°F) | 65 | 31.1 |  |  |
| Zone 4 | Flow Rate (%GPM) | 10 | 100 | -3.15 | 214.55 |
|  | Dry Bulb T (°F) | 65 | 36.4 |  |  |
| Zone 5 | Flow Rate (%GPM) | 10 | 100 | -2.26 | 156.62 |
|  | Dry Bulb T (°F) | 65 | 25.1 |  |  |

Step 2 - Calculate the %power for the applicable baseline and the new VFD technology:

Baseline Technologies

For AHU supply fan:

%poweri,OutletDamper =0.00745 × %CFMi2+0.10983 ×%CFMi +20.41905

Equation 38

%poweri,InletDamper = 0.00013×%CFMi3-0.01452×%CFMi2+0.71648×%CFMi+50.25833
0.00013×%CFMi3-0.01452×%CFMi2+0.71648×%CFMi+50.25833

Equation 39

%poweri,InletGuideVane= 0.00009×%CFMi3-0.00128×%CFMi2+0.06808×%CFMi+20

Equation 40

Note: %power for constant volume baseline technologies with no fan control is set equal to 1 for each hour where %power is less than 1 for the other baseline control types. When %power exceeds 1 for the other baseline control types, %power for no fan control is set equal to the maximum value from the other baseline control types.

For chilled and hot water pumps:

%powerbase =2.5294×%GPMi3-4.7443×%GPMi2+3.2485×%GPMi+0

Equation 41

VFD Technology

For AHU supply fan:

%powerVFD = 0.00004×%CFMi3+0.00766×%CFMi2-0.19567×%CFMi+5.9

Equation 42

For chilled and hot water pumps:

%powerVFD =0.7347×%GPMi3-0.301×%GPMi2+0.5726×%GPMi+0

Equation 43

Step 3 - Calculate kWfull using the hp from the motor nameplate, LF (75%), and the applicable motor efficiency from ASHRAE 2013, Table 10.8-1 Minimum Nominal Efficiency for General Purpose Electric Motors; Use that result and the %power results to determine power consumption at each hour:

kWfull=0.746×HP×LFη

Equation 44

kWi=kWfull×%poweri

Equation 45

Where:

%poweri	=	Percentage of full load power at the ith hour calculated by an equation based on the control type (outlet damper, inlet box damper, inlet guide vane-IGV, or VFD)

kWfull	=	Fan motor power demand operating at the fan design 100% CFM or pump design 100% GPM

kWi	=	Fan or Pump real-time power at the ith hour of a year

HP 	=	Rated horsepower of the motor

LF	=	Load factor—ratio of the operating load to the nameplate rating of the motor—assumed to be 75% at the fan or pump design 100% per DEER 2005

η	=	Motor efficiency of a standard efficiency Open Drip Proof (ODP) motor operating at 1800 RPM taken from ASHRAE Standard 90.1-2013

| Motor Horsepower | Full Load Efficiency |
| --- | --- |
| 1 | 0.855 |
| 2 | 0.865 |
| 3 | 0.895 |
| 5 | 0.895 |
| 7.5 | 0.91 |
| 10 | 0.917 |
| 15 | 0.93 |
| 20 | 0.93 |
| 25 | 0.936 |
| 30 | 0.941 |
| 40 | 0.941 |
| 50 | 0.945 |
| 60 | 0.95 |
| 75 | 0.95 |
| 100 | 0.954 |

0.746	=	HP to kW conversion factor

Step 4 - Calculate the kW savings for each of the top 20 hours within the applicable peak probability analysis for the building’s climate zone from Volume 1. Sum the kW savings for each hour multiplied by the peak demand probability factor from the 20 individual hourly calculations, then divide by the sum of the PDPF for the 20 hours to get the average peak demand impact, and then calculate the total peak demand saved by adding peak demand interactive effects:

Hourly Savings Calculations

(kWi)Saved=[(kWi)Baseline -kWi)VFD × schedulei

Equation 46

Where:

schedule	=	1 when building is occupied, 0.2 when building is unoccupied, see Table 65

Table 65: Yearly Motor Operation Hours by Building Type

| Building Type | Weekday Schedule | Weekend Schedule | Annual Building Occupied Hours | Annual Motor Operation Hours |
| --- | --- | --- | --- | --- |
| Hospitals and Healthcare | 24 hr | 24 hr | 8,760 | 8,760 |
| Office—Large | 8am–8pm | 8am–10am | 3,340 | 4,424 |
| Office—Small | 8am–6pm | 8am–10am | 2,818 | 4,006 |
| Education—K-12 | 7am–5pm | 8am–12pm | 3,026 | 4,173 |
| Education—College and University | 8am–8pm | 8am–12pm | 3,548 | 4,590 |
| Retail | 9am–10pm | 9am–10pm | 4,745 | 5,548 |
| Restaurants—Fast Food | 6am–11pm | 6am–11pm | 6,205 | 6,716 |
| Restaurants—Sit Down | 11am–11pm | 11am–11pm | 4,380 | 5,256 |
| Other | 8am–6pm | 8am–10am | 2,818 | 4,006 |

Average Peak Demand Saved Calculation, excluding interactive effects

kWPDPF,Saved= i=120kWi)Saved *PDPFii=120PDPFi

Equation 47

Where:

PDPF	=	Peak demand probability factor from the applicable climate zone table in Volume 1.

Total Peak Demand Saved Calculation, including interactive effects.This applies only to AHU supply fans. Total peak demand savings for pumps are found using equation 46 above.:

kWTotalSaved=kWPDPF, Saved × (1+ 3.412CoolingEER)

Equation 48

Where:

CoolingEER	=	Air conditioner full-load cooling efficiency, assumed at 11.2, based on IECC 2015 minimum efficiency of a unitary AC system between 5 and 11.3 tons

Energy Savings are calculated in the following manner:

Step 1 – For both the baseline and new technology, calculate the sum of individual kWh consumption in each hour of the year:

Annual kWh= i=18760(kWi×schedulei)

Equation 49

Where:

8760	= 	Total number of hours in a year

Step 2 - Subtract the Annual kWhnew from the Annual kWhbaseline to get the Annual Energy Savings:

Annual Energy Savings [kWh]=kWhbaseline-kWhnew

Equation 50

##### Deemed Energy and Demand Savings Tables

Table 66: AHU Supply Fan Outlet Damper Baseline Savings per Motor HP

| Building Type | Climate Zone |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 |
| Energy Savings (kWh per Motor HP) |  |  |  |  |  |
| Hospitals and Healthcare | 1,160 | 1,101 | 1,071 | 1,046 | 1,121 |
| Office—Large | 569 | 536 | 515 | 499 | 545 |
| Office—Small | 514 | 484 | 464 | 449 | 493 |
| Education—K-12 | 539 | 508 | 484 | 469 | 517 |
| Education—College and University | 590 | 555 | 533 | 517 | 565 |
| Retail | 710 | 668 | 645 | 629 | 680 |
| Restaurants—Fast Food | 872 | 823 | 796 | 776 | 838 |
| Restaurants—Sit Down | 674 | 635 | 617 | 603 | 646 |
| Other | 514 | 484 | 464 | 449 | 493 |
| Summer kW Savings (kW per Motor HP) |  |  |  |  |  |
| All Building Types | 0.041 | 0.032 | 0.038 | 0.061 | 0.041 |

Table 67: AHU Supply Fan Inlet Damper Baseline Savings per Motor HP

| Building Type | Climate Zone |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 |
| Energy Savings (kWh per Motor HP) |  |  |  |  |  |
| Hospitals and Healthcare | 1,824 | 1,672 | 1,597 | 1,533 | 1,722 |
| Office—Large | 881 | 801 | 754 | 716 | 822 |
| Office—Small | 797 | 724 | 678 | 643 | 743 |
| Education—K-12 | 837 | 761 | 709 | 673 | 782 |
| Education—College and University | 914 | 830 | 780 | 741 | 852 |
| Retail | 1,098 | 998 | 944 | 904 | 1,024 |
| Restaurants- Fast Food | 1,358 | 1,238 | 1,172 | 1,122 | 1,272 |
| Restaurants—Sit Down | 1,044 | 949 | 906 | 870 | 974 |
| Other | 797 | 724 | 678 | 643 | 743 |
| Summer kW Savings (kW per Motor HP) |  |  |  |  |  |
| All Building Types | 0.047 | 0.037 | 0.047 | 0.067 | 0.047 |

Table 68: AHU Supply Fan Inlet Guide Vane Baseline Savings per Motor HP

| Building Type | Climate Zone |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 |
| Energy Savings (kWh per Motor HP) |  |  |  |  |  |
| Hospitals and Healthcare | 388 | 345 | 324 | 307 | 359 |
| Office—Large | 185 | 163 | 151 | 141 | 169 |
| Office—Small | 167 | 148 | 135 | 126 | 153 |
| Education—K-12 | 176 | 156 | 142 | 132 | 161 |
| Education—College and University | 192 | 169 | 156 | 145 | 175 |
| Retail | 230 | 203 | 189 | 178 | 210 |
| Restaurants- Fast Food | 286 | 253 | 236 | 222 | 262 |
| Restaurants—Sit Down | 219 | 194 | 182 | 172 | 200 |
| Other | 167 | 148 | 135 | 126 | 153 |
| Summer kW Savings (kW per Motor HP) |  |  |  |  |  |
| All Building Types | 0.009 | 0.009 | 0.01 | 0.011 | 0.01 |

Table 69: AHU Supply Fan No Control Baseline Savings per Motor HP

| Building Type | Climate Zone |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 |
| Energy Savings (kWh per Motor HP) |  |  |  |  |  |
| Hospitals and Healthcare | 3,300 | 3,035 | 2,904 | 2,792 | 3,124 |
| Office—Large | 1,595 | 1,453 | 1,368 | 1,299 | 1,490 |
| Office—Small | 1,442 | 1,313 | 1,228 | 1,165 | 1,348 |
| Education—K-12 | 1,514 | 1,380 | 1,285 | 1,219 | 1,418 |
| Education—College and University | 1,654 | 1,505 | 1,414 | 1,344 | 1,545 |
| Retail | 1,988 | 1,809 | 1,712 | 1,640 | 1,857 |
| Restaurants—Fast Food | 2,458 | 2,245 | 2,128 | 2,040 | 2,307 |
| Restaurants—Sit Down | 1,889 | 1,720 | 1,644 | 1,579 | 1,765 |
| Other | 1,442 | 1,313 | 1,228 | 1,165 | 1,348 |
| Summer kW Savings (kW per Motor HP) |  |  |  |  |  |
| All Building Types | 0.049 | 0.037 | 0.061 | 0.086 | 0.051 |

Table 70: Chilled Water Pump Savings per Motor HP

| Building Type | Climate Zone |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 |
| Energy Savings (kWh per Motor HP) |  |  |  |  |  |
| Hospitals and Healthcare | 777 | 1,154 | 1,337 | 1,479 | 1,049 |
| Office—Large | 455 | 621 | 699 | 758 | 590 |
| Office—Small | 411 | 560 | 633 | 683 | 533 |
| Education—K-12 | 422 | 577 | 655 | 710 | 549 |
| Education—College and University | 475 | 644 | 727 | 788 | 613 |
| Retail | 576 | 780 | 888 | 958 | 738 |
| Restaurants—Fast Food | 662 | 924 | 1,057 | 1,152 | 868 |
| Restaurants—Sit Down | 540 | 736 | 837 | 908 | 690 |
| Other | 411 | 560 | 633 | 683 | 533 |
| Summer kW Savings (kW per Motor HP) |  |  |  |  |  |
| All Building Types | 0.046 | 0.029 | 0.035 | 0.087 | 0.049 |

Table 71: Hot Water Pump Savings per Motor HP

| Building Type | Climate Zone |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 |
| Energy Savings (kWh per Motor HP) |  |  |  |  |  |
| Hospitals and Healthcare | 1,304 | 912 | 723 | 597 | 1,044 |
| Office—Large | 600 | 417 | 323 | 257 | 468 |
| Office—Small | 541 | 378 | 286 | 228 | 421 |
| Education—K-12 | 572 | 399 | 301 | 239 | 448 |
| Education—College and University | 620 | 431 | 332 | 264 | 487 |
| Retail | 746 | 510 | 397 | 321 | 593 |
| Restaurants—Fast Food | 940 | 649 | 510 | 413 | 745 |
| Restaurants—Sit Down | 710 | 487 | 386 | 314 | 566 |
| Other | 541 | 378 | 286 | 228 | 421 |
| Winter kW Savings (kW per Motor HP) |  |  |  |  |  |
| All Building Types | 0.123 | 0.045 | 0.047 | 0.108 | 0.229 |

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

The estimated useful life (EUL) for this VFD measure is 15 years per both the PUCT-approved Texas EUL filing (Docket No. 36779) and DEER 2014 (EUL ID—HVAC-VSD-fan).

#### Program Tracking Data and Evaluation Requirements

The below list of primary inputs and contextual data is recommended to be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Building type

- Application type (AHU supply fan, hot water pump, chilled water pump)

- Climate zone

- Motor horsepower

- For AHU supply fans only: Baseline part-load control type (e.g., outlet damper, inlet damper, inlet guide vane, constant volume/no control).

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 36779—Provides EUL for VFD equipment

- PUCT Docket 40668—Provides details on deemed savings calculations for VFDs.

##### Relevant Standards and Reference Sources

- ASHRAE Fundamentals 1997: Chapter 26, Table 1B—Cooling and Dehumidification Design Conditions—United States.

- ASHRAE Standard 90.1-2013: Table 10.8-1 Minimum Nominal Full-load Efficiency for General Purpose Electric Motors (Subtype I), Except Fire-Pump Electric Motors and Table 10.8-2 Minimum Nominal Full-load Efficiency for General Purpose Electric Motors (Subtype II), Except Fire-Pump Electric Motors.

- National Renewable Energy Laboratory’s (NREL) National Solar Radiation Data Base: 1991- 2005 Update for Typical Meteorological Year 3 (TMY3).  Available at https://sam.nrel.gov/weather-data.html.

- California Public Utility Commission. Database for Energy Efficiency Resources, 2005.

- Bonneville Power Authority Adjustable Speed Drive Calculator—Fan curves utilized from that calculator were derived from "Flow Control," a Westinghouse publication, Bulletin B-851, F/86/Rev-CMS 8121. http://www.bpa.gov/EE/Sectors/Industrial/Documents/ASDCalculators.xls. Accessed 07/09/2020.

### Condenser Air Evaporative Pre-Cooling Measure Overview

TRM Measure ID: NR-HV-EP

Market Sector: Commercial

Measure Category: HVAC

Applicable Building Types: See Table 73 through Table 77

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This section summarizes the deemed savings methodology for the installation of an evaporative pre-cooling system onto HVAC equipment. This process reduces the temperature of the outside air before it is used to cool the condenser coil for direct expansion (DX) units or air-cooled chillers. The temperature reduction is achieved by having the incoming air pass through a saturated media or mist wall, which will increase the humidity ratio under adiabatic conditions. This allows the dry bulb temperature to decrease while the wet bulb temperature remains constant, effectively increasing the heat rejection capacity from the condenser coils into the air. This measure is not applicable to the replacement of an air-cooled condenser with an evaporative condenser.

Applicable evaporative pre-cooling product types include:

- Evaporative media panels that incoming air must pass through

- Misting based system that sprays fine droplets into the air in front of the air intake area

##### Eligibility Criteria

For a measure to be eligible to use this deemed savings approach, the following conditions must be met:

Must have chemical or mechanical water treatment

Must have periodic purge control for sump-based systems

Must have a control system for operation

  - Minimum temperature controls for sump-based systems

  - Minimum enthalpy controls for mist-based systems

All air to condenser coils must pass through the evaporative pre-cooling system

- Systems must be installed by a qualified contractor and must be commissioned

- Evaporative effectiveness performance of greater than or equal to 0.75 (i.e., 75 percent) for average dry bulb temperature and humidity during peak hours

- Operation manuals must be provided

- If these conditions are not met, the deemed savings approach cannot be used, and the Simplified M&V Methodology or the Full M&V Methodology must be used.

##### Baseline Condition

The baseline conditions are the operation of a direct expansion (DX) unit or air-cooled chiller without evaporative pre-cooling.

##### High-efficiency Condition

Evaporative pre-cooling systems must exceed the evaporative effectiveness performance of 75 percent for average dry bulb temperature humidity during peak hours. Table 72 contains values that can be used as a reference for evaluating evaporative effectiveness.

Table 72: Average Weather during Peak Conditions

| Climate Zone | Temperature (°F) | Humidity (%) |
| --- | --- | --- |
| 1—Amarillo | 95.8 | 25 |
| 2—Dallas | 101.2 | 34 |
| 3—Houston | 99.1 | 37 |
| 4—Corpus Christi | 92.5 | 49 |
| 5—El Paso | 97.4 | 15 |

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

| Energy Savings kWhsavings=CapC×ηC×EFLH reduction |  |  |
| --- | --- | --- |
| Equation 51 |  |  |
| Peak Demand [kWSavings]=CapC×ηC×DRF |  |  |
|  |  | Equation 52 |

Where:

CapC	=	Rated equipment cooling capacity of the existing equipment at AHRI standard conditions [Btuh or ton]

ηC	= 	Cooling efficiency of existing equipment [Btu/W-h, or kW/ton]

EFLHreduction 	=	Annual cooling energy reduction divided by the rated full loaded demand. Annual cooling energy reduction is determined according to the same method as other HVAC coefficients contained in the TRM. Rated full loaded demand is the CapC divided by its rated full load efficiency. See Table 73 through Table 77.

DRF	=	Demand reduction factor. The average peak hour energy reduction divided by the rated full loaded demand. See Table 73 through Table 77.

Note: For DX systems, use EER for kW savings calculations and SEER/IEER for kWh savings calculations. For air-cooled chillers, use full-load efficiency (kW/ton) for kW savings calculations and part-load efficiency (IPLV) for kWh savings calculations. In the cases where the full-load efficiency is provided in terms of EER rather than kW/ton, a conversion to kW/ton needs to be performed using the following conversion:

kWTon=12EER

Equation 53

##### Deemed Energy and Demand Savings Tables

Deemed peak demand reduction factor (DRF) and equivalent full-load hour reduction (EFLHreduction) values are presented by building type and climate zone. A description of the building types that are used for HVAC systems is presented in Table 26. These building types are derived from the EIA CBECS study.

The DRF and EFLHreduction values for packaged and split AC are presented in Table 73 through Table 77. These tables also include an “Other” building type, which can be used for business types that are not explicitly listed. The DRF and EFLHreduction values used for Other are the most conservative values from the explicitly listed building types. When the Other building type is used, a description of the actual building type, the primary business activity, the business hours, and the HVAC schedule must be collected for the project site and stored in the utility tracking data system.

Deemed savings are estimated using building simulation models, which estimate the hourly impacts of installing an evaporative pre-cooling system (i.e., modeling the difference between base and change case). The base models are the same models used to derive values for the other commercial HVAC sections of the TRM. Adjustments are made for the evaporative pre-cooling measure by updating all existing HVAC equipment to operate with evaporative pre-cooling when the outside temperature is above 70°F.

Table 73: DRF and EFLH Reduction Values for Amarillo (Climate Zone 1)

| Building Type | Principal Building Activity | Direct Expansion |  | Air Cooled Chiller |  |
| --- | --- | --- | --- | --- | --- |
|  |  | DRF | EFLHreduction | DRF | EFLHreduction |
| Education | College | 0.19 | 130 | 0.17 | 150 |
|  | Primary School | 0.20 | 83 | 0.13 | 69 |
|  | Secondary School | 0.19 | 89 | 0.17 | 102 |
| Food Sales | Convenience | 0.18 | 125 | - | - |
|  | Supermarket | 0.08 | 37 | - | - |
| Food Service | Full-service Restaurant | 0.21 | 134 | - | - |
|  | Quick-service Restaurant | 0.18 | 109 | - | - |
| Healthcare | Hospital | 0.21 | 160 | 0.18 | 151 |
|  | Outpatient Healthcare | 0.17 | 145 | - | - |
| Large Multifamily | Midrise Apartment | 0.18 | 113 | 0.10 | 59 |
| Lodging | Large Hotel | 0.13 | 111 | 0.15 | 165 |
|  | Nursing Home | 0.18 | 115 | 0.10 | 60 |
|  | Small Hotel/Motel | 0.13 | 104 | - | - |
| Mercantile | Stand-alone Retail | 0.19 | 108 | 0.14 | 74 |
|  | Strip Mall | 0.21 | 121 | - | - |
| Office | Large Office | 0.25 | 206 | 0.18 | 119 |
|  | Medium Office | 0.19 | 75 | - | - |
|  | Small Office | 0.20 | 111 | - | - |
| Public Assembly | Public Assembly | 0.20 | 112 | 0.13 | 93 |
| Religious Worship | Religious Worship | 0.19 | 65 | 0.14 | 45 |
| Service | Service | 0.21 | 104 | - | - |
| Warehouse | Warehouse | 0.12 | 34 | - | - |
| Other | Other | 0.08 | 34 | 0.10 | 45 |

Table 74: DRF and EFLH Reduction Values for Fort Worth (Climate Zone 2)

| Building Type | Principal Building Activity | Direct Expansion |  | Air Cooled Chiller |  |
| --- | --- | --- | --- | --- | --- |
|  |  | DRF | EFLHreduction | DRF | EFLHreduction |
| Education | College | 0.21 | 192 | 0.19 | 195 |
|  | Primary School | 0.24 | 120 | 0.12 | 80 |
|  | Secondary School | 0.21 | 131 | 0.19 | 132 |
| Food Sales | Convenience | 0.24 | 214 | - | - |
|  | Supermarket | 0.15 | 78 | - | - |
| Food Service | Full-service Restaurant | 0.23 | 194 | - | - |
|  | Quick-service Restaurant | 0.24 | 185 | - | - |
| Healthcare | Hospital | 0.24 | 230 | 0.22 | 216 |
|  | Outpatient Healthcare | 0.19 | 174 | - | - |
| Large Multifamily | Midrise Apartment | 0.16 | 230 | 0.15 | 120 |
| Lodging | Large Hotel | 0.15 | 137 | 0.18 | 212 |
|  | Nursing Home | 0.16 | 234 | 0.15 | 122 |
|  | Small Hotel/Motel | 0.15 | 133 | - | - |
| Mercantile | Stand-alone Retail | 0.24 | 158 | 0.19 | 120 |
|  | Strip Mall | 0.23 | 156 | - | - |
| Office | Large Office | 0.26 | 220 | 0.23 | 231 |
|  | Medium Office | 0.20 | 102 | - | - |
|  | Small Office | 0.22 | 156 | - | - |
| Public Assembly | Public Assembly | 0.24 | 161 | 0.12 | 108 |
| Religious Worship | Religious Worship | 0.24 | 95 | 0.19 | 72 |
| Service | Service | 0.23 | 150 | - | - |
| Warehouse | Warehouse | 0.20 | 93 | - | - |
| Other | Other | 0.15 | 78 | 0.12 | 72 |

Table 75: DRF and EFLH Reduction Values for Houston (Climate Zone 3)

| Building Type | Principal Building Activity | Direct Expansion |  | Air Cooled Chiller |  |
| --- | --- | --- | --- | --- | --- |
|  |  | DRF | EFLHreduction | DRF | EFLHreduction |
| Education | College | 0.20 | 173 | 0.17 | 175 |
|  | Primary School | 0.21 | 118 | 0.10 | 74 |
|  | Secondary School | 0.20 | 118 | 0.17 | 119 |
| Food Sales | Convenience | 0.22 | 193 | - | - |
|  | Supermarket | 0.14 | 76 | - | - |
| Food Service | Full-service Restaurant | 0.21 | 171 | - | - |
|  | Quick-service Restaurant | 0.22 | 167 | - | - |
| Healthcare | Hospital | 0.21 | 202 | 0.19 | 187 |
|  | Outpatient Healthcare | 0.18 | 157 | - | - |
| Large Multifamily | Midrise Apartment | 0.17 | 257 | 0.14 | 105 |
| Lodging | Large Hotel | 0.14 | 120 | 0.14 | 193 |
|  | Nursing Home | 0.17 | 261 | 0.14 | 107 |
|  | Small Hotel/Motel | 0.13 | 113 | - | - |
| Mercantile | Stand-alone Retail | 0.22 | 152 | 0.19 | 128 |
|  | Strip Mall | 0.21 | 152 | - | - |
| Office | Large Office | 0.24 | 203 | 0.23 | 150 |
|  | Medium Office | 0.19 | 94 | - | - |
|  | Small Office | 0.20 | 138 | - | - |
| Public Assembly | Public Assembly | 0.21 | 159 | 0.10 | 99 |
| Religious Worship | Religious Worship | 0.22 | 92 | 0.19 | 77 |
| Service | Service | 0.21 | 132 | - | - |
| Warehouse | Warehouse | 0.18 | 81 | - | - |
| Other | Other | 0.13 | 76 | 0.10 | 74 |

Table 76: DRF and EFLH Reduction Values for Corpus Christi (Climate Zone 4)

| Building Type | Principal Building Activity | Direct Expansion |  | Air Cooled Chiller |  |
| --- | --- | --- | --- | --- | --- |
|  |  | DRF | EFLHreduction | DRF | EFLHreduction |
| Education | College | 0.13 | 161 | 0.11 | 160 |
|  | Primary School | 0.14 | 113 | 0.07 | 68 |
|  | Secondary School | 0.13 | 110 | 0.11 | 109 |
| Food Sales | Convenience | 0.14 | 188 | - | - |
|  | Supermarket | 0.08 | 74 | - | - |
| Food Service | Full-service Restaurant | 0.13 | 157 | - | - |
|  | Quick-service Restaurant | 0.14 | 162 | - | - |
| Healthcare | Hospital | 0.15 | 199 | 0.09 | 169 |
|  | Outpatient Healthcare | 0.12 | 150 | - | - |
| Large Multifamily | Midrise Apartment | 0.14 | 181 | 0.09 | 104 |
| Lodging | Large Hotel | 0.08 | 116 | 0.10 | 179 |
|  | Nursing Home | 0.14 | 183 | 0.09 | 106 |
|  | Small Hotel/Motel | 0.08 | 109 | - | - |
| Mercantile | Stand-alone Retail | 0.14 | 148 | 0.12 | 120 |
|  | Strip Mall | 0.13 | 146 | - | - |
| Office | Large Office | 0.16 | 192 | 0.13 | 137 |
|  | Medium Office | 0.11 | 90 | - | - |
|  | Small Office | 0.13 | 131 | - | - |
| Public Assembly | Public Assembly | 0.14 | 152 | 0.07 | 92 |
| Religious Worship | Religious Worship | 0.14 | 89 | 0.12 | 72 |
| Service | Service | 0.13 | 122 | - | - |
| Warehouse | Warehouse | 0.12 | 74 | - | - |
| Other | Other | 0.08 | 74 | 0.07 | 68 |

Table 77: DRF and EFLH Reduction Values for El Paso (Climate Zone 5)

| Building Type | Principal Building Activity | Direct Expansion |  | Air Cooled Chiller |  |
| --- | --- | --- | --- | --- | --- |
|  |  | DRF | EFLHreduction | DRF | EFLHreduction |
| Education | College | 0.27 | 240 | 0.22 | 254 |
|  | Primary School | 0.30 | 161 | 0.17 | 120 |
|  | Secondary School | 0.27 | 163 | 0.22 | 172 |
| Food Sales | Convenience | 0.25 | 232 | - | - |
|  | Supermarket | 0.12 | 76 | - | - |
| Food Service | Full-service Restaurant | 0.25 | 223 | - | - |
|  | Quick-service Restaurant | 0.25 | 201 | - | - |
| Healthcare | Hospital | 0.26 | 273 | 0.20 | 247 |
|  | Outpatient Healthcare | 0.23 | 259 | - | - |
| Large Multifamily | Midrise Apartment | 0.28 | 264 | 0.15 | 140 |
| Lodging | Large Hotel | 0.19 | 201 | 0.19 | 300 |
|  | Nursing Home | 0.28 | 268 | 0.15 | 142 |
|  | Small Hotel/Motel | 0.17 | 193 | - | - |
| Mercantile | Stand-alone Retail | 0.25 | 198 | 0.18 | 131 |
|  | Strip Mall | 0.26 | 207 | - | - |
| Office | Large Office | 0.32 | 314 | 0.22 | 199 |
|  | Medium Office | 0.25 | 137 | - | - |
|  | Small Office | 0.26 | 215 | - | - |
| Public Assembly | Public Assembly | 0.30 | 217 | 0.17 | 162 |
| Religious Worship | Religious Worship | 0.25 | 119 | 0.18 | 79 |
| Service | Service | 0.25 | 173 | - | - |
| Warehouse | Warehouse | 0.25 | 82 | - | - |
| Other | Other | 0.12 | 76 | 0.15 | 79 |

##### Claimed Peak Demand Savings

A summer peak period value is used for this measure. Refer to Volume 1, Section 4 for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

Pre-cooling components may consist of pumps, sprayers, electronic controllers, and evaporative media, with the evaporative media requiring periodic replacement.

The EUL for Evaporative Pre-cooling System is 10 years, consistent with the typical manufacturer warranty for evaporative pre-cooling equipment.

#### Program Tracking Data and Evaluation Requirements

The below list of primary inputs and contextual data is recommended to be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Decision/action type: Retrofit or new construction

- Building type

- Climate zone

- Baseline equipment type

- Baseline equipment rated cooling capacity

- Baseline equipment cooling efficiency ratings

- Baseline number of units

- Baseline manufacturer and model

- Installed number of units

- Installed evaporative pre-cooling system manufactuer and model

- Installed evaporative pre-cooling system evaporative effectiveness

- Copy of operation manuals

- For Other building types only: A description of the actual building type, the primary business activity, the business hours, and the HVAC schedule.

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 47612—Provides deemed savings for Condenser Evaporative Pre-cooling

##### Relevant Standards and Reference Sources

Not applicable.

### Computer Room Air Conditioners Measure Overview

TRM Measure ID: NR-HV-CR

Market Sector: Commercial

Measure Category: HVAC

Applicable Building Types: See Table 79 and Table 80

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Calculator

#### Measure Description

This section summarizes the deemed savings methodology for the installation of computer room air conditioning (CRAC) systems. A CRAC unit is a device that monitors and maintains the temperature, air distribution, and humidity in a network room or data center. This measure covers assumptions made for baseline equipment efficiencies for early retirement (ER) based on the age of the replaced equipment and replace-on-burnout (ROB) and new construction (NC) situations based on efficiency standards. Savings calculations incorporate the use of only part-load efficiency values, as these types of units are only rated in units of seasonal COP (SCOP). For ER, the actual age of the baseline system should be determined from the equipment nameplate or other physical documentation whenever possible. If the actual age of the unit is unknown, default values are provided.

##### Eligibility Criteria

For a measure to be eligible to use this deemed savings approach, the following conditions must be met:

- The existing and proposed cooling equipment is electric

- The building type is a network room or data center

- For early retirement projects: ER projects involve the replacement of a working system. Additionally, the ER approach cannot be used for projects involving a renovation where a major structural change or internal space remodel has occurred. A ROB approach should be used for these scenarios.

- In the event that these conditions are not met, the deemed savings approach cannot be used, and the Simplified M&V Methodology or the Full M&V Methodology must be used.

Manufacturer datasheets for installed equipment or documentation of AHRI or DOE CCMS certification must be provided.,

##### Baseline Condition

The baseline conditions related to efficiency and system capacity for early retirement and replace-on-burnout/new construction are as follows:

Early Retirement

Early retirement projects should claim savings using the replace-on-burnout/new construction baseline, as no additional savings are specified for early retirement projects. This section will not apply until the current baseline is updated, allowing the measure to refer to the existing baseline for early retirement projects.

Replace-on-Burnout (ROB) and New Construction (NC)

Baseline efficiency levels for CRACs are provided in Table 78. These baseline efficiency levels reflect the minimum efficiency requirements from IECC 2015, which uses the Sensible Coefficient of Performance (SCOP) as the standard efficiency metric.

Table 78: Baseline Efficiency Levels for ROB and NC CRACs

| System Type | Cooling Capacity [Btu/hr] | Baseline Efficiencies for Downflow/Upflow Units (SCOP) | Source |
| --- | --- | --- | --- |
| Air conditioners, air cooled | < 65,000 | 2.20 / 2.09 | IECC 2015 |
|  | > 65,000 and < 240,000 | 2.10 / 1.99 |  |
|  | > 240,000 | 1.90 / 1.79 |  |
| Air conditioners, water cooled | < 65,000 | 2.60 / 2.49 |  |
|  | > 65,000 and < 240,000 | 2.50 / 2.39 |  |
|  | > 240,000 | 2.40 / 2.29 |  |
| Air conditioners, water cooled with fluid economizer | < 65,000 | 2.55 / 2.44 |  |
|  | > 65,000 and < 240,000 | 2.45 / 2.34 |  |
|  | > 240,000 | 2.35 / 2.24 |  |
| Air conditioners, glycol cooled (rated at 40% propylene glycol) | < 65,000 | 2.50 / 2.39 |  |
|  | > 65,000 and < 240,000 | 2.15 / 2.04 |  |
|  | > 240,000 | 2.10 / 1.99 |  |
| Air conditioners, glycol cooled (rated at 40% propylene glycol) with fluid economizer | < 65,000 | 2.45 / 2.34 |  |
|  | > 65,000 and < 240,000 | 2.10 / 1.99 |  |
|  | > 240,000 | 2.05 / 1.94 |  |

##### High-efficiency Condition

Package and split-systems must exceed the minimum efficiencies specified in Table 25.

Additional conditions for replace-on-burnout, early retirement, and new construction are as follows:

New Construction and Replace on Burnout

This scenario includes equipment used for new construction and retrofit/replacements that are not covered by early retirement, such as units that are replaced after natural failure.

Early Retirement

Early retirement projects should claim savings using the replace-on-burnout/new construction baseline, as no additional savings are specified for early retirement projects. This section will not apply until the current baseline is updated, allowing the measure to refer to the existing baseline for early retirement projects.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Peak Demand [kWSavings,C]=CapC,preηbaseline,C-CapC,postηinstalled,C×DFC×1 kW3,412 Btuh

Equation 54

Energy Cooling kWhSavings,C=CapC,preηbaseline,C-CapC,postηinstalled,C×EFLHC×1 kWh3,412 Btu

Equation 55

Where:

CapC,pre	=	Rated equipment cooling capacity of the newly installed equipment at AHRI standard conditions [Btuh]; 1 ton = 12,000 Btuh

CapC,post	=	Rated equipment cooling capacity of the newly installed equipment at AHRI standard conditions [Btuh]; 1 ton = 12,000 Btuh

ηbaseline,C	= 	Cooling efficiency of existing equipment (ER) or standard equipment (ROB/NC) [SCOP]

ηinstalled,C	=	Rated cooling efficiency of the newly installed equipment (SCOP)—(Must exceed ROB/NC baseline efficiency standards in Table 25) [SCOP]

Note: Use SCOP for both kW and kWh savings calculations.

DF	=	Seasonal peak demand factor for appropriate climate zone and equipment type (Table 28)

EFLHC	=	Cooling equivalent full-load hours for appropriate climate zone and equipment type [hours] (Table 28)

Early Retirement Savings

Early retirement projects should claim savings using the replace-on-burnout/new construction baseline, as no additional savings are specified for early retirement projects. This section will not apply until the current baseline is updated, allowing the measure to refer to the existing baseline for early retirement projects.

##### Deemed Energy and Demand Savings Tables

Deemed peak demand factor (DF) and equivalent full-load hour (EFLH) values are presented by building type and climate zone. This measure is restricted to data center building types, derived from the EIA CBECS study.

The DF and EFLH values for CRAC units are presented in Table 80. A description of the calculation method used to derive these values can be found in Docket No. 40885, Attachment B.

Table 79: Commercial CRAC Building Type Descriptions and Examples

| Building Type | Principal Building Activity | Definition | Detailed Business Type Examples |
| --- | --- | --- | --- |
| Data Center | Data Center | Buildings used to house computer systems and associated components. | 1) Data Center |

Table 80: DF and EFLH Values for All Climate Zones

| Climate Zone Reference City | Building Type and Principal Building Activity | CRACs |  |
| --- | --- | --- | --- |
|  |  | DFC | EFLHC |
| Climate Zone 1: Amarillo | Data Center | 0.89 | 2,048 |
| Climate Zone 2: Dallas |  | 1.08 | 3,401 |
| Climate Zone 3: Houston |  | 1.05 | 4,022 |
| Climate Zone 4: Corpus Christi |  | 0.97 | 4,499 |
| Climate Zone 5: El Paso |  | 0.88 | 2,547 |

##### Claimed Peak Demand Savings

A summer peak period value is used for this measure. Refer to Volume 1, Section 4 for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

The EUL and RULs for this HVAC equipment are provided below. The reader should refer to the definitions of effective useful life and remaining useful life in the glossary in Volume 1 for guidance on how to determine the decision type for system installations.

Effective Useful Life (EUL)

The EUL for CRACs is 15 years, consistent with the EUL specified for split and packaged air conditioners and heat pumps.

Remaining Useful Life (RUL)

This section will not apply unless the current baseline is updated, allowing the measure to refer to the existing baseline for early retirement projects.

#### Program Tracking Data and Evaluation Requirements

The below list of primary inputs and contextual data is recommended to be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Decision/action type: ER, ROB, NC, system type conversion

- Climate zone

- Baseline number of units

- Baseline equipment type

- Baseline equipment rated cooling capacity

- Installed number of units

- Installed equipment type

- Installed equipment rated cooling capacity

- Installed cooling efficiency rating

- Installed manufacturer and model

- Installed unit AHRI/DOE CCMS certificate or reference number

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 36779—Provides EUL for HVAC equipment.

- PUCT Docket 40083– Provides incorporation of early retirement savings for existing commercial HVAC SOP designs and updates for baseline equipment efficiency levels for ROB and new construction projects involving package and split systems.

- PUCT Docket 40885—Provides a petition to revise deemed savings values for Commercial HVAC replacement measures. Items covered by this petition include the following:

- Updated baseline efficiencies use for estimating deemed savings for commercial PTAC/PTHP’s, Room Air Conditioners, and chilled water systems.

- Approved estimates of RUL of working chilled water systems.

- Updated demand and energy coefficients for all commercial HVAC systems.

- Updated EUL of centrifugal chilled water systems installed in ROB or new construction projects.

- Provide a method for utilizing the early retirement concept developed in the petition in Docket No. 40083 for Packaged and Split DX systems and applied to chilled water systems when the age of the system being replaced cannot be ascertained.

- PUCT Docket 41070—Provides energy and demand savings coefficients for an additional climate zone, El Paso, TX. Prior to this filing, savings for the Dallas-Fort Worth area were used for El Paso, but Dallas-Fort Worth has a colder winter, somewhat more moderate summer, more sunshine, and less precipitation than El Paso.

- PUCT Docket 43681—Updated the approach for calculating early replacement energy and demand savings using a net present value (NPV) method. Documented in Appendix A.

##### Relevant Standards and Reference Sources

- ANSI/ASHRAE/IES Standard 90.1-2010. Energy Standard for Buildings Except Low-Rise Residential Buildings. Table 6.8.1A through Table 6.8.1D.

- ANSI/ASHRAE/IES Standard 90.1-2010. Energy Standard for Buildings Except Low-Rise Residential Buildings. Table 6.8.1-1 and Table 6.8.1-2.

- 2015 International Energy Conservation Code. Table C403.2.3(1) and Table C403.2.3(2).

- Code of Federal Regulations. Title 10. Part 431—Energy Efficiency Program for Certain Commercial and Industrial Equipment. https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=31.

### High-Volume Low-Speed (HVLS) Fans Measure Overview

TRM Measure ID: NR-HV-HF

Market Sector: Commercial

Measure Category: HVAC

Applicable Business Types: Agriculture

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

Circulation fans are used in agricultural applications such as dairy, swine, or poultry barns to destratify air, reduce animal heat stress, control insects, dry surfaces, and cool people and animals. This measure applies to the installation of high-volume low-speed (HVLS) fans in a horizontal orientation in such agricultural applications. HVLS fans may be installed in lieu of conventional (small diameter) circulation fans in new construction applications or in replacement of existing (still functioning) conventional circulation fans in retrofit projects.

Deemed savings are provided for displaced fan load only: applications in which HVLS fans are installed to reduce air conditioning requirements may be considered in the future: for now, such applications would require additional M&V to demonstrate (and claim) complete savings.

##### Eligibility Criteria

While many applications exist for HVLS fans, the guidance in this measure is specific to agricultural operations. Savings estimates may be developed for other applications in future iterations of the TRM.

HVLS fans may be used to replace existing conventional circulating fans or installed in new barns. To claim savings for a retrofit, the conventional fans being replaced should be in proper working condition.

Default values are provided for dairy applications while other facility types are eligible and should use the dairy values until other livestock specific factors are developed.

##### Baseline Condition

The baseline condition is an installation of conventional fans.

Retrofit (Early Retirement)

When replacing existing (working) fans, the baseline is set by the number of fans to be replaced, with power requirements calculated according to their operating airflow rates (CFM), and rated efficiency (e.g., CFM/watt).

Replace on Burnout/New Construction

When existing fans are reaching the end of their useful life, or for new construction, the baseline assumes installation of conventional fans that would produce a comparable total airflow (CFM) as the HVLS fan to be installed.

##### High-efficiency Condition

HVLS fans with diameters of eight to 24 feet typically use 1 hp to 2 hp motors per fan and move between 50,000 CFM and 150,000 or more CFM. To be eligible for this measure, HVLS fans shall be a minimum of 8 feet in diameter and move more cubic feet of air per watt than conventional circulating fans. The fan should be installed in a horizontal orientation and have the ability to operate at different speeds.

#### Energy and Demand Savings Methodology

Savings are estimated assuming operation of the baseline (conventional) and high efficiency (HVLS) fans at their rated speed and power input during all hours of expected use.

##### Savings Algorithms and Input Variables

Energy Savings kWh=Wbase- WHVLS1000×Hours

Equation 56

Summer Demand Savings (kW) =Wbase- WHVLS1000×CF

Equation 57

Where:

Wbase	=	power input required to move replaced fans at rated speed

WHVLS	=	power input required to move installed HVLS fans at rated speed

Hours	=	hours of operation in the project application, as described below

CF	=	coincidence factor (1.0, as fans are always operating in summer peak conditions)

Retrofit (Early Retirement)

For early retirement projects, the base wattage (Wbase) is estimated according to the number of fans replaced and their rated efficiency:

Wbase,ER=CFMbase*Nbaseηbase

Equation 58

Where:

CFMbase	=	airflow rate produced by replaced fans

ηbase	=	efficacy of replaced fans (CFM/watt)

Note: For retrofit projects where the baseline equipment ratings cannot be determined, the use of the replace-on-burnout/new construction calculation procedure is permitted.

Replace-on-Burnout/New Construction

For replace-on-burnout or new construction projects, base case power requirements are estimated for conventional fans producing an equivalent/comparable airflow (CFM) as that of the HVLS fan(s) being installed. The efficiency of the baseline conventional fans shall be 22 CFM/watt.

Wbase,ROB/NC=CFMHVLS22 CFM/W

Equation 59

Hours of Operation

Table 81 provides the hours to be used in calculating energy savings for HVLS fan installation by climate zone.

Table 81: Hours of Circulating Fan Operation by Barn Type

| Climate Zone | Hours |
| --- | --- |
| Climate Zone 1: Amarillo | 2,215 |
| Climate Zone 2: Dallas | 3,969 |
| Climate Zone 3: Houston | 4,750 |
| Climate Zone 4: Corpus Christi | 5,375 |
| Climate Zone 5: El Paso | 3,034 |

##### Claimed Peak Demand Savings

Demand savings shall be claimed according to the Summer Demand Savings estimated using Equation 57, above. While there is a strong case for winter operation of HVLS fans in reverse for circulating warm air trapped below the roof back to the ground, this operation is not currently considered and as such there are no winter demand savings developed for this measure.

A coincidence factor of 1.0 should be used to calculate the summer demand savings for this measure, as the criteria for whether fans will be operating or not are always met during peak hours as defined in Section 4 of Volume 1 of this TRM.

##### Deemed Energy and Demand Savings Tables

This section is not applicable as these calculations are entirely dependent on site-specific parameters.

##### Measure Life and Lifetime Savings

The EUL of an HVLS fan is closely related to that of its motor. The US DOE Advanced Manufacturing Office’s Motor Systems Tip Sheet #3 suggests motors should last approximately 35,000 hours. The average annual hours of operation in dairy farms for the Texas TRM zones is about 3,870 hours. Accordingly, the EUL for HVLS fans in Texas is estimated to be 9 years.

#### Program Tracking Data and Evaluation Requirements

The below list of primary inputs and contextual data is recommended to be specified and tracked by the program database to inform the evaluation and apply the savings properly.

All Projects:

- Barn type (animal)

- Climate zone

- Decision/action type: ROB, NC, or ER

- HVLS fan(s): diameter

- HVLS fan(s): rated HP

- HVLS fan(s): rated CFM

- HVLS fan(s): count

- For early retirement only: replaced fans: count

- For early retirement only: replaced fans: diameter

- For early retirement only: replaced fans: rated HP

- For early retirement only: replaced fans: rated CFM

- For early retirement only: replaced fans: rated CFM/watt

#### References and Efficiency Standards

##### Petitions and Rulings

None

##### Relevant Standards and Reference Sources

- Kammel, David and Raabe, and Kappelman, J.. (2003). Design of high-volume low-speed fan supplemental cooling system in dairy freestall barns. Proceedings of the Fifth International Dairy Housing Conference. 10.13031/2013.11628. Online. Available: https://www.researchgate.net/publication/271433461_Design_of_high_volume_low_speed_fan_supplemental_cooling_system_in_dairy_freestall_barns.

- https://macroairfans.com/wp-content/uploads/2012/03/Horse-Barn-Ventilation-White-Paper.pdf

- BESS Laboratory Database of Agricultural Fans. Bioenvironmental and Structural Systems Laboratory of the Agricultural and Biological Engineering Dept., University of Illinois at Urbana-Champagne. Online. Data for Circulating Fans available: http://www.bess.illinois.edu/currentc.asp.

### Computer Room Air Handler (CRAH) Motor Efficiency Measure Overview

TRM Measure ID: NS-HV-CM

Market Sector: Commercial

Measure Category: HVAC

Applicable Building Types: Data Centers

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed Savings Calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This measure involves improving the operational efficiency of a computer room air handler (CRAH) through the installation of a variable frequency drive (VFD) or electronically commutated motor (ECM). Savings for this measure include fan motor savings resulting from the ability to modulate the fan speed. Any associated cooling energy savings are not captured.

##### Eligibility Criteria

Eligible equipment includes fan motors and VFDs, 15 horsepower and smaller used to distribute conditioned air throughout a data center.

##### Baseline Condition

The CRAH baseline is a conventional AC motor driven, constant speed fan.

##### High-efficiency Condition

The high-efficiency condition is the installation of a variable frequency drive (VFD) and/or electronically commutated motor (ECM).

##### Savings Algorithms and Input Variables

##### Energy and demand savings are estimated using input assumptions taken from site measured motor kW and operating hours for 243 CRAH units.

Energy Savings Algorithms

Annual Energy Savings kWh=kWprekWhppre×hppre-kWhppost×hppost×hours

Equation 60

kWpre=0.746×hppre×LFη

Equation 61

Where:

kW/hppre		=	rated horsepower of the existing motor

LF			=	Load factor—ratio of the operating load to the nameplate rating of the motor—assumed to be 75% at the fan or pump design 100% per DEER

η	=	Motor efficiency of a standard efficiency Open Drip Proof (ODP) motor operating at 1800 RPM taken from ASHRAE Standard 90.1-2013

| Motor Horsepower | Full Load Efficiency |
| --- | --- |
| 1 | 0.855 |
| 2 | 0.865 |
| 3 | 0.895 |
| 5 | 0.895 |
| 7.5 | 0.91 |
| 10 | 0.917 |
| 15 | 0.93 |

0.746	=	HP to kW conversion factor

kW/hppost	=	efficient kW per motor hp, 0.27

hppre

hppost		=	total efficient motor horsepower

hours		=	annual operating hours, 8760

Demand Savings Algorithms

Demand Savings kW=Annual Energy Savings kWhhours×CF

Equation 62

Where:

CF	=	peak coincidence factor, summer and winter: 0.11

##### Deemed Energy and Demand Savings Tables

##### There are no deemed savings tables for this measure.

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

##### The median estimated useful life (EUL) premium efficiency motors is 15 years.

The estimated useful life (EUL) for HVAC VFD measure is 15 years.

#### Program Tracking Data and Evaluation Requirements

The below list of primary inputs and contextual data is recommended to be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Motor quantity, type, horsepower, and control; pre-installation

- Motor quantity, type, horsepower, and control; post-installation

- Climate zone

#### References and Efficiency Standards

##### Petitions and Rulings

##### Relevant Standards and Reference Sources

## Nonresidential: Building Envelope

### Cool Roofs Measure Overview

TRM Measure ID: NR-BE-CR

Market Sector: Commercial

Measure Category: Building envelope

Applicable Building Types: All commercial

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Energy modeling, engineering algorithms, and estimates

#### Measure Description

Reflective roofing materials reduce the overall heat load on a building by reducing the total heat energy absorbed into the building system from incident solar radiation. This reduction in total load provides space cooling energy savings during the cooling season but reduces free heat during the heating season, so the measure saves energy in the summer but uses more energy in winter. Cool roofs are most beneficial in warmer climates and may not be recommended for buildings where the primary heat source is electric resistance. The measure is for retrofit of existing buildings.

##### Eligibility Criteria

Measures installed through utility programs must be a roof that is compliant with the current ENERGY STAR® specification, effective July 2017. For nonresidential facilities, these criteria for a high-efficiency roof include:

- An existing roof undergoing retrofit conditions as further defined under high-efficiency condition below; a roof installed in a new construction application is not eligible for applying these methodologies.

- A roof with a low-slope of 2:12 inches or less

- An initial solar reflectance of greater than or equal to 65 percent

- Maintenance of solar reflectance of greater than or equal to 50 percent three years after installation under normal conditions

- 75 percent of the roof surface over conditioned space must be replaced

- No significant obstruction of direct sunlight to roof

- The facility must be conditioned with cooling, heating, or both

- Be listed on the ENERGY STAR® list of qualified products or have a performance rating that is validated by the Cool Roof Rating Council (CRRC). ENERGY STAR® test criteria allows for products already participating in the CRRC Product Rating Program to submit solar reflectance and thermal emittance product information derived from CRRC certification.

- The ENERGY STAR® specification for roof products will sunset effective June 1, 2022. No new roof products will be certified as of June 1, 2021. At this point, ENERGY STAR® legacy or CRRC product certification will be required to demonstrate compliance with the previous ENERGY STAR® specification.

If one of these conditions is not met, the deemed savings approach cannot be used, and the Simplified M&V Methodology or the Full M&V Methodology must be used.

##### Baseline Condition

The baseline is the thermal resistance (i.e., R-value) of the existing roof make-up and the solar reflectance and emissivity of the surface layer. The R-value is estimated based on code envelope requirements applicable in the year of construction. Solar reflectance and emissivity of the surface layer are assumed to be 0.2 and 0.9, respectively, based on roof properties listed in the LBLN Roofing Materials Database.

The cooling and heating efficiencies are assumed based on the space conditioning of the top floor of the building and are based on typical code requirements applicable in the year of construction.

Table 82. Cool Roofs – Assumed Cooling and Heating Efficiencies (COP)

| Year of Construction; Applicable Code | RTU | PTHP Cooling | PTHP Heating | Air Cooled Chiller | Water Cooled Chiller |
| --- | --- | --- | --- | --- | --- |
| Before 2011; 2000 IECC | 2.9 | 2.9 | 2.9 | 2.5 | 4.2 |
| Between 2011-2016; 2009 IECC | 3.8 | 3.1 | 2.9 | 2.8 | 5.5 |
| After 2016; 2015 IECC | 3.8 | 3.1 | 2.9 | 2.8 | 5.5 |

##### High-Efficiency Condition

The high-efficiency condition depends on the project scope. The project scope is defined as one of:

- Adding surface layer only

- Adding insulation and surface layer

- Rebuilding entire roof assembly

If the project scope is only to add a new ENERGY STAR® material as the new surface layer, then the R-value used for the baseline condition is used for the high-efficiency condition. If the project scope is to add insulation and an ENERGY STAR® material as the new surface layer, then the R-value of the additional insulation is added to the R-value used for the baseline condition. If the entire roof assembly is rebuilt, then the R-value for each layer of the new roof construction is summed to get a total new R-value.

The measure requires installation of roof products that have been rated by the CRRC and demonstrate compliance with ENERGY STAR® certified roof product performance specifications for the relevant roof application. Initial and 3-year reflectance ratings must meet or exceed the minimum thresholds specified in Table 83.

Table 83. Cool Roofs – ENERGY STAR® Specification

| Roof Slope | Characteristic | Performance Specification |
| --- | --- | --- |
| Low Slope < 2/12 | Initial Solar Reflectance | > 0.65 |
|  | 3-Year Solar Reflectance | > 0.50 |

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Energy savings are estimated using EnergyPlus v8.3.0 whole-building simulation. The prototype building characteristics match those used for developing commercial HVAC demand factors and EFLH and can be found from Table 85 through Table 89. The savings represent the difference of the modeled energy use of the baseline condition and the high-efficiency condition divided by the square foot of the roof area. The demand savings are calculated following the method described in TRM Volume 1.

The deemed energy and demand savings factors are used in the following formulas to calculate savings:

Energy Savings=Roof Area×ESF

Equation 63

Peak Summer Demand Savings=Roof Area×PSDF×10-5

Equation 64

Peak Winter Demand Savings=Roof Area×PWDF×10-6

Equation 65

Where:

Roof Area	=	Total area of ENERGY STAR® roof in square feet

ESF	=	Energy Savings Factor from Table 85 through Table 89 by building type, pre/post insulation levels, and heating/cooling system.

PSDF	=	Peak Summer Demand Factor from Table 85 through Table 89 by building type, pre/post insulation levels, and heating/cooling system.

PWDF	=	Peak Winter Demand Savings Factor from Table 85 through Table 89 by building type, pre/post insulation levels, and heating/cooling system.

If the insulation levels are unknown, use the mapping in Table 84 to estimate the R-value based on the year of construction.

Table 84. Cool Roofs – Estimated R-value based on Year of Construction

| Year of Construction | Estimated R-value |
| --- | --- |
| Before 2011 | R ≤ 13 |
| Between 2011 - 2016 | 13 < R ≤ 20 |
| After 2016 | 20 < R |

Table 85. Cool Roofs – Savings Factors for Amarillo (Climate Zone 1)

| Building Type | Pre R-Value | Post R-Value | ESF | PSDF | PWDF |
| --- | --- | --- | --- | --- | --- |
| Retail | R ≤ 13 | R ≤ 13 | 0.72 | 19.28 | 31.74 |
|  | R ≤ 13 | 13 < R ≤ 20 | 1.26 | 36.23 | 36.71 |
|  | R ≤ 13 | 20 < R | 1.25 | 38.58 | 35.31 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.13 | 4.81 | 1.88 |
|  | 13 < R ≤ 20 | 20 < R | 0.12 | 6.47 | 0.48 |
|  | 20 < R | 20 < R | 0.09 | 3.32 | 1.30 |
| Education - Chiller | R ≤ 13 | R ≤ 13 | 0.65 | 11.80 | 8.31 |
|  | R ≤ 13 | 13 < R ≤ 20 | 1.10 | 21.76 | 31.52 |
|  | R ≤ 13 | 20 < R | 1.25 | 25.53 | 37.31 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.26 | 4.85 | 4.59 |
|  | 13 < R ≤ 20 | 20 < R | 0.38 | 7.80 | 9.20 |
|  | 20 < R | 20 < R | 0.17 | 3.40 | 1.17 |
| Education - RTU | R ≤ 13 | R ≤ 13 | 0.26 | 8.26 | 2.62 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.43 | 15.47 | 12.49 |
|  | R ≤ 13 | 20 < R | 0.49 | 18.20 | 14.02 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.12 | 4.11 | 2.05 |
|  | 13 < R ≤ 20 | 20 < R | 0.18 | 6.67 | 3.58 |
|  | 20 < R | 20 < R | 0.08 | 2.91 | 0.28 |
| Office - Chiller | R ≤ 13 | R ≤ 13 | 0.21 | 6.80 | 1.43 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.31 | 3.44 | 3.50 |
|  | R ≤ 13 | 20 < R | 0.33 | 19.30 | 3.87 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.09 | 16.58 | 0.11 |
|  | 13 < R ≤ 20 | 20 < R | 0.11 | 5.94 | 0.47 |
|  | 20 < R | 20 < R | 0.06 | 2.36 | 0.08 |
| Office - RTU | R ≤ 13 | R ≤ 13 | 0.28 | 7.46 | 11.88 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.87 | 15.48 | 168.51 |
|  | R ≤ 13 | 20 < R | 1.10 | 18.61 | 236.76 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.15 | 4.12 | -1.23 |
|  | 13 < R ≤ 20 | 20 < R | 0.38 | 6.73 | 67.02 |
|  | 20 < R | 20 < R | 0.11 | 2.92 | -2.61 |
| Hotel | R ≤ 13 | R ≤ 13 | 0.07 | 1.33 | -2.60 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.07 | 1.83 | 6.98 |
|  | R ≤ 13 | 20 < R | 0.07 | 2.03 | 11.77 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.04 | 0.81 | -1.45 |
|  | 13 < R ≤ 20 | 20 < R | 0.04 | 1.00 | 3.39 |
|  | 20 < R | 20 < R | 0.03 | 0.60 | -1.12 |
| Warehouse | R ≤ 13 | R ≤ 13 | 0.04 | 3.83 | -0.20 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.11 | 6.99 | 3.89 |
|  | R ≤ 13 | 20 < R | 0.14 | 8.07 | 5.35 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.01 | 1.35 | -0.10 |
|  | 13 < R ≤ 20 | 20 < R | 0.04 | 2.24 | 1.36 |
|  | 20 < R | 20 < R | 0.01 | 0.90 | -0.07 |
| Other | R ≤ 13 | R ≤ 13 | 0.04 | 1.33 | -2.60 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.07 | 1.83 | 3.50 |
|  | R ≤ 13 | 20 < R | 0.07 | 2.03 | 3.87 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.01 | 0.81 | -1.45 |
|  | 13 < R ≤ 20 | 20 < R | 0.04 | 1.00 | 0.47 |
|  | 20 < R | 20 < R | 0.01 | 0.60 | -2.61 |

Table 86. Cool Roofs – Savings Factors for Dallas (Climate Zone 2)

| Building Type | Pre R-Value | Post R-Value | ESF | PSDF | PWDF |
| --- | --- | --- | --- | --- | --- |
| Retail | R ≤ 13 | R ≤ 13 | 0.61 | 22.03 | 13.53 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.97 | 37.67 | 17.30 |
|  | R ≤ 13 | 20 < R | 0.98 | 40.54 | 17.32 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.16 | 7.57 | 1.28 |
|  | 13 < R ≤ 20 | 20 < R | 0.17 | 9.67 | 1.29 |
|  | 20 < R | 20 < R | 0.13 | 6.22 | 1.04 |
| Education - Chiller | R ≤ 13 | R ≤ 13 | 0.56 | 10.49 | 5.11 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.82 | 16.50 | 8.60 |
|  | R ≤ 13 | 20 < R | 0.92 | 18.86 | 11.17 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.29 | 5.41 | 2.36 |
|  | 13 < R ≤ 20 | 20 < R | 0.36 | 7.28 | 4.55 |
|  | 20 < R | 20 < R | 0.24 | 4.37 | 1.88 |
| Education - RTU | R ≤ 13 | R ≤ 13 | 0.27 | 10.65 | 1.53 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.39 | 18.31 | 3.68 |
|  | R ≤ 13 | 20 < R | 0.43 | 21.33 | 4.89 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.17 | 7.21 | 0.77 |
|  | 13 < R ≤ 20 | 20 < R | 0.21 | 10.08 | 1.97 |
|  | 20 < R | 20 < R | 0.13 | 5.88 | 0.60 |
| Office - Chiller | R ≤ 13 | R ≤ 13 | 0.23 | 11.99 | 0.81 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.33 | 27.48 | 1.78 |
|  | R ≤ 13 | 20 < R | 0.34 | 30.55 | 1.93 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.13 | 6.68 | 0.10 |
|  | 13 < R ≤ 20 | 20 < R | 0.15 | 9.76 | 0.26 |
|  | 20 < R | 20 < R | 0.10 | 6.01 | 0.08 |
| Office - RTU | R ≤ 13 | R ≤ 13 | 0.27 | 12.14 | 14.86 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.52 | 24.53 | 84.63 |
|  | R ≤ 13 | 20 < R | 0.62 | 29.45 | 112.16 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.18 | 7.25 | 11.53 |
|  | 13 < R ≤ 20 | 20 < R | 0.28 | 11.09 | 39.06 |
|  | 20 < R | 20 < R | 0.15 | 6.03 | 8.66 |
| Hotel | R ≤ 13 | R ≤ 13 | 0.07 | 1.71 | -0.64 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.07 | 2.30 | 0.78 |
|  | R ≤ 13 | 20 < R | 0.07 | 2.56 | 1.39 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.05 | 1.17 | -0.46 |
|  | 13 < R ≤ 20 | 20 < R | 0.05 | 1.42 | 0.17 |
|  | 20 < R | 20 < R | 0.05 | 1.01 | -0.36 |
| Warehouse | R ≤ 13 | R ≤ 13 | 0.05 | 4.01 | -0.07 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.09 | 6.54 | 1.47 |
|  | R ≤ 13 | 20 < R | 0.16 | 11.16 | 2.38 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.02 | 1.18 | -0.05 |
|  | 13 < R ≤ 20 | 20 < R | 0.08 | 4.94 | 0.86 |
|  | 20 < R | 20 < R | 0.01 | 1.02 | -0.03 |
| Other | R ≤ 13 | R ≤ 13 | 0.05 | 1.71 | -0.64 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.07 | 2.30 | 0.78 |
|  | R ≤ 13 | 20 < R | 0.07 | 2.56 | 1.39 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.02 | 1.17 | -0.46 |
|  | 13 < R ≤ 20 | 20 < R | 0.05 | 1.42 | 0.17 |
|  | 20 < R | 20 < R | 0.01 | 1.01 | -0.36 |

Table 87. Cool Roofs – Savings Factors for Houston (Climate Zone 3)

| Building Type | Pre R-Value | Post R-Value | ESF | PSDF | PWDF |
| --- | --- | --- | --- | --- | --- |
| Retail | R ≤ 13 | R ≤ 13 | 0.62 | 17.21 | 9.86 |
|  | R ≤ 13 | 13 < R ≤ 20 | 1.00 | 29.60 | 17.11 |
|  | R ≤ 13 | 20 < R | 1.01 | 31.61 | 16.52 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.41 | 10.43 | 7.67 |
|  | 13 < R ≤ 20 | 20 < R | 0.41 | 11.89 | 7.07 |
|  | 20 < R | 20 < R | 0.14 | 4.66 | 1.07 |
| Education - Chiller | R ≤ 13 | R ≤ 13 | 0.62 | 9.56 | -0.28 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.87 | 15.28 | 3.52 |
|  | R ≤ 13 | 20 < R | 0.95 | 17.53 | 4.52 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.33 | 5.04 | -0.28 |
|  | 13 < R ≤ 20 | 20 < R | 0.39 | 6.81 | 0.50 |
|  | 20 < R | 20 < R | 0.26 | 4.05 | -0.29 |
| Education - RTU | R ≤ 13 | R ≤ 13 | 0.29 | 9.39 | -0.03 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.40 | 15.76 | 0.90 |
|  | R ≤ 13 | 20 < R | 0.44 | 18.26 | 1.08 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.18 | 6.21 | -0.01 |
|  | 13 < R ≤ 20 | 20 < R | 0.22 | 8.58 | 0.16 |
|  | 20 < R | 20 < R | 0.14 | 5.08 | -0.07 |
| Office - Chiller | R ≤ 13 | R ≤ 13 | 0.25 | 9.45 | 0.70 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.33 | 21.39 | 1.26 |
|  | R ≤ 13 | 20 < R | 0.34 | 23.54 | 1.23 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.17 | 10.75 | 0.65 |
|  | 13 < R ≤ 20 | 20 < R | 0.18 | 12.84 | 0.61 |
|  | 20 < R | 20 < R | 0.12 | 4.54 | 0.12 |
| Office - RTU | R ≤ 13 | R ≤ 13 | 0.28 | 8.30 | 6.91 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.46 | 18.66 | 37.60 |
|  | R ≤ 13 | 20 < R | 0.54 | 22.36 | 50.18 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.19 | 5.42 | 4.29 |
|  | 13 < R ≤ 20 | 20 < R | 0.26 | 8.39 | 16.87 |
|  | 20 < R | 20 < R | 0.15 | 4.35 | 3.35 |
| Hotel | R ≤ 13 | R ≤ 13 | 0.08 | 1.69 | 0.54 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.07 | 2.26 | 0.17 |
|  | R ≤ 13 | 20 < R | 0.07 | 2.50 | -0.02 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.06 | 1.21 | 0.37 |
|  | 13 < R ≤ 20 | 20 < R | 0.05 | 1.43 | 0.21 |
|  | 20 < R | 20 < R | 0.05 | 1.03 | 0.32 |
| Warehouse | R ≤ 13 | R ≤ 13 | 0.05 | 2.96 | -0.09 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.09 | 5.13 | 0.76 |
|  | R ≤ 13 | 20 < R | 0.16 | 9.21 | 1.26 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.02 | 1.32 | -0.07 |
|  | 13 < R ≤ 20 | 20 < R | 0.08 | 4.66 | 0.43 |
|  | 20 < R | 20 < R | 0.01 | 0.79 | 0.08 |
| Other | R ≤ 13 | R ≤ 13 | 0.05 | 1.69 | -0.28 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.07 | 2.26 | 0.17 |
|  | R ≤ 13 | 20 < R | 0.07 | 2.50 | -0.02 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.02 | 1.21 | -0.28 |
|  | 13 < R ≤ 20 | 20 < R | 0.05 | 1.43 | 0.16 |
|  | 20 < R | 20 < R | 0.01 | 0.79 | -0.29 |

Table 88. Cool Roofs – Savings Factors for Corpus Christi (Climate Zone 4)

| Building Type | Pre R-Value | Post R-Value | ESF | PSDF | PWDF |
| --- | --- | --- | --- | --- | --- |
| Retail | R ≤ 13 | R ≤ 13 | 0.62 | 13.05 | 54.33 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.99 | 21.99 | 35.94 |
|  | R ≤ 13 | 20 < R | 1.00 | 23.21 | 34.63 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.41 | 8.08 | 16.20 |
|  | 13 < R ≤ 20 | 20 < R | 0.41 | 8.95 | 14.89 |
|  | 20 < R | 20 < R | 0.13 | 3.42 | 2.05 |
| Education - Chiller | R ≤ 13 | R ≤ 13 | 0.60 | 8.46 | 0.28 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.83 | 13.55 | 17.33 |
|  | R ≤ 13 | 20 < R | 0.90 | 15.49 | 30.14 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.31 | 4.48 | -3.69 |
|  | 13 < R ≤ 20 | 20 < R | 0.36 | 6.00 | 6.37 |
|  | 20 < R | 20 < R | 0.24 | 3.64 | -0.06 |
| Education - RTU | R ≤ 13 | R ≤ 13 | 0.28 | 7.34 | -0.41 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.38 | 11.78 | 5.15 |
|  | R ≤ 13 | 20 < R | 0.41 | 13.53 | 8.09 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.17 | 4.64 | -1.46 |
|  | 13 < R ≤ 20 | 20 < R | 0.20 | 6.29 | 1.47 |
|  | 20 < R | 20 < R | 0.14 | 3.77 | -0.14 |
| Office - Chiller | R ≤ 13 | R ≤ 13 | 0.22 | 6.44 | 2.33 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.31 | 13.55 | 2.86 |
|  | R ≤ 13 | 20 < R | 0.32 | 15.30 | 2.47 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.17 | 6.34 | 1.78 |
|  | 13 < R ≤ 20 | 20 < R | 0.18 | 7.96 | 1.40 |
|  | 20 < R | 20 < R | 0.10 | 3.27 | 0.45 |
| Office - RTU | R ≤ 13 | R ≤ 13 | 0.26 | 5.02 | 23.11 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.40 | 8.66 | 78.05 |
|  | R ≤ 13 | 20 < R | 0.45 | 10.09 | 100.16 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.18 | 3.61 | 15.10 |
|  | 13 < R ≤ 20 | 20 < R | 0.24 | 4.83 | 37.21 |
|  | 20 < R | 20 < R | 0.15 | 2.95 | 10.35 |
| Hotel | R ≤ 13 | R ≤ 13 | 0.07 | 1.13 | 1.99 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.07 | 1.44 | -1.23 |
|  | R ≤ 13 | 20 < R | 0.07 | 1.57 | -2.70 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.05 | 0.78 | 1.36 |
|  | 13 < R ≤ 20 | 20 < R | 0.05 | 0.90 | 0.00 |
|  | 20 < R | 20 < R | 0.04 | 0.67 | 1.19 |
| Warehouse | R ≤ 13 | R ≤ 13 | 0.05 | 2.10 | 0.22 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.09 | 3.51 | 1.39 |
|  | R ≤ 13 | 20 < R | 0.16 | 6.54 | 1.35 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.02 | 1.21 | 0.28 |
|  | 13 < R ≤ 20 | 20 < R | 0.08 | 3.71 | 0.24 |
|  | 20 < R | 20 < R | 0.01 | 0.70 | -0.07 |
| Other | R ≤ 13 | R ≤ 13 | 0.05 | 1.13 | -0.41 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.07 | 1.44 | -1.23 |
|  | R ≤ 13 | 20 < R | 0.07 | 1.57 | -2.70 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.02 | 0.78 | -3.69 |
|  | 13 < R ≤ 20 | 20 < R | 0.05 | 0.90 | 0.00 |
|  | 20 < R | 20 < R | 0.01 | 0.67 | -0.14 |

Table 89. Cool Roofs – Savings Factors for El Paso (Climate Zone 5)

| Building Type | Pre R-Value | Post R-Value | ESF | PSDF | PWDF |
| --- | --- | --- | --- | --- | --- |
| Retail | R ≤ 13 | R ≤ 13 | 0.67 | 16.55 | 42.72 |
|  | R ≤ 13 | 13 < R ≤ 20 | 1.01 | 26.85 | 67.80 |
|  | R ≤ 13 | 20 < R | 1.02 | 28.78 | 65.27 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.19 | 5.83 | 6.64 |
|  | 13 < R ≤ 20 | 20 < R | 0.19 | 7.24 | 4.12 |
|  | 20 < R | 20 < R | 0.15 | 4.74 | 5.40 |
| Education - Chiller | R ≤ 13 | R ≤ 13 | 0.69 | 9.09 | 3.85 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.97 | 14.42 | 4.87 |
|  | R ≤ 13 | 20 < R | 1.07 | 16.52 | 5.43 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.36 | 4.80 | 1.87 |
|  | 13 < R ≤ 20 | 20 < R | 0.44 | 6.47 | 2.34 |
|  | 20 < R | 20 < R | 0.28 | 3.91 | 1.19 |
| Education - RTU | R ≤ 13 | R ≤ 13 | 0.30 | 8.21 | 3.09 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.42 | 13.43 | 4.02 |
|  | R ≤ 13 | 20 < R | 0.46 | 15.49 | 4.27 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.18 | 5.16 | 1.47 |
|  | 13 < R ≤ 20 | 20 < R | 0.22 | 7.09 | 1.72 |
|  | 20 < R | 20 < R | 0.14 | 4.14 | 0.86 |
| Office - Chiller | R ≤ 13 | R ≤ 13 | 0.29 | 9.72 | 7.27 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.39 | 17.57 | 12.46 |
|  | R ≤ 13 | 20 < R | 0.42 | 20.35 | 13.25 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.17 | 6.68 | 0.12 |
|  | 13 < R ≤ 20 | 20 < R | 0.20 | 9.22 | 0.79 |
|  | 20 < R | 20 < R | 0.14 | 5.39 | 2.02 |
| Office - RTU | R ≤ 13 | R ≤ 13 | 0.31 | 9.93 | 24.02 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.55 | 16.57 | 105.15 |
|  | R ≤ 13 | 20 < R | 0.64 | 19.26 | 135.96 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.20 | 5.75 | 16.21 |
|  | 13 < R ≤ 20 | 20 < R | 0.29 | 7.78 | 47.02 |
|  | 20 < R | 20 < R | 0.16 | 4.70 | 12.77 |
| Hotel | R ≤ 13 | R ≤ 13 | 0.10 | 1.33 | 7.04 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.08 | 1.58 | 1.80 |
|  | R ≤ 13 | 20 < R | 0.08 | 1.68 | -0.78 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.07 | 0.95 | 4.98 |
|  | 13 < R ≤ 20 | 20 < R | 0.06 | 1.04 | 2.57 |
|  | 20 < R | 20 < R | 0.06 | 0.81 | 4.27 |
| Warehouse | R ≤ 13 | R ≤ 13 | 0.04 | 2.76 | -0.61 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.09 | 4.91 | 1.33 |
|  | R ≤ 13 | 20 < R | 0.15 | 8.27 | 2.06 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.02 | 1.31 | -0.42 |
|  | 13 < R ≤ 20 | 20 < R | 0.07 | 3.98 | 0.30 |
|  | 20 < R | 20 < R | 0.01 | 0.76 | -0.19 |
| Other | R ≤ 13 | R ≤ 13 | 0.04 | 1.33 | -0.61 |
|  | R ≤ 13 | 13 < R ≤ 20 | 0.08 | 1.58 | 1.33 |
|  | R ≤ 13 | 20 < R | 0.08 | 1.68 | -0.78 |
|  | 13 < R ≤ 20 | 13 < R ≤ 20 | 0.02 | 0.95 | -0.42 |
|  | 13 < R ≤ 20 | 20 < R | 0.06 | 1.04 | 0.30 |
|  | 20 < R | 20 < R | 0.01 | 0.76 | -0.19 |

##### Deemed Energy and Demand Savings Tables

There are no deemed energy or demand savings tables for this measure. Please use algorithms and inputs, as described above.

##### Claimed Peak Demand Savings

Refer to Volume 1, Section 4 for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

Estimated Useful Life is 15 years for cool roofs, as discussed in PUCT Docket Nos. 36779 and 41070. The DEER 2014 update also provides a 15-year life for cool roofs (EUL ID—BldgEnv-CoolRoof).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Climate zone or county location

- Total and treated roofing square footage (over conditioned space)

- Roof slope

- Existing roof insulation R-value, or year of building construction

- New roof insulation R-Value, if adding insulation

- New roofing initial solar reflectance

- New roofing 3-year solar reflectance

- New roofing rated life

- Copy of ENERGY STAR® certification, or alternative

- Copy of proof of purchase including date of purchase, manufacturer, and model

#### Building Type References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 36779—Provides EUL for Commercial Cool Roof

##### Relevant Standards and Reference Sources

- ENERGY STAR® Certified Cool Roof Products. http://www.energystar.gov/productfinder/product/certified-roof-products/.

- IECC 2000 Table 802.2(17), 2009 Table 502.2(1), and 2015 Table C402.1.4

- DEER 2014 EUL update.

### Window Treatments Measure Overview

TRM Measure ID: NR-BE-WT

Market Sector: Commercial

Measure Category: Building Envelope

Applicable Building Types: All commercial building types

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This section presents the deemed savings methodology for the installation of window films and solar screens. The installation of window treatments decreases the window-shading coefficient and reduces the solar heat transmitted to the building space. During months when perimeter cooling is required in the building, this measure decreases cooling energy use and summer demand.

##### Eligibility Criteria

This measure is applicable for treatment of single or double-paned clear glass windows without reflective or low-E coatings in south or west facing orientations (as specified in Table 90). Existing windows must have no solar films/screens, interior shades, or exterior awnings or overhangs and must be installed in buildings that are mechanically cooled (DX or chilled water).

This methodology may be adapted for windows with existing shading devices on an individual project basis with prior evaluator approval of baseline solar heat gain coefficient (SHGC).

##### Baseline Condition

The baseline condition is single-pane clear glass, without existing window treatments.

##### High-efficiency Condition

The high-efficiency condition is an eligible window treatment applied to eligible windows.

#### Energy and Demand Savings Methodology

The demand and energy savings equations in this section originated in calculations by the EUMMOT utilities, as presented in the EUMMOT program manual Commercial Standard Offer Program: Measurement and Verification Guidelines for Retrofit and New Construction Projects. The method estimates the reduction in solar heat gain/insolation attributable to a given window treatment using shading coefficients for the treated and untreated window and solar heat gain estimates by window orientation, according to ASHRAE Fundamentals. The reduction in building energy use attributable to the reduction in cooling system energy use is estimated based on the reduced heat removal requirement for a standard efficiency cooling system.

##### Savings Algorithms and Input Variables

Demand Savingso kW=Afilm,o×SHGFo×SHGCpre, o-SHGCpost,o34123×COP

Equation 66

Peak Demand Savings kW=DemandSavingo, max

Equation 67

Energy Savingso kWh= Afilm,o×SHGo×SHGCpre, o-SHGCpost,o34123×COP

Equation 68

Energy Savings kWh= Energy Savingso

Equation 69

Where:

Demand Savings 	=		Peak demand savings per window orientation

Energy Savings		=		Energy savings per window orientation

Afilm,o		=		Area of window film/screens applied to orientation [ft2]

SHGFo	=		Peak solar heat gain factor for orientation of interest [Btu/hr-ft2-year]. See Table 90.

SHGo		=		Solar heat gain for orientation of interest [Btu/ft2-year]. See Table 90.

SHGCpre		=	Solar heat gain coefficient for existing glass with no interior-shading device. See Table 91.

SHGCpost		=	Solar heat gain coefficient for new film/interior-shading device, from manufacturer specs

Note: Shading coefficients (SC) have been retired, but if a product specification lists SC instead of SHGC, you can convert to SHGC by multiplying SC by 0.87.

COP		=	Cooling equipment COP based on Table 92 or actual COP equipment, whichever is greater; if building construction year is unknown, assume IECC 2009 as applicable code

3412		=		Conversion factor [Btu/kWh]

Table 90: Window Treatments – Solar Heat Gain Factors

| Orientation | Solar Heat Gain (SHG) [Btu/ft2-year] | Peak Hour Solar Heat Gain (SHGF) [Btu/hr-ft2-year] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 |
| South-East | 158,844 | 28 | 30 | 26 | 27 | 35 |
| South-South-East | 134,794 | 28 | 31 | 28 | 28 | 37 |
| South | 120,839 | 37 | 44 | 47 | 45 | 56 |
| South-South-West | 134,794 | 88 | 94 | 113 | 113 | 101 |
| South-West | 158,844 | 152 | 151 | 170 | 173 | 141 |
| West-South-West | 169,696 | 191 | 184 | 201 | 206 | 160 |
| West | 163,006 | 202 | 189 | 201 | 207 | 155 |
| West-North-West | 139,615 | 183 | 167 | 171 | 178 | 128 |
| North-West | 107,161 | 136 | 120 | 115 | 121 | 85 |

Table 91: Window Treatments – Recommended Clear Glass SHGCpre by Window Thickness

| Existing Window Thickness (inches) | SHGCpre |
| --- | --- |
| Single-pane 1/8-inch clear glass | 0.87 |
| Single-pane 1/4-inch clear glass | 0.83 |
| Single-pane 1/2-inch clear glass | 0.77 |
| Double-pane clear glass | 0.70 |

Table 92: Window Treatments – Recommended COP by HVAC System Type

| Year of Construction; Applicable Code | AC/HP | PTAC/PTHP | Air-Cooled Chiller | Water-Cooled Chiller |
| --- | --- | --- | --- | --- |
| Before 2011; 2000 IECC | 2.9 | 2.9 | 2.5 | 4.2 |
| Between 2011-2016; 2009 IECC | 3.8 | 3.1 | 2.8 | 5.5 |
| After 2016; 2015 IECC | 3.8 | 3.1 | 2.8 | 5.5 |

##### Measure Life and Lifetime Savings

Estimated Useful Life is 10 years for solar screens, as discussed in PUCT Docket Nos. 36779 and 41070. The DEER 2014 update also provides an EUL of 10 years for this measure (EUL ID—GlazDayIt-WinFilm).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Existing window type, thickness, & SHGC

- Description of existing window presence of exterior shading from other buildings or obstacles

- Window film or solar screen SHGC

- Eligible window treatment application area by orientation (e.g., S, SSW, SW)

- Year of construction, if available

- Cooling equipment type

- Cooling equipment rated efficiency

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 36779—Provides EUL for reflective window films and sunscreens.

##### Relevant Standards and Reference Sources

- 1997 ASHRAE Fundamentals, Chapter 29, Table 17.

- International Energy Conservation Code (IECC) 2000, 2009, and 2015

- DEER 2014 EUL update

### Entrance and Exit Door Air Infiltration Measure Overview

TRM Measure ID: NR-BE-DI

Market Sector: Commercial

Measure Category: Building Envelope

Applicable Building Types: All commercial building types

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

      - Measure Description

This measure applies to the installation of weather stripping or door sweeps on entrance and exit doors for a contained, pressurized space. Entrance and exit doors often leave clearance gaps to allow for proper operation. The gaps around the doors allow for the infiltration of unconditioned air into the building, adding to the cooling and heating load of the HVAC system. Weatherstripping and door sweeps are designed to be installed along the bottom and jambs of exterior doors to prevent air infiltration to conditioned space.

        - Eligibility Criteria

Weatherstripping or doors sweeps must be installed on doors of a conditioned and/or heated space. Treated doors must have visible gaps of at least 1/8–3/4 inches along the outside edge of the door. Spaces with interior vestibule doors are not eligible.

        - Baseline Condition

The baseline standard for this measure is a commercial building with exterior doors that are not sealed from unconditioned space.

        - High-efficiency Condition

The high-efficiency condition for this measure is a commercial building with exterior doors that have been sealed from unconditioned space using weather stripping and/or brush style door sweeps.

      - Energy and Demand Savings Methodology

This savings methodology was derived by analyzing TMY3 weather data for each Texas weather zone representative city.

Derivation of Pre-Retrofit Air Infiltration Rate

The pre-retrofit air infiltration rate for each crack width is calculated by applying the methodologies presented in Chapter 5 of the ASHRAE Cooling and Heating Load Calculation Manual (CHLCM). Building type characteristics for a typical commercial building were found in the DOE study PNNL-20026, and an average building height of 20 feet is assumed for the deemed savings approach.

Because air infiltration is a function of differential pressure due to stack effect, wind speed, velocity head, and the design conditions of the building, TMY3 for each Texas weather zone reference city was applied to account for the varying weather conditions that are characteristic throughout an average year.

Figure 5.13 from the ASHRAE CHLCM provides the infiltration rate based on various crack width and the corresponding pressure difference across a door. Figures 5.1 and 5.2 (CHLCM) provide the differential pressure due to stack and wind pressure necessary to determine the total pressure difference across the door.

Applying a regression analysis to Figure 5.1 returns an equation that allows solving for the pressure difference due to stack effect, Δps. The aggregate curve fit for Figure 5.1 is shown below where x is based on the dry bulb temperature from the TMY3 data and the design temperature based on the appropriate seasonal condition.

∆psCd=0.0000334003x-0.00014468

Equation 70

Where Cd is an assumed constant, 0.63, and the neutral pressure distance is 10 feet.

From Figure 5.2, Δpw/Cp is determined by applying a polynomial regression, which returns an equation for solving for the pressure difference due to wind, Δpw. The curve fit for Figure 5.2 is shown below where x is the wind velocity based on TMY3 data.

∆pwCp=0.00047749x2-0.00013041x

Equation 71

Where Cp is an assumed constant, 0.13 (average wind pressure coefficient from Table 5.5 from CHLCM).

This yields the total pressure difference across the door, ΔpTotal:

∆pTotal=∆ps+∆pw

Equation 72

Solving for ΔpTotal allows for the air infiltration rate per linear foot to be determined in Figure 5.13 (CHLCM). Applying a power regression analysis for each crack width (described in inches) represented in Figure 5.13 returns the equations listed below. In these equations, Q is the infiltration rate in cubic feet per minute through cracks around the door, and P is the perimeter of the door in feet.

QP1/8"=41.572x0.5120

Equation 73

QP1/4"=81.913x0.5063

Equation 74

QP1/2"=164.26x0.5086

Equation 75

QP3/4"=246.58x0.5086

Equation 76

These infiltration rates were further disaggregated based on TMY3 average monthly day and night conditions.

Derivation of Design and Average Outside Ambient Temperatures

Taking average daytime and nighttime outdoor temperature values, standard set points, and setbacks for daytime and nighttime design cooling and heating will yield the temperature difference needed for the sensible heat equation:

∆T=Tdesign-Tavg outside ambient

Equation 77

Where:

Tdesign	=	Daytime and nighttime design temperature (°F, see Table 94)

Tavg outside ambient	=	Average outside ambient temperature, specified by month (°F, see Table 93)

Table 93: Average Monthly Ambient Temperatures (°F)

| Month | Climate Zone 1 Amarillo |  | Climate Zone 2 Dallas |  | Climate Zone 3 Houston |  | Climate Zone 4 Corpus Christi |  | Climate Zone 5 El Paso |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Day | Night | Day | Night | Day | Night | Day | Night | Day | Night |
| Jan | 41.5 | 31.5 | 48.1 | 40.3 | 54.8 | 47.0 | 58.1 | 50.9 | 50.9 | 42.4 |
| Feb | 44.9 | 34.5 | 52.8 | 44.8 | 59.4 | 50.5 | 61.7 | 54.4 | 55.8 | 45.2 |
| Mar | 52.9 | 40.7 | 63.6 | 54.4 | 65.5 | 56.8 | 69.1 | 61.3 | 61.0 | 48.2 |
| April | 65.4 | 52.7 | 71.4 | 62.7 | 73.1 | 64.7 | 75.9 | 67.7 | 72.7 | 60.5 |
| May | 69.2 | 57.2 | 77.6 | 68.7 | 79.4 | 71.1 | 80.5 | 72.0 | 80.9 | 69.0 |
| June | 79.9 | 69.7 | 85.3 | 75.0 | 85.1 | 76.2 | 86.4 | 77.9 | 88.2 | 76.1 |
| July | 84.5 | 72.1 | 90.4 | 80.6 | 87.8 | 78.0 | 88.6 | 78.0 | 86.7 | 76.5 |
| Aug | 81.4 | 69.7 | 89.1 | 79.2 | 88.0 | 77.5 | 88.0 | 78.4 | 84.2 | 74.4 |
| Sept | 75.3 | 64.3 | 84.5 | 73.8 | 85.5 | 73.6 | 85.0 | 75.2 | 80.9 | 67.3 |
| Oct | 63.6 | 50.4 | 70.2 | 59.9 | 75.4 | 61.8 | 77.5 | 67.9 | 70.2 | 59.7 |
| Nov | 48.5 | 38.5 | 59.3 | 52.3 | 67.6 | 57.9 | 72.3 | 63.8 | 57.3 | 47.0 |
| Dec | 41.8 | 32.4 | 49.5 | 41.8 | 59.2 | 50.0 | 60.4 | 53.7 | 49.1 | 39.4 |

Table 94: Daytime and Nighttime Design Temperatures

| Temperature Description | Tdesign (°F) |
| --- | --- |
| Daytime Cooling Design Temperature | 74 |
| Daytime Heating Design Temperature | 72 |
| Nighttime Cooling Design Temperature | 78 |
| Nighttime Heating Design Temperature | 68 |

        - Savings Algorithms and Input Variables

To calculate HVAC load associated with air infiltration, the following sensible heat equation is used:

Electric Cooling Energy Savings

Cooling Energy Savings [kWh]Day=CFMpre,day × CFMreduction × 1.08 × ∆T × 1.0kWton× Hoursday12,000 Btuh/ton

Equation 78

Cooling Energy Savings [kWh]Night=CFMpre,night × CFMreduction × 1.08 × ∆T × 1.0kWton× Hoursnight12,000 Btuh/ton

Equation 79

Cooling Energy Savings kWh=Cooling Energy Savings kWhDay+Cooling Energy Savings [kWh]Night

Equation 80

Electric Heating Energy Savings

Heating Energy Savings [kWh]Day=CFMpre,day × CFMreduction × 1.08 × ∆T × 1.0kWton× HoursdayCOP × 3,412 Btuh/kW

Equation 81

Heating Energy Savings [kWh]Night=CFMpre,night × CFMreduction × 1.08 × ∆T × 1.0kWton× HoursnightCOP × 3,412 Btuh/kW

Equation 82

Heating Energy Savings kWh=Cooling Energy Savings kWhDay+Cooling Energy Savings [kWh]Night

Equation 83

Electric Cooling Demand Savings (weighted by climate zone peak hour probability)

Summer Demand Savings [kW]Day=CFMpre,day × CFMreduction × 1.08 × ∆T × 1.0kWton12,000 Btuh/ton

Equation 84

Electric Heating Demand Savings (weighted by climate zone peak hour probability)

Winter Demand Savings [kW]Day/Night=CFMpre,day/night × CFMreduction × 1.08 × ∆T × 1.0kWtonCOP × 3,412 Btuh/kW

Equation 85

Where:

CFMpre 	=	Calculated pre-retrofit air infiltration (cubic feet per minute)

CFMreduction 	=	59% x TDF

TDF = Technical Degradation Factor = 85%

1.08 	=	Sensible heat equation conversion

ΔT 	=	Change in temperature across gap barrier (°F)

Hoursday 	=	12 hour cycles per day, per month = 4,380 hours

Hoursnight 	=	12 hour cycles per night, per month = 4,380 hours

COP 	=	Heating coefficient of performance; 1.0 for electric resistance and 3.3 for heat pumps

        - Deemed Energy and Demand Savings Tables

Deemed energy and demand savings per linear foot of installed weather stripping or door sweep are specified below based on climate zone and existing door gap width.  The length measurement should be initially measured to the nearest ¼ inch and converted to linear feet rounded to hundredths (0.02) including any segments that are not sealed due to corners, hinges, handles, or other obstructions.  The width of the door gap should be rounded to nearest gap width in inches in Table 95.  Heating savings are specified for both electric resistance (ER) and heat pump (HP) heating. Cooling savings are available for buildings with electric cooling and gas heat, but no heating savings should be claimed for buildings with gas heat.

Table 95: Deemed Cooling Energy Savings per Linear Foot of Weather Stripping/Door Sweep

| Climate Zone | Gap Width (inches) |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1/8 | 1/4 | 1/2 | 3/4 |
| Zone 1: Amarillo | 1.90 | 3.83 | 7.60 | 11.42 |
| Zone 2: Dallas | 3.90 | 7.88 | 15.65 | 23.49 |
| Zone 3: Houston | 3.01 | 6.09 | 12.09 | 18.14 |
| Zone 4: Corpus Christi | 5.00 | 10.08 | 20.03 | 30.06 |
| Zone 5: El Paso | 2.81 | 5.69 | 11.28 | 16.93 |

Table 96: Deemed ER Heating Energy Savings per Linear Foot of Weather Stripping/Door Sweep

| Climate Zone | Gap Width (inches) |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1/8 | 1/4 | 1/2 | 3/4 |
| Zone 1: Amarillo | 101.26 | 204.24 | 405.72 | 609.05 |
| Zone 2: Dallas | 48.90 | 98.82 | 196.15 | 294.44 |
| Zone 3: Houston | 27.18 | 55.06 | 109.19 | 163.91 |
| Zone 4: Corpus Christi | 22.78 | 46.02 | 91.35 | 137.13 |
| Zone 5: El Paso | 45.59 | 92.23 | 182.99 | 274.69 |

Table 97: Deemed HP Heating Energy Savings per Linear Foot of Weather Stripping/Door Sweep

| Climate Zone | Gap Width (inches) |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1/8 | 1/4 | 1/2 | 3/4 |
| Zone 1: Amarillo | 30.69 | 61.89 | 122.94 | 184.56 |
| Zone 2: Dallas | 14.82 | 29.95 | 59.44 | 89.22 |
| Zone 3: Houston | 8.24 | 16.69 | 33.09 | 49.67 |
| Zone 4: Corpus Christi | 6.90 | 13.94 | 27.68 | 41.56 |
| Zone 5: El Paso | 13.81 | 27.95 | 55.45 | 83.24 |

Table 98: Deemed Summer Demand Savings per Linear Foot of Weather Stripping/Door Sweep

| Climate Zone | Gap Width (inches) |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1/8 | 1/4 | 1/2 | 3/4 |
| Zone 1: Amarillo | 0.0053 | 0.0105 | 0.0210 | 0.0315 |
| Zone 2: Dallas | 0.0044 | 0.0090 | 0.0179 | 0.0269 |
| Zone 3: Houston | 0.0043 | 0.0087 | 0.0173 | 0.0259 |
| Zone 4: Corpus Christi | 0.0041 | 0.0082 | 0.0164 | 0.0246 |
| Zone 5: El Paso | 0.0041 | 0.0083 | 0.0165 | 0.0247 |

Table 99: Deemed ER Winter Demand Savings per Linear Foot of Weather Stripping/Door Sweep

| Climate Zone | Gap Width (inches) |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1/8 | 1/4 | 1/2 | 3/4 |
| Zone 1: Amarillo | 0.0268 | 0.0541 | 0.1074 | 0.1612 |
| Zone 2: Dallas | 0.0412 | 0.0828 | 0.1648 | 0.2474 |
| Zone 3: Houston | 0.0211 | 0.0425 | 0.0844 | 0.1267 |
| Zone 4: Corpus Christi | 0.0190 | 0.0383 | 0.0762 | 0.1144 |
| Zone 5: El Paso | 0.0099 | 0.0202 | 0.0400 | 0.0602 |

Table 100: Deemed HP Winter Demand Savings per Linear Foot of Weather Stripping/Door Sweep

| Climate Zone | Gap Width (inches) |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1/8 | 1/4 | 1/2 | 3/4 |
| Zone 1: Amarillo | 0.0138 | 0.0277 | 0.0550 | 0.0825 |
| Zone 2: Dallas | 0.0178 | 0.0357 | 0.0710 | 0.1066 |
| Zone 3: Houston | 0.0102 | 0.0207 | 0.0410 | 0.0615 |
| Zone 4: Corpus Christi | 0.0087 | 0.0175 | 0.0348 | 0.0523 |
| Zone 5: El Paso | 0.0049 | 0.0099 | 0.0197 | 0.0296 |

##### Claimed Peak Demand Savings

Refer to Volume 1, Section 4 for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

The EUL for this measure is 11 years, according to the California Database of Energy Efficiency Resources (DEER 2014). This measure life is consistent with the residential air infiltration measure in the Texas TRM.

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Climate zone

- Existing gap width (1/8”, 1/4", 1/2", or 3/4")

- Installed measure (weather stripping or door sweep)

- Linear feet  (to nearest 0.02 feet = 1/4”) of installed weather stripping or door sweep

#### References and Efficiency Standards

        - Petitions and Rulings

- Docket No. 48265. Petition of AEP Texas Inc., CenterPoint Energy Houston Electric, LLC, El Paso Electric Company, Entergy Texas, Inc., Oncor Electric Delivery Company LLC, Southwestern Electric Power Company, Southwestern Public Service Company, and Texas-New Mexico Power Company. Petition to Approve Deemed Savings for New Nonresidential Door Air Infiltration, Nonresidential Door Gaskets, and Residential ENERGY STAR Connected Thermostats. Public Utility Commission of Texas.

        - Relevant Standards and Reference Sources

- Not applicable.

## Nonresidential: Food Service Equipment

### ENERGY STAR® Combination Ovens Measure Overview

TRM Measure ID: NR-FS-CO

Market Sector: Commercial

Measure Category: Food Service Equipment

Applicable Business Types: See Eligibility Criteria

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This section presents the deemed savings methodology for the installation of high efficiency combination ovens. Combination ovens are convection ovens that include the added capability to inject steam into the oven cavity and typically offer at least three distinct cooking modes: combination mode to roast or bake with moist heat, convection mode to operate purely as a convection oven providing dry heat, and a straight pressure-less steamer mode. The energy and demand savings are determined on a per-oven basis.

##### Eligibility Criteria

Eligible units must meet ENERGY STAR® qualifications, with half-size and full-size ovens as defined by ENERGY STAR® and a pan capacity ≥ 5 and ≤ 20.

- Half-size combination oven: capable of accommodating a single 12 x 20 x 2½-inch steam table pan per rack position, loaded from front-to-back or lengthwise.

- Full-size combination oven: capable of accommodating two 12 x 20 x 2½-inch steam table pans per rack position, loaded from front-to-back or lengthwise.

Eligible building types include independent restaurants, chain restaurants, elementary and secondary schools, colleges and universities, corporate and industrial foodservice operations, healthcare, hospitality, and supermarkets.

The following products are excluded from the ENERGY STAR® eligibility criteria:

- 2/3-sized combination ovens

- Dual-fuel heat source combination ovens

- Gas combination ovens

- Electric combination ovens with a pan capacity < 5 or > 20

- Hybrid ovens not defined as eligible above (e.g. those incorporating microwave settings)

- Electric rack ovens

- Conventional or standard ovens, conveyor, slow cook-and-hold, deck, range, rapid cook, and rotisserie

##### Baseline Condition

The baseline condition for retrofit situations is a half-size or full-size combination oven with a pan capacity ≥ 5 and ≤ 20.

##### High-efficiency Condition

Eligible equipment must be compliant with the current ENERGY STAR® v2.2 specification, effective October 7, 2015. Qualified products must meet the minimum energy efficiency and idle energy rate requirements from Table 101.

Table 101: Cooking Energy Efficiency and Idle Energy Rate Requirements

| Operation | Idle Rate (kW) | Cooking Energy Efficiency (%) |
| --- | --- | --- |
| Steam Mode | ≤ 0.133P + 0.6400 | ≥ 55 |
| Convection Mode | ≤ 0.080P + 0.4989 | ≥ 76 |

Furthermore, Pan Capacity must be ≥ 5 and ≤ 20 (for both half- and full-size combination ovens).

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

The deemed values are calculated by using the following algorithms:

Energy Savings kWh=kWhbase-kWhpost

Equation 86

Peak Demand kW=ΔkWhthrs×tdays×CF

Equation 87

kWhbase=kWhconv+ kWhst

Equation 88

kWhpost=kWhconv+ kWhst

Equation 89

kWhconv and kWhst are each calculated the same for both the base (baseline) and post (ENERGY STAR® ) cases, as shown in Equation 88 and Equation 89, except they require their respective η (Cooking Efficiencies), EIdle (Idle Energy Rates) and Ccap (Production Capacity) relative to Convection and Steam Modes as seen in Table 102.

kWh=  Wfood× Efood ×50%ηcooking + Eidle × thours-  WfoodCcap×50%×tdays1000

Equation 90

Where:

kWhbase	=	Baseline annual energy consumption [kWh]

kWhpost	=	Post annual energy consumption [kWh]

tdays	=	Facility operating days per year

thours	=	Equipment operating hours per day

CF	=	Peak coincidence factor

Wfood	=	Pounds of food cooked per day [lb/day]

Efood	=	ASTM energy to food [Wh/lb]. (Differs for Convection-Mode and Steam-Mode. See Table 102)

EIdle	=	Idle energy rate [W]. (Differs for Convection-Mode and Steam-Mode, for Baseline and ENERGY STAR®. See Table 102)

ηcooking	=	Cooking energy efficiency [%]. (Differs for Convection-Mode and Steam-Mode, for Baseline and ENERGY STAR®. See Table 102)

CCap	=	Production capacity per pan [lb/hr]. (Differs for Convection-Mode and Steam-Mode, for Baseline and ENERGY STAR®. See Table 102)

1000	=	Wh to kWh conversion

Table 102: Deemed Variables for Energy and Demand Savings Calculations

| Parameter |  | Convection-mode |  | Steam-mode |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Baseline | ENERGY STAR® | Baseline | ENERGY STAR® |
| kWhbase |  | See Table 103 |  |  |  |
| kWhpost |  |  |  |  |  |
| Wfood | P < 15 | 200 |  |  |  |
|  | P ≥ 15 | 250 |  |  |  |
| Thours |  | 12 |  |  |  |
| Tdays |  | 365 |  |  |  |
| CF |  | 0.92 |  |  |  |
| Efood |  | 73.2 |  | 30.8 |  |
| ηcooking |  | 72% | 76% | 49% | 55% |
| Eidle | P < 15 | 1,320 | (0.133P + 0.6400) * 1000 | 5,260 | (0.080P + 0.4989) * 1000 |
|  | P ≥ 15 | 2,280 |  | 8,710 |  |
| Ccap | P < 15 | 79 | 119 | 126 | 177 |
|  | P ≥ 15 | 166 | 201 | 295 | 349 |

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of High-efficiency Combination Ovens in Table 103 are calculated in the Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment using the default parameters shown above in Table 102.

Table 103: Deemed Energy and Demand Savings Values

| Pan Capacity | kWhbase | kWhpost | Annual Energy Savings [kWh] | Peak Demand Savings [kW] |
| --- | --- | --- | --- | --- |
| 5 | 18,282 | 9,841 | 8,440 | 1.773 |
| 6 | 18,282 | 10,256 | 8,026 | 1.686 |
| 7 | 18,282 | 10,670 | 7,611 | 1.599 |
| 8 | 18,282 | 11,085 | 7,197 | 1.512 |
| 9 | 18,282 | 11,499 | 6,782 | 1.425 |
| 10 | 18,282 | 11,914 | 6,368 | 1.338 |
| 11 | 18,282 | 12,328 | 5,953 | 1.250 |
| 12 | 18,282 | 12,743 | 5,539 | 1.163 |
| 13 | 18,282 | 13,157 | 5,124 | 1.076 |
| 14 | 18,282 | 13,572 | 4,710 | 0.989 |
| 15 | 29,601 | 15,711 | 13,890 | 2.918 |
| 16 | 29,601 | 16,141 | 13,459 | 2.827 |
| 17 | 29,601 | 16,572 | 13,028 | 2.737 |
| 18 | 29,601 | 17,003 | 12,597 | 2.646 |
| 19 | 29,601 | 17,434 | 12,167 | 2.556 |
| 20 | 29,601 | 17,865 | 11,736 | 2.465 |

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 12 years, consistent with the ENERGY STAR® calculator and with the DEER 2014 EUL update (EUL ID—Cook-ElecCombOven).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- High efficiency manufacturer and model

- High efficiency heavy load cooking efficiency

- High efficiency equipment idle rate

- Oven size

- Pan Capacity

- Copy of ENERGY STAR® certification

- Copy of proof of purchase including date of purchase, manufacturer, and model number

#### References and Efficiency Standards

##### Petitions and Rulings

Not applicable.

##### Relevant Standards and Reference Sources

- ENERGY STAR® Equipment Standards for Commercial Ovens. http://www.energystar.gov/products/certified-products/detail/Commercial-ovens

- DEER 2014 EUL update.

### ENERGY STAR® Electric Convection Ovens Measure Overview

TRM Measure ID: NR-FS-CV

Market Sector: Commercial

Measure Category: Food Service Equipment

Applicable Building Types: See Eligibility Criteria

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This section covers the savings from retrofit (early retirement), replacement, or new installation of a full-size or half-size high efficiency electric convection oven. Convection ovens cook their food by forcing hot dry air over the surface of the food product. The rapidly moving hot air strips away the layer of cooler air next to the food and enables the food to absorb the heat energy. The energy and demand savings are deemed and based on oven energy rates, cooking efficiencies, operating hours, production capacities, and building type. Average energy and demand consumption, used to calculate the savings, are determined using these assumed default input values on a per-oven basis.

##### Eligibility Criteria

Eligible units must meet ENERGY STAR® qualifications, with half-size and full-size electric ovens as defined by ENERGY STAR®

- Full-size convection oven: capable of accommodating standard full-size sheet pans measuring 18 x 26 x 1-inch.

- Half-size convection oven: capable of accommodating half-size sheet pans measuring 18 x 13 x 1-inch.

Eligible building types include independent restaurants, chain restaurants, elementary and secondary schools, colleges and universities, corporate and industrial foodservice operations, healthcare, hospitality, and supermarkets.

Convection ovens eligible for rebate do not include ovens that have the ability to heat the cooking cavity with saturated or superheated steam. However, eligible convection ovens may have moisture injection capabilities (e.g., baking ovens and moisture-assist ovens). Ovens that include a “hold feature” are eligible under this specification as long as convection is the only method used to fully cook the food.

The following products are excluded from the ENERGY STAR® eligibility criteria:

- Hybrid ovens not defined as eligible above (e.g. those incorporating microwave settings)

- Electric rack ovens

- Conventional or standard ovens, conveyor, slow cook-and-hold, deck, range, rapid cook, and rotisserie

##### Baseline Condition

The baseline condition for retrofit situations is an electric convection oven.

##### High-efficiency Condition

Eligible equipment must be compliant with the current ENERGY STAR® v2.2 specification, effective October 7, 2015. Qualified products must must meet the minimum energy efficiency and idle energy rate requirements from Table 104.

Table 104: Convection Oven Cooking Energy Efficiency and Idle Energy Requirements

| Oven Capacity | Idle Rate (W) | Cooking Energy Efficiency (%) |
| --- | --- | --- |
| Full-Size | ≤ 1,600 | ≥ 71 |
| Half-Size | ≤ 1,000 |  |

#### Energy and Demand Savings Methodology

##### Savings Calculations and Input Variables

The deemed savings from these ovens are based on the following algorithms:

Energy kWh=(Ebase-EHE)×days1000

Equation 91

Peak Demand kW=Ebase-EHETon×CF1000

Equation 92

Ebase=LB×EFoodEFFbase+IDLEbase×Ton-LBPCbase

Equation 93

EHE=LB×EFoodEFFHE+IDLEHE×Ton-LBPCHE

Equation 94

Where:

Ebase	=	Baseline daily energy consumption (kWh/day)

EHE	=	High efficiency daily energy consumption (kWh/day)

LB	=	Pounds of food cooked per day [lb/day]

Days	=	Number of operating days per year [days/yr]

CF 	=	Coincidence Factor

Efood	=	ASTM energy to food of energy absorbed by food product during cooking [Wh/lb]

EFFbase	=	Baseline heavy load cooking energy efficiency [%]

EFFHE	=	High efficiency heavy load cooking energy efficiency [%]

IDLEbase	=	Baseline idle energy rate [kW]

IDLEHE	=	High efficiency idle energy rate [kW]

Ton	=	Operating hours per day [hrs./day]

PCbase	=	Baseline production capacity [lbs./hr]

PCHE	=	High efficiency production capacity [lbs/hr]

Table 105: Deemed Variables for Energy and Demand Savings Calculations

| Variable | Full-Size | Half-Size |
| --- | --- | --- |
| LB237 | 100 |  |
| Days | 365 |  |
| CF | 0.92 |  |
| Efood | 73.2 |  |
| EFFbase237 | 65% | 68% |
| EFFHE237 | 71% |  |
| IDLEbase237 | 2,000 | 1,030 |
| IDLEHE237 | 1,600 | 1,000 |
| Ton | 12 |  |
| PCbase237 | 90 | 45 |
| PCHE237 |  | 50 |

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of high efficiency convection ovens are deemed values based on the assumed capacity for an average convection oven installed. The following table provides these deemed values.

Table 106: Deemed Energy and Demand Savings Values

| Oven Size | Annual Energy Savings [kWh] | Peak Demand Savings [kW] |
| --- | --- | --- |
| Full-Size | 1,937 | 0.410 |
| Half-Size | 192 | 0.040 |

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 12 years, consistent with ENERGY STAR® research and with the DEER 2014 EUL update (EUL ID—Cook-ElecConvOven).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- High efficiency equipment manufacturer and model number

- High efficiency equipment heavy load cooking efficiency

- High efficiency equipment idle rate

- Oven size

- Copy of ENERGY STAR® certification

- Copy of proof of purchase including date of purchase, manufacturer, and model number

#### References and Efficiency Standards

##### Petitions and Rulings

Not applicable.

##### Relevant Standards and Reference Sources

- ENERGY STAR® requirements for Commercial Ovens. http://www.energystar.gov/index.cfm?c=ovens.pr_crit_comm_ovens. Accessed 07/2020.

- ENERGY STAR® list of Qualified Commercial Ovens. https://www.energystar.gov/productfinder/product/certified-commercial-ovens/results. Accessed 07/2020.

- DEER 2014 EUL update.

### ENERGY STAR® Commercial Dishwashers Measure Overview

TRM Measure ID: NR-FS-DW

Market Sector: Commercial

Measure Category: Food Service Equipment

Applicable Building Types: See Eligibility Criteria

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of an ENERGY STAR® commercial dishwasher. Commercial dishwashers that have earned the ENERGY STAR® label are, on average, 25 percent more energy-efficient and 25 percent more water-efficient than standard models. The energy savings associated with ENERGY STAR® commercial dishwashers are primarily due to reduced water use and reduced need to heat water. A commercial kitchen may have external booster water heaters, or booster water heaters may be internal to specific equipment. Both primary and booster water heaters may be either gas or electric; therefore, dishwasher programs need to ensure the savings calculations used are appropriate for the water heating equipment installed at the participating customer’s facility. The energy and demand savings are determined on a per-dishwasher basis.

##### Eligibility Criteria

The dishwasher must be ENERGY STAR® certified and fall under one of the following categories, and are described in Table 107:

- Under counter dishwasher

- Stationary rack, single tank, door type dishwasher

- Single tank conveyor dishwasher

- Multiple tank conveyor dishwasher

- Pot, pan, and utensil

Eligible building types include independent restaurants, chain restaurants, elementary and secondary schools, colleges and universities, corporate and industrial foodservice operations, healthcare, hospitality, and supermarkets.

Dishwashers intended for use in residential or laboratory applications are not eligible for ENERGY STAR® under this product specification. Steam, gas, and other non-electric models also do not qualify.

Additionally, though Single and Multiple Tank Flight Type Conveyor dishwashing machines (where the dishes are loaded directly on the conveyor rather than transported within a rack – also referred to as a rackless conveyor) are eligible as per the version 2.0 specification, they are considered ineligible for this measure, since default values are not available for Flight Type dishwashers in the Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment.

Table 107: Nonresidential ENERGY STAR® Commercial Dishwashers Descriptions

| Equipment Type | Equipment Description |
| --- | --- |
| Under Counter Dishwasher | A machine with an overall height of 38" or less, in which a rack of dishes remains stationary within the machine while being subjected to sequential wash and rinse sprays and is designed to be installed under food preparation workspaces. Under counter dishwashers can be either chemical or hot water sanitizing, with an internal booster heater for the latter. For purposes of this specification, only those machines designed for wash cycles of ten minutes or less can qualify for ENERGY STAR®. |
| Stationary Rack, Single Tank, Door Type Dishwasher | A machine in which a rack of dishes remains stationary within the machine while subjected to sequential wash and rinse sprays. This definition also applies to machines in which the rack revolves on an axis during the wash and rinse cycles. Subcategories of stationary door type machines include single and multiple wash tank, double rack, pot, pan and utensil washers, chemical dump type, and hooded wash compartment ("hood type"). Stationary rack, single tank, door type models are covered by this specification and can be either chemical or hot water sanitizing, with an internal or external booster heater for the latter. |
| Single Tank Conveyor Dishwasher | A washing machine that employs a conveyor or similar mechanism to carry dishes through a series of wash and rinse sprays within the machine. Specifically, a single tank conveyor machine has a tank for wash water followed by a final sanitizing rinse and does not have a pumped rinse tank. This type of machine may include a pre-washing section before the washing section. Single tank conveyor dishwashers can either be chemical or hot water sanitizing, with an internal or external booster heater for the latter. |
| Multiple Tank Conveyor Dishwasher | A conveyor type machine that has one or more tanks for wash water and one or more tanks for pumped rinse water, followed by a final sanitizing rinse. This type of machine may include one or more pre-washing sections before the washing section. Multiple tank conveyor dishwashers can be either chemical or hot water sanitizing, with an internal or external hot water booster heater for the latter. |
| Pot, Pan, and Utensil | A stationary rack, door type machine designed to clean and sanitize pots, pans, and kitchen utensils. |

##### Baseline Condition

Baseline equipment is either a low-temperature or high temperature machine as defined by Table 107, which is not used in a residential or laboratory setting. For low-temperature units, the DHW is assumed to be electrically heated. For high-temperature units, the DHW can either be heated by electric or natural gas methods. For units heated with natural gas, the unit shall have an electric booster heater attached to it.

##### High-efficiency Condition

Qualifying equipment must be compliant with the current ENERGY STAR® v2.0 specification, effective February 1, 2013. High-temperature equipment sanitizes using hot water and requires a booster heater. Booster heaters must be electric. Low-temperature equipment uses chemical sanitization and does not require a booster heater. Qualified products must be less than or equal to the maximum idle energy rate and water consumption requirements from Table 108.

Table 108: High-efficiency Requirements for Commercial Dishwashers

| Machine Type | Low-temperature Efficiency Requirements |  | High-temperature Efficiency Requirements |  |
| --- | --- | --- | --- | --- |
|  | Idle Energy Rate [kW] | Water Consumption [gal/rack] | Idle Energy Rate [kW] | Water Consumption [gal/rack] |
| Under Counter | ≤ 0.50 | ≤ 1.19 | ≤ 0.50 | ≤ 0.86 |
| Stationary Single Tank Door | ≤ 0.60 | ≤ 1.18 | ≤ 0.70 | ≤ 0.89 |
| Single Tank Conveyor | ≤ 1.50 | ≤ 0.79 | ≤ 1.50 | ≤ 0.70 |
| Multiple Tank Conveyor | ≤ 2.00 | ≤ 0.54 | ≤ 2.25 | ≤ 0.54 |
| Pot, Pan, and Utensil | < 1.00 | ≤0.58 | ≤ 1.20 | ≤ 0.58244 |

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Deemed savings values are calculated using the following algorithms:

Energy Savings kWh = VwaterB-VwaterP×∆TDHW+∆TboostηDHW×ρwater×Cp×1 W3413 kBtuh +(Idlebase-Idlepost)×tdays×thours-tdays×Nracks×WashTime60

Equation 95

Peak Demand kW=∆kWhthrs×tdays×CF

Equation 96

VwaterB=tdays×Nracks×VgalrackB

Equation 97

VwaterP=tdays×Nracks×VgalrackP

Equation 98

Where:

VwaterB	=	Baseline volume of water consumed per year [gallons]

VwaterP	=	Post measure volume of water consumed per year [gallons]

tdays	=	Facility operating days per year [days]

thours	= 	Equipment operating hours per day [hours]

Nracks	=	Number of racks washed per days

CF	=	Peak coincidence factor

Vgalrack,B	=	Gallons of water used per rack of dishes washed for conventional dishwashers [gallons]

Vgalrack,P	=	Gallons of water used per rack of dishes washed for ENERGY STAR® dishwashers [gallons]

ρwater	=	Density of water [lbs/gallon]

Cp	=	Specific heat of water [Btu/lb ºF]

ΔTDHW	=	Inlet water temperature increase for building water heater [ºF]

ηDHW	=	Building electric water heater and booster heater efficiency [%]

ΔTboost	=	Inlet water temperature for booster water heater [ºF]

IDLEbase	=	Baseline Idle Energy Rate [kW]

IDLEpost	=	High Efficiency Idle Energy Rate [kW]

WashTime	=	Wash time per Rack

Table 109: Deemed Variables for Energy and Demand Savings Calculations

| Inputs | Under Counter | Single Door Type | Single Tank Conveyor | Multiple Tank Conveyor | Pot, Pan and Utensil |
| --- | --- | --- | --- | --- | --- |
| tdays | 365 |  |  |  |  |  |
| thours5 | 18 |  |  |  |  |  |
| CF | 0.97 |  |  |  |  |  |
| ρwater | 8.208 [lbs/gallon] |  |  |  |  |  |
| Cp | 1.0 [Btu/lb ºF] |  |  |  |  |  |
| ΔTDHW4 | Gas Hot Water Heaters: 0 ºF Electric Hot Water Heaters: 70 ºF |  |  |  |  |  |
| ηDHW | 98% |  |  |  |  |  |
| ΔTboost | Gas Booster Heaters: 0 ºF Electric Booster Heaters: 40 ºF |  |  |  |  |  |
| ηboost | 98% |  |  |  |  |  |
| Low-temperature Units |  |  |  |  |  |  |
| Nracks | 75 | 280 | 400 | 600 | N/a |
| VgalrackB | 1.73 | 2.10 | 1.31 | 1.04 | N/a |
| VgalrackP | 1.19 | 1.18 | 0.79 | 0.54 | N/a |
| IDLEbase | 0.50 | 0.60 | 1.60 | 2.00 | N/a |
| IDLEpost | 0.50 | 0.60 | 1.50 | 2.00 | N/a |
| WashTime | 2.0 | 1.5 | 0.3 | 0.3 | N/a |
| High-temperature Units |  |  |  |  |  |  |
| Nracks | 75 | 280 | 400 | 600 | 280 |
| VgalrackB | 1.09 | 1.29 | 0.87 | 0.97 | 0.70 |
| VgalrackP | 0.86 | 0.89 | 0.70 | 0.54 | 0.58 |
| IDLEbase | 0.76 | 0.87 | 1.93 | 2.59 | 1.20 |
| IDLEpost | 0.50 | 0.70 | 1.50 | 2.25 | 1.20 |
| WashTime | 2.0 | 1.0 | 0.3 | 0.2 | 3.0 |

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of high-efficiency dishwashers are deemed values based on an assumed capacity for the average convection oven installed. The following tables provide these deemed values.

Table 110: Deemed Energy and Peak Demand Savings Values by Dishwasher

| Facility Description | Under Counter |  | Door Type |  | Single Tank Conveyor |  | Multi-tank Conveyor |  | Pot, Pan, and Utensil |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | kWh | kW | kWh | kW | kWh | kW | kWh | kW | kWh | kW |
| Low Temp./ Electric Hot Water Heater | 2,540 | 0.375 | 16,153 | 2.385 | 13,626 | 2.012 | 18,811 | 2.777 | NA | NA |
| High Temp./ Electric Hot Water Heater with Electric Booster Heater | 3,171 | 0.468 | 11,863 | 1.751 | 9,212 | 1.360 | 27,408 | 4.046 | 3,311 | 0.489 |
| High Temp./ Gas Hot Water Heater with Electric Booster Heater | 2,089 | 0.308 | 4,840 | 0.715 | 4,948 | 0.730 | 11,230 | 1.658 | 1,204 | 0.178 |

##### Measure Life and Lifetime Savings

The EUL varies per eligible dishwasher type, as stated in the ENERGY STAR® v2.0 Commercial Kitchen Equipment Savings Calculator. The Equipment Lifetime is tabulated per Dishwasher type in Table 111:

Table 111: Equipment Lifetime per Dishwasher Category

| Machine Type | EUL (years) |
| --- | --- |
| Under Counter | 10 |
| Stationary Single Tank Door | 15 |
| Single Tank Conveyor | 20 |
| Multiple Tank Conveyor | 20 |
| Pot, Pan, and Utensil | 10 |

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Baseline and post-retrofit dishwasher machine type

- Post-retrofit manufacturer and model number

- Energy source for primary water heater

- Energy source for booster water heater

- Copy of ENERGY STAR® certification

- Copy of proof of purchase including date of purchase, manufacturer, and model number

#### References and Efficiency Standards

##### Petitions and Rulings

Not applicable.

##### Relevant Standards and Reference Sources

- ENERGY STAR® requirements for Commercial Dishwashers. http://www.energystar.gov/sites/default/files/specs//private/Commercial_Dishwasher_Program_Requirements%20v2_0.pdf. Accessed 07/2020.

- ENERGY STAR® maintains an online list of qualified Commercial dishwashers meeting or exceeding ENERGY STAR® requirements at http://www.energystar.gov/productfinder/product/certified-Commercial-dishwashers/results. Accessed 07/2020.

- ENERGY STAR® v2.0 Calculator (Commercial Kitchen Equipment Savings Calculator). http://www.energystar.gov/buildings/sites/default/uploads/files/Commercial_kitchen_equipment_calculator.xlsx. Accessed 07/2020.

### ENERGY STAR® Hot Food Holding Cabinets Measure Overview

TRM Measure ID: NR-FS-HC

Market Sector: Commercial

Measure Category: Food Service Equipment

Applicable Building Types: See Eligibility Criteria

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

A commercial Hot Food Holding Cabinet is a heated, fully enclosed compartment with one or more solid or transparent doors designed to maintain the temperature of hot food that has been cooked using a separate appliance. Models that meet ENERGY STAR® specifications incorporate better insulation, thus reducing heat loss, and may also offer additional energy-saving devices such as magnetic door gaskets, auto-door closers, or Dutch doors. The insulation of the cabinet offers better temperature uniformity within the cabinet from top to bottom. The energy and demand savings are deemed and based on an interior volume range of the holding cabinets and the building type. An average wattage has been calculated for each volume range: half size, three-quarter size, and full size. The energy and demand savings are determined on a per-cabinet basis.

##### Eligibility Criteria

Hot food holding cabinets must be ENERGY STAR® certified. Eligible building types include independent restaurants, chain restaurants, elementary and secondary schools, colleges and universities, corporate and industrial foodservice operations, healthcare, hospitality, and supermarkets.

The following products are excluded from the ENERGY STAR® eligibility criteria:

- Dual function equipment (e.g. “cook-and-hold” and proofing units)

- Heated transparent merchandising cabinets

- Drawer warmers

##### Baseline Condition

The baseline condition is a half-size, three-quarter size, or full-size hot food holding cabinet with a maximum idle energy rate of < 40 watts/ft3 for all equipment sizes.

##### High-efficiency Condition

Eligible equipment must be compliant with the current ENERGY STAR® v2.0 specification, effective October 1, 2011. Table 112 summarizes idle energy rate requirements based on cabinet interior volume.

Table 112: Maximum Idle Energy Rate Requirements ENERGY STAR® Qualification

| Product Interior Volume [ft3] | Idle Energy Rate [W] |
| --- | --- |
| 0 < V < 13 | ≤ 21.5 V |
| 13 ≤ V < 28 | ≤ 2.0 V + 254.0 |
| 28 ≤ V | ≤ 3.8 V + 203.5 |

#### Energy and Demand Savings Methodology

##### Savings Calculations and Input Variables

Deemed values are calculated using the following algorithms:

Energy Saving kWh= EIdleB-EIdleP×11000×thrs×tdays

Equation 99

Peak Demand kW=EIdleB-EIdleP×11000×CF

Equation 100

Where:

EIdleB	=	Baseline idle energy rate [W] (See Table 113)

EIdleP	=	Idle energy rate after installation [W] (See Table 113)

V	=	Product Interior Volume [ft3]

thrs	=	Equipment operating hours per day [hrs]

tdays	=	Facility operating days per year

CF	=	Peak coincidence factor

Table 113: Deemed Variables for Energy and Demand Savings Calculations

| Input Variable | Product Interior Volume Range |  |  |
| --- | --- | --- | --- |
|  | 0 < V < 13 | 13 ≤ V < 28 | 28 ≤ V |
| Assumed Product Interior Volume [ft3] | 8 | 22 | 53 |
| Baseline Equipment Idle Energy Rate [EIdleB] | 40 × V |  |  |
| Assumed Baseline Equipment Idle Energy Rate [EIdleB] | 320 | 880 | 2,120 |
| Efficient Equipment Idle Energy Rate [EIdleP] | 21.5 × V | 2 × V + 254 | 3.8 × V +203.5 |
| Operating Hours per Day [thours] | 15 |  |  |
| Facility Operating Days per Year [tdays] | 365 |  |  |
| Peak Coincidence Factor [CF] | 0.92 |  |  |

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of electric hot food holding cabinets are deemed values. The following table provide these deemed values.

Table 114: Deemed Energy and Demand Savings Values by HFHC Size

| Product Interior Volume [ft3] | Annual Energy Savings [kWh] | Peak Demand Savings [kW] |
| --- | --- | --- |
| 0 < V < 13 | 1,215 | 0.204 |
| 13 ≤ V < 28 | 2,770 | 0.466 |
| 28 ≤ V | 4,832 | 0.812 |

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 12 years per the PUCT approved Texas EUL filing (Docket No. 36779) and is consistent with ENERGY STAR®’s research and the DEER 2014 EUL update (EUL ID—Cook-Hold Cab).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Baseline equipment interior cabinet volume

- Baseline equipment idle energy rate

- Post-retrofit equipment interior cabinet volume

- Copy of ENERGY STAR® certification

- Copy of proof of purchase including date of purchase, manufacturer, and model number

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 36779—Provides EUL for Hot Food Holding Cabinets

##### Relevant Standards and Reference Sources

- ENERGY STAR® requirements for Hot Food Holding Cabinets. https://www.energystar.gov/ia/partners/product_specs/program_reqs/Commercial_HFHC_Program_Requirements_2.0.pdf. Accessed 01/21/2015.

- DEER 2014 EUL update.

### ENERGY STAR® Electric Fryers Measure Overview

TRM Measure ID: NR-FS-EF

Market Sector: Commercial

Measure Category: Cooking Equipment

Applicable Building Types: See Eligibility Criteria

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This section presents the deemed savings methodology for the installation of an ENERGY STAR® Electric Fryer. Fryers that have earned the ENERGY STAR® rating offer shorter cook times and higher production rates through advanced burner and heat exchanger designs. Fry pot insulation reduces standby losses resulting in a lower idle energy rate. The energy and demand savings are determined on a per-fryer basis.

##### Eligibility Criteria

Eligible units must meet ENERGY STAR® qualifications, either counter-top or floor type designs, with standard-size and large vat fryers as defined by ENERGY STAR.®

- Standard-Size Electric Fryer: A fryer with a vat that measures ≥ 12 inches and < 18 inches wide, and a shortening capacity ≥ 25 pounds and ≤ 65 pounds

- Large Vat Electric Fryer: A fryer with a vat that measures ≥ 18 inches and ≤ 24 inches wide, and a shortening capacity > 50 pounds

Eligible building types include independent restaurants, chain restaurants, elementary and secondary schools, colleges and universities, corporate and industrial foodservice operations, healthcare, hospitality, and supermarkets.

The following products are excluded from the ENERGY STAR® eligibility criteria:

- Fryers with vats measuring < 12 inches wide, or > 24 inches wide

##### Baseline Condition

The baseline condition is an electric standard-size fryer ≥ 12 inches and < 18 inches wide or large vat fryer > 18 inches and < 24 inches wide that do not meet ENERGY STAR® product criteria.

##### High-efficiency Condition

Eligible equipment must be compliant with the current ENERGY STAR® specification, effective October 2016. New electric standard fryers ≥ 12 inches and < 18 inches wide and large vat fryers > 18 inches and < 24 inches wide that meet or exceed the requirements are listed below in Table 115.

Table 115: High-efficiency Requirements for Electric Fryers

| Inputs | Standard | Large-Vat |
| --- | --- | --- |
| Cooking energy efficiency | ≥ 83% | ≥ 80% |
| Idle energy rate [W] | ≤ 800 | ≤ 1,100 |

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Deemed values are calculated using the following algorithms:

Energy Savings kWh=kWhbase-kWhpost

Equation 101

Peak Demand kW=kWhbase-kWhposttOpHrs×tdays×CF

Equation 102

kWhbase =Wfood ×EfoodηcookingB+ EidleB × tOpHours- Wfood CCapB×tdays1000

Equation 103

kWhpost =Wfood ×EfoodηcookingP+ EidleP × tOpHours- Wfood CCapP×tdays1000

Equation 104

Where:

kWhbase	=	Baseline annual energy consumption [kWh]

kWhpost	=	Post annual energy consumption [kWh]

Wfood	=	Pounds of food cooked per day [lb/day]

Efood	=	ASTM energy to food [Wh/lb]

ηcookingP	=	Post measure cooking energy efficiency [%]

ηcookingB	=	Baseline cooking energy efficiency [%]

EIdleP	=	Post measure idle energy rate [W]

EIdleB	=	Baseline idle energy rate [W]

CCapP	=	Post measure production capacity per pan [lb/hr]

CCapB	=	Baseline production capacity per pan [lb/hr]

tDays	=	Facility operating days per year [days/yr]

tOpHrs	=	Average daily operating hours per day [hr]

ηPC	=	Percent of rated production capacity [%]

CF	=	Peak coincidence factor

Table 116: Deemed Variables for Energy and Demand Savings Calculations

| Parameter | Standard-sized Vat |  |  | Large Vat |  |
| --- | --- | --- | --- | --- | --- |
|  | Baseline | Post Retrofit |  | Baseline | Post Retrofit |
| kWhbase | See Table 117 |  |  |  |  |
| kWhpost |  |  |  |  |  |
| Wfood | 150 |  |  |  |  |
| tOpHrs | 16 |  | 12 |  |  |
| tdays | 365 |  |  |  |  |
| CF | 0.92 |  |  |  |  |
| Efood | 167 |  |  |  |  |
| ηcooking | 75% | 83% |  | 70% | 80% |
| Eidle | 1,050 | 800 |  | 1,350 | 1,110 |
| CCap | 65 | 70 |  | 100 | 110 |

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of Electric Fryers are deemed values. Table 117 provides these deemed values.

Table 117: Deemed Energy and Demand Savings Values by Fryer Type

| Fryer Type | kWhbase | kWhpost | Annual Energy Savings [kWh] | Peak Demand Savings [kW] |
| --- | --- | --- | --- | --- |
| Standard | 17,439 | 15,063 | 2,376 | 0.374 |
| Large Vat | 18,236 | 15,739 | 2,497 | 0.525 |

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 12 years per the PUCT approved Texas EUL filing (Docket No. 36779) and by the DEER 2014 EUL update (EUL ID—Cook-ElecFryer).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Manufacturer and model number

- High-efficiency unit heavy load cooking efficiency

- High-efficiency unit equipment idle rate

- Fryer width

- Copy of ENERGY STAR® certification

- Copy of proof of purchase including date of purchase, manufacturer, and model number

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 36779—Provides EUL for Electric Fryers.

##### Relevant Standards and Reference Sources

- ENERGY STAR® requirements for Electric Fryers https://www.energystar.gov/sites/default/files/specs/private/Commercial_Fryers_Program_Requirements.pdf. Accessed 11/13/2019.

- DEER 2014 EUL update.

### Pre-Rinse Spray Valves Measure Overview

TRM Measure ID: NR-FS-SV

Market Sector: Commercial

Measure Category: Food Service Equipment

Applicable Building Types: See Table 119

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Direct install or point of sale

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of pre-rinse sprayers to reduce hot water usage which, in turn, saves energy associated with heating the water. Water heating is assumed to be electric. The energy and demand savings are determined on a per-sprayer basis and are algorithmically based.

##### Eligibility Criteria

. Units must be used for commercial food preparation only and have flow rates which are no greater than the baseline flow rates specified in Table 118 (on a per product class or ozf, i.e. spray force in ounce-force, basis).

##### Baseline Condition

Effective January 28, 2019, eligible baseline equipment is a pre-rinse spray valve with a flow-rate that does not exceed the maximum flow rate per product class as specified in Table 118.

Table 118: Pre-rinse Spray Valve Flow Rate Limits

| Product class (ozf) | Flow rate (gpm) |
| --- | --- |
| Product Class 1 (≤ 5 ozf) | 1.00 |
| Product Class 2 (> 5 ozf and ≤ 8 ozf) | 1.20 |
| Product Class 3 (> 8 ozf) | 1.28 |

##### High-efficiency Condition

Following the passing of the Energy Policy Act of 2005, the EPA announced on September 21st, 2005 that it would no longer pursue an ENERGY STAR® specification for Pre-rinse Spray Valves. Rather than simply disallowing pre-rinse spray valves altogether, it has been decided that the savings resulting from the retrofitting of this measure be algorithm-based (as opposed to deemed using baseline and high-efficiency assumptions). If identification of a standard flow rate for post-retrofit equipment can be identified, future updates will address the transformation of this measure from an algorithm-based approach to one which is deemed.

The eligible high-efficiency equipment is thus a pre-rinse spray valve which has a flow rate no greater than the flow rate specified in Table 118 for the pre-rinse spray valve’s respective product class. The sprayer should be capable of the same cleaning ability as the old sprayer.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Energy and demand savings are calculated using the following algorithms:

Energy kWh =(FB×UB-FP×UP)×DaysYear×(TH-TC)×CH×CEEffE

Equation 105

Peak Demand kW=P×(FB×UB-FP×UP)×(TH-TC)×CH×CEEffE

Equation 106

Where:

FB	=	Average baseline flow rate of sprayer (GPM)

FP	=	Average post measure flow rate of sprayer (GPM)

UB	=	Baseline water usage duration

UP	=	Post-retrofit water usage duration

TH	=	Average mixed hot water (after spray valve) temperature (ºF)

TC	=	Average supply (cold) water temperature (ºF)

Days	=	Annual facility operating days for the applications

CH	=	Unit conversion: 8.33 BTU/(Gallons-ºF)

CE	=	Unit conversion: 1 BTU = 0.00029308 kWh (1/3412)

EffE	=	Efficiency of electric water heater

P	=	Hourly peak demand as percent of daily demand

Table 119: Assumed Variables for Energy and Demand Savings Calculations

| Variable | Assumed Value |
| --- | --- |
| FB | See Table 118 |
| UB =UP | Fast Food Restaurant: 45 min/day/unit Casual Dining Restaurant: 105 min/day/unit262 Institutional: 210 min/day/unit262 Dormitory: 210 min/day/unit262 K-12 School: 105 min/day/unit |
| TH | 120 |
| TC | 69 |
| Days | Fast Food Restaurant: 360 Casual Dining Restaurant: 360 Institutional: 360 Dormitory: 270 K-12 School: 193 |
| CH | 8.33 |
| CE | 0.00029 |
| EffE | 1.0 |
| P | Fast Food Restaurant: 6.81% Casual Dining Restaurant: 17.36% Institutional: 5.85% Dormitory: 17.36% K-12 School: 11.35% |

##### Deemed Energy and Demand Savings Tables

There are no deemed energy or demand savings tables for this measure. Please see the High-efficiency Condition section for the rationale used in opting for an algorithm-based approach.

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 5 years.259,265 This is consistent with PUCT Docket No. 36779.

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Spray force in ounce-force (ozf)

- Baseline Equipment flow-rate

- Retrofit Equipment flow-rate

- Building Type

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40669—Provides energy and demand savings and measure specifications. Attachment A: https://interchange.puc.texas.gov/Documents/40669_3_735684.PDF. Accessed 09/09/2013.

- PUCT Docket 36779—Provides EUL for pre-rinse sprayers

##### Relevant Standards and Reference Sources

Not applicable.

### ENERGY STAR® Electric Steam Cookers Measure Overview

TRM Measure ID: NR-FS-SC

Market Sector: Commercial

Measure Category: Cooking Equipment

Applicable Building Types: See Eligibility Criteria

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of ENERGY STAR® electric Steam Cookers. Steam cookers are available in 3, 4, 5, or ≥ 6 pan capacities. ENERGY STAR® qualified units are up to 50 percent more efficient than standard models. They have higher production rates and reduced heat loss due to better insulation and a more efficient steam delivery system. The energy and demand savings are determined on a per-cooker basis.

##### Eligibility Criteria

Eligible Steam Cookers can have a 3, 4, 5, or ≥ 6 pan capacity. A list of eligible equipment is found on the ENERGY STAR® list of qualified equipment. Eligible building types include independent restaurants, chain restaurants, elementary and secondary schools, colleges and universities, corporate and industrial foodservice operations, healthcare, hospitality, and supermarkets.

It is required that the post-retrofit ENERGY STAR® electric Steam Cooker and the conventional Steam Cooker it replaces are of equivalent pan capacities.

##### Baseline Condition

The baseline condition for retrofit situations is an electric steam cooker that is not ENERGY STAR® certified.

##### High-efficiency Condition

Eligible equipment must be compliant with the current ENERGY STAR® specification, effective August 2003. Qualified products must meet the requirements from Table 120.

Table 120: ENERGY STAR® Energy Efficiency and Idle Rate Requirements for Electric Steam Cookers

| Pan Capacity | Cooking Energy Efficiency [%] | Idle Rate [W] |
| --- | --- | --- |
| 3-Pan | 50% | 400 |
| 4-Pan | 50% | 530 |
| 5-Pan | 50% | 670 |
| 6-Pan and Larger | 50% | 800 |

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Energy Savings ∆kWh=kWhbase-kWhpost

Equation 107

Peak Demand kW=ΔkWhthrs×tdays×CF

Equation 108

kWhbase = Wfood × Efoodηbase+ 1- ηtSteam ×EidleRate, base+ ηtSteam×Cpan×Npan ×Efoodηbase ×tdays-Wfoodηbase×Npan×NOpDays1000

Equation 109

kWhpost = Wfood × Efoodηpost+ 1- ηtSteam×EidleRate, post+ ηtSteam×Cpan×Npan ×Efoodηpost ×tdays-Wfoodηpost×Npan×NOpDays1000

Equation 110

Where:

kWhbase	=	Baseline annual energy consumption [kWh]

kWhpost	=	Post annual energy consumption [kWh]

ΔkWh	=	Energy Savings = kWhbase — kWhpost

Wfood	=	Pounds of food cooked per day [lb/day]

Efood	=	ASTM energy to food [Wh/lb]

ηbase	=	Baseline Cooking energy efficiency (Differs for boiler-based or steam generator equipment)

ηpost	=	Post-retrofit Cooking energy efficiency

ηtSteam	=	Percent of time in constant steam mode [%]

EIdleRate, base	=	Idle energy rate [W] (Differs for boiler-based or steam-generator equipment)

EIdleRate, post	=	Idle energy rate [W]

Cpan	=	Production capacity per pan [lb/hr]

Npan	=	Number of pans

NOpDays	=	Facility operating days per year [days/yr]

tOpHrs	=	Average daily operating hours per day [hr]

CF	=	Peak coincidence factor

1000	=	Wh to kWh conversion factor

Table 121: Deemed Variables for Energy and Demand Savings Calculations

| Parameter | Baseline Value | Post Retrofit Value |
| --- | --- | --- |
| kWhbase | See Table 122 |  |  |
| kWhpost |  |  |  |
| Wfood | 100 |  |  |
| Efood | 30.8 |  |  |
| η | Boiler-based Efficiency: 26% Steam-Generator Efficiency: 30% | 50% |
| ηtSteam | 40% |  |  |
| EIdleRate | Boiler-based Idle Rate: 1,000 Steam Generator Idle Rate: 1,200 | 3-Pan: 400 4-Pan: 530 5-Pan: 670 6-Pan: 800 |
| Cpan | 23.3 | 16.7 |
| Npan | 3, 4, 5, or 6 |  |  |
| tOpHrs | 12 |  |  |
| NOpDays | 365 |  |  |
| CF | 0.92 |  |  |

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of high efficiency steam cookers are deemed by substituting the assumed input values from Table 120 into the savings algorithms, and are tabulated in Table 122 per steam cooker type and per pan capacity.

Table 122: Annual Energy Consumption and Daily Food Cooked

| Steam Cooker Type | Npan | kWhbase | kWhPost | Annual Energy Savings [kWh] | Peak Demand Savings [kW] |
| --- | --- | --- | --- | --- | --- |
| Boiler Based | 3-Pan | 19,416 | 7,632 | 11,784 | 2.475 |
|  | 4-Pan | 24,330 | 9,777 | 14,553 | 3.057 |
|  | 5-Pan | 29,213 | 11,946 | 17,268 | 3.627 |
|  | 6-Pan and Larger | 34,080 | 14,090 | 19,990 | 4.199 |
| Steam Generator | 3-Pan | 17,599 | 7,632 | 9,967 | 2.093 |
|  | 4-Pan | 21,884 | 9,777 | 12,107 | 2.543 |
|  | 5-Pan | 26,132 | 11,946 | 14,186 | 2.980 |
|  | 6-Pan and Larger | 30,360 | 14,090 | 16,270 | 3.417 |

##### Measure Life and Lifetime Savings.

The EUL has been defined for this measure as 12 years, consistent with both ENERGY STAR® specifications and DEER 2014 EUL update (EUL ID—Cook-ElecStmCooker).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- High efficiency manufacturer and model number

- Number of pans

- Copy of ENERGY STAR® certification

- Copy of proof of purchase including date of purchase, manufacturer, and model number

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40669—Provides energy and demand savings and measure specifications

##### Relevant Standards and Reference Sources

- ENERGY STAR® specifications for Commercial Steam Cookers. https://www.energystar.gov/sites/default/files/specs/private/Commercial_Steam_Cookers_Program_Requirements%20v1_2.pdf. Accessed 11/13/2019.

- DEER 2014 EUL update.

### Demand Controlled Kitchen Ventilation Measure Overview

TRM Measure ID: NR-FS-KV

Market Sector: Commercial

Measure Category: Food Service

Applicable Building Types: Restaurants

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed value

Savings Methodology: Algorithms

#### Measure Description

This measure presents deemed savings for implementation of demand controlled ventilation (DCV) installed in commercial kitchens. DCV systems make use of control strategies to modulate exhaust fans and make-up air units. Various control strategies may be implemented such as time-of-day scheduling; sensors including exhaust temperature, cook surface temperature, smoke, or steam sensors; or direct communication from cooking equipment to the DCV processor.

##### Eligibility Criteria

Kitchen ventilation systems both with or without dedicated makeup air units are eligible for this measure.

##### Baseline Condition

The baseline condition is a commercial kitchen operating the cooking exhaust and make-up air operation at a single fixed speed with on/off controls or operating on an occupancy based schedule.

##### High-efficiency Condition

The efficient condition is a commercial kitchen varying the flow rates of cooking exhaust and make-up air operation based on periods of high and low demand as indicated by schedules or monitors of cooktop operation.

#### Energy and Demand Savings Methodology

Energy savings are calculated based on monitoring data gathered during field studies conducted by the Food Service Technology Center (FSTC) and published in the ASHRAE Journal. Assumptions for average savings, operating hours and days, and makeup air factors are calculated as the averages for corresponding building types from FSTC monitoring data.

When there is no dedicated makeup air unit, only the exhaust fan power is expected to modulate based on demand and a makeup air unit factor is applied to the savings algorithm. The makeup air unit (MAU) factor is calculated as the percent of total kitchen ventilation system power (exhaust plus makeup air fans) that comes from exhaust fans.

Interactive heating and cooling savings are taken by multiplying the percent airflow savings from the FSTC study by the estimated heating and cooling loads output by the FSTC Outdoor Air Load Calculator (OALC). This output is adjusted by population to account for the percentage of sites with electric resistance or heat pump heating. Additionally, because output from the OALC is per 1,000 CFM, a CFM per HP ratio is applied in order to simplify implementation tracking requirements. Interactive heating and cooling savings are presented per horsepower. Assumed efficiency of AC systems is 10 EER; assumed efficiency of electric resistance heating is 1.0 COP; assumed efficiency of HP heating is 7.7 HSPF.

##### Savings Algorithms and Input Variables

kWhsavings=HPexhaust ×(SavingsInteractive/HP+AvgSavkWhHP×HPexhaust×Hrsday×Daysyr×MAU)+Heatsavings+Coolingsavings×CFMoutdoor1000

Equation 111

kWsavings=kWhsavings×PWPLS

Equation 112

Where:

AvgSavkWhHP		= 	Average hourly energy savings per horsepower based on the building type, see Table 123

HPexhaust		= 	Total exhaust horsepower of the kitchen ventilation system included in the DCV operating strategy, facility specific

Hrsday		= 	Average daily operating hours, facility specific; if unknown, use defaults from Table 123

Daysyr		= 	Number of operational days per year, facility specific; if unknown use defaults from Table 123

MAU		= 	Make-up Air Unit factor applied to account for presence of dedicated MAU; value = 1 if there is a dedicated MAU; see Table 123 for values when there is no dedicated MAU

SavingsInteractive/HP	= 	Population adjusted interactive HVAC savings per horsepower, see Table 124

Heatsavings

Coolingsavings

CFMoutdoor

PWPLS	= 	Probability Weighted Peak Load Share; see Table 125

Table 123: Demand Controlled Kitchen Ventilation – Default Assumptions

| Building Type | AvgSavkWhHP | Hrsday | Daysyr | MAU factor with no dedicated MAU |
| --- | --- | --- | --- | --- |
| Casual Dining/Fast Food | 0.650 | 15 | 365 | 0.65 |
| 24-Hr Restaurant/Hotel | 0.631 | 24 | 365 | 0.65 |
| School Café with summer | 0.566 | 11 | 325 | 0.51 |
| School Café without summer | 0.566 | 11 | 252 | 0.51 |

Table 124: Demand Controlled Kitchen Ventilation – Population-Adjusted Interactive HVAC Savings per hp

| Climate Zone | Building Type | Interactive Savings (kWh/hp) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | Casual Dining/Fast Food | 608 |  |  |  |
|  | 24-Hr Restaurant/Hotel | 851 |  |  |  |
|  | School Café with summer | 455 |  |  |  |
|  | School Café without summer | 206 |  |  |  |
| 2 | Casual Dining/Fast Food | 1,123 |  |  |  |
|  | 24-Hr Restaurant/Hotel | 1,758 |  |  |  |
|  | School Café with summer | 838 |  |  |  |
|  | School Café without summer | 409 |  |  |  |
| 3 | Casual Dining/Fast Food | 1,191 |  |  |  |
|  | 24-Hr Restaurant/Hotel | 1,844 |  |  |  |
|  | School Café with summer | 959 |  |  |  |
|  | School Café without summer | 571 |  |  |  |
| 4 | Casual Dining/Fast Food | 1,393 |  |  |  |
|  | 24-Hr Restaurant/Hotel | 2,262 |  |  |  |
|  | School Café with summer | 1,119 |  |  |  |
|  | School Café without summer | 689 |  |  |  |
| 5 | Casual Dining/Fast Food | 1,023 |  |  |  |
|  | 24-Hr Restaurant/Hotel | 1,510 |  |  |  |
|  | School Café with summer | 775 |  |  |  |
|  | School Café without summer | 450 |  |  |  |

Table 125: Demand Controlled Kitchen Ventilation – Probability Weighted Peak Load Share

| Climate Zone | Summer PWPLS | Winter PWPLS |
| --- | --- | --- |
| 1 | 1.33E-04 | 1.46E-04 |
| 2 | 1.36E-04 | 1.45E-04 |
| 3 | 1.34E-04 | 1.43E-04 |
| 4 | 1.31E-04 | 1.45E-04 |
| 5 | 1.45E-04 | 1.46E-04 |

##### Deemed Energy and Demand Savings Tables

Table 126: Demand Controlled Kitchen Ventilation – Deemed Annual Energy Savings per horsepower

| Climate Zone | Building Type | Annual Savings (kWh/hp) |  |
| --- | --- | --- | --- |
|  |  | With dedicated MAU | W/out dedicated MAU |
| 1 | Casual Dining/Fast Food | 4,253 | 2,990 |
|  | 24-Hr Restaurant/Hotel | 6,376 | 4,418 |
|  | School Café with summer | 2,480 | 1,498 |
|  | School Café without summer | 1,779 | 1,016 |
| 2 | Casual Dining/Fast Food | 4,768 | 3,504 |
|  | 24-Hr Restaurant/Hotel | 7,282 | 5,324 |
|  | School Café with summer | 2,864 | 1,881 |
|  | School Café without summer | 1,981 | 1,218 |
| 3 | Casual Dining/Fast Food | 4,836 | 3,572 |
|  | 24-Hr Restaurant/Hotel | 7,368 | 5,410 |
|  | School Café with summer | 2,985 | 2,002 |
|  | School Café without summer | 2,144 | 1,381 |
| 4 | Casual Dining/Fast Food | 5,038 | 3,775 |
|  | 24-Hr Restaurant/Hotel | 7,787 | 5,829 |
|  | School Café with summer | 3,144 | 2,162 |
|  | School Café without summer | 2,261 | 1,499 |
| 5 | Casual Dining/Fast Food | 4,668 | 3,404 |
|  | 24-Hr Restaurant/Hotel | 7,034 | 5,077 |
|  | School Café with summer | 2,801 | 1,818 |
|  | School Café without summer | 2,023 | 1,260 |

Table 127: Demand Controlled Kitchen Ventilation – Deemed Summer and Winter Peak Demand Savings per horsepower

| Climate Zone | Building Type | Summer Demand Savings (kW/hp) |  | Winter Demand Savings (kW/hp) |  |
| --- | --- | --- | --- | --- | --- |
|  |  | With dedicated MAU | W/out dedicated MAU | With dedicated MAU | W/out dedicated MAU |
| 1 | Casual Dining/Fast Food | 0.57 | 0.40 | 0.62 | 0.44 |
|  | 24-Hr Restaurant/Hotel | 0.85 | 0.59 | 0.93 | 0.65 |
|  | School Café with summer | 0.33 | 0.20 | 0.36 | 0.22 |
|  | School Café without summer | 0.24 | 0.14 | 0.26 | 0.15 |
| 2 | Casual Dining/Fast Food | 0.65 | 0.48 | 0.69 | 0.51 |
|  | 24-Hr Restaurant/Hotel | 0.99 | 0.72 | 1.05 | 0.77 |
|  | School Café with summer | 0.39 | 0.26 | 0.41 | 0.27 |
|  | School Café without summer | 0.27 | 0.17 | 0.29 | 0.18 |
| 3 | Casual Dining/Fast Food | 0.65 | 0.48 | 0.69 | 0.51 |
|  | 24-Hr Restaurant/Hotel | 0.99 | 0.72 | 1.05 | 0.77 |
|  | School Café with summer | 0.40 | 0.27 | 0.43 | 0.29 |
|  | School Café without summer | 0.29 | 0.18 | 0.31 | 0.20 |
| 4 | Casual Dining/Fast Food | 0.66 | 0.50 | 0.73 | 0.55 |
|  | 24-Hr Restaurant/Hotel | 1.02 | 0.76 | 1.13 | 0.85 |
|  | School Café with summer | 0.41 | 0.28 | 0.46 | 0.31 |
|  | School Café without summer | 0.30 | 0.20 | 0.33 | 0.22 |
| 5 | Casual Dining/Fast Food | 0.68 | 0.49 | 0.68 | 0.50 |
|  | 24-Hr Restaurant/Hotel | 1.02 | 0.74 | 1.03 | 0.74 |
|  | School Café with summer | 0.41 | 0.26 | 0.41 | 0.27 |
|  | School Café without summer | 0.29 | 0.18 | 0.30 | 0.18 |

##### Measure Life and Lifetime Savings

#### The estimated useful life (EUL) for this VFD measure is 15 years per both the PUCT-approved Texas EUL filing (Docket No. 36779) and DEER 2014 (EUL ID—HVAC-VSD-fan).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Kitchen ventilation system exhaust fan horsepower

- Building Type

- Kitchen ventilation makeup air unit fan horsepower, if present

- Presence of dedicated makeup air unit

- Testing and balancing report, if available

#### References and Efficiency Standards

##### Petitions and Rulings

This section is not applicable.

##### Relevant Standards and Reference Sources

This section is not applicable.

### Commercial Ice Makers Measure Overview

TRM Measure ID: NR-FS-IM

Market Sector: Commercial

Measure Category: Food Service Equipment

Applicable Building Types: Any commercial

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

      - Measure Description

##### This measure applies to automatic ice makers installed in commercial sites.

##### Eligibility Criteria

##### Eligible equipment includes air-cooled batch and continuous ice makers with the following design types: ice-making head (IMH), self-contained (SCU), and remote condensing (RCU) units.

Any commercial-type building is eligible; building types include independent restaurants, chain restaurants, elementary and secondary schools, colleges and universities, corporate and industrial foodservice operations, healthcare, hospitality, and supermarkets.

The following products are excluded from the ENERGY STAR® eligibility criteria:

- Water-cooled ice makers

- Ice makers with ice and water dispensing systems

- Air cooled RCUs that are designed only for connection to remote rack compressors

##### Baseline Condition

The baseline condition is an ice maker meeting the federal standards published in 10 CFR 431,listed in Table 128. The baseline applies to automatic air-cooled commercial ice makers with capacities between 50 and 4,000 pounds per 24-hour period manufactured on or after January 28, 2018.

Table 128: Ice Maker Baseline Efficiency

| Equipment Type | Harvest Rate (lbs ice per 24 Hrs) | Max Energy Use Rate (kWh/100 lb ice) H=harvest rate |
| --- | --- | --- |
| Batch |  |  |
| IMH | < 300 | 10 - 0.01233H |
|  | ≥ 300 and < 800 | 7.05 - 0.0025H |
|  | ≥ 800 and < 1,500 | 5.55 - 0.00063H |
|  | ≥ 1,500 and < 4,000 | 4.61 |
| RCU (but not Remote Compressor) | < 988 | 7.97 - 0.00342H |
|  | ≥ 988 and < 4,000 | 4.59 |
| RCU and Remote Compressor | < 930 | 7.97 - 0.00342H |
|  | ≥ 930 and < 4,000 | 4.79 |
| SCU | < 110 | 14.79 - 0.0469H |
|  | ≥ 110 and < 200 | 12.42 - 0.02533H |
|  | ≥ 200 and < 4,000 | 7.35 |
| Continuous |  |  |
| IMH | < 310 | 9.19 - 0.00629H |
|  | ≥ 310 and < 820 | 8.23 - 0.0032H |
|  | ≥ 820 and < 4,000 | 5.61 |
| RCU (but not Remote Compressor) | < 800 | 9.7 - 0.0058H |
|  | ≥ 800 and < 4,000 | 5.06 |
| RCU and Remote Compressor | < 800 | 9.9 - 0.0058H |
|  | ≥ 800 and < 4,000 | 5.26 |
| SCU | < 200 | 14.22 - 0.03H |
|  | ≥ 200 and < 700 | 9.47 - 0.00624H |
|  | ≥ 700 and < 4,000 | 5.1 |

##### High-Efficiency Condition

#### Eligible equipment must be compliant with the current ENERGY STAR® v3.0 specification, effective January 28, 2018. Qualified products must meet the minimum energy consumption (kWh/100 lbs ice)from Table 129.

Table 129: ENERGY STAR® Criteria - Automatic Ice Makers

| Equipment Type | Harvest Rate (lbs ice per 24 Hrs) | Max Energy Use Rate (kWh/100 lb ice) H=harvest rate |
| --- | --- | --- |
| Batch |  |  |
| IMH | H < 300 | < 9.20 - 0.01134H |
|  | 300 ≤ H < 800 | < 6.49 - 0.0023H |
|  | 800 ≤ H < 1500 | < 5.11 - 0.00058H |
|  | 1500 ≤ H ≤ 4000 | < 4.24 |
| RCU | H < 988 | < 7.17 – 0.00308H |
|  | 988 ≤ H ≤ 4000 | < 4.13 |
| SCU | H < 110 | < 12.57 - 0.0399H |
|  | 110 ≤ H < 200 | < 10.56 - 0.0215H |
|  | 200 ≤ H ≤ 4000 | < 6.25 |
| Continuous |  |  |
| IMH | H < 310 | < 7.90 – 0.005409H |
|  | 310 ≤ H < 820 | < 7.08 – 0.002752H |
|  | 820 ≤ H ≤ 4000 | < 4.82 |
| RCU | H < 800 | < 7.76 – 0.00464H |
|  | 800 ≤ H ≤ 4000 | < 4.05 |
| SCU | H < 200 | < 12.37 – 0.0261H |
|  | 200 ≤ H < 700 | < 8.24 – 0.005429H |
|  | 700 ≤ H ≤ 4000 | < 4.44 |

#### Energy and Demand Savings Methodology

Average Harvest Rates per design-type were computed for both batch and continuous Ice Makers utilizing the ENERGY STAR® qualified products listing for Commercial Ice Makers for the purpose of possibly deeming energy and demand savings, but were determined to be too variable to be utilized as assumptions in computed deemed savings. A strictly algorithmic approach was thus opted for. Savings for air-cooled batch and continuous Commercial Ice Makers are dependent on the Harvest Rate and can be calculated using the following algorithms.

##### Savings Algorithms and Input Variables

Annual Energy Savings kWh=(UseRatebase-UseRateESTAR)×Harvest Rate100 ×Duty Cycle×Days

Equation 113

Demand Savings kW=Annual Energy Savings ×PLS

Equation 114

Where:

UseRatebase	=		The rated energy consumption (kWh) per 100 pounds of ice, Table 128 of the baseline machine.

UseRateESTAR	=		The rated energy consumption (kWh) per 100 pounds of ice,

Harvest Rate	=		Pounds of ice produced per 24 hours

Duty Cycle	=		Machine duty cycle, 80%

Days	=		Number of days per year, default is 365 based on continuous use for both batch and continuous type ice makers.

PLS	=		Probability-weighted peak load share, Table 130

Table 130: Probability-weighted Peak Load Share - Ice Makers

| Probability Weighted Peak Load Share (PLS) |  |  |
| --- | --- | --- |
| Climate Zone | Summer Peak | Winter Peak |
| 1 | 0.00012 | 0.00011 |
| 2 |  | 0.00011 |
| 3 |  | 0.00011 |
| 4 |  | 0.00012 |
| 5 |  | 0.00012 |

Deemed Energy Savings Tables

There are no deemed energy savings tables for this measure.

##### Deemed Summer and Winter Demand Savings Tables

There are no deemed demand savings tables for this measure.

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Additional Calculators and Tools

This section is not applicable.

##### Measure Life and Lifetime Savings

The estimated useful life (EUL) for automatic ice makers is 8.5 years.

#### Program Tracking Data and Evaluation Requirements

It is required that the following list of primary inputs and contextual data be specified and tracked by the program database to inform the evaluation and apply the savings properly:

- Machine Type

  - IMH, RC, or SCU

  - Batch or continuous

- Machine harvest rate

- Climate zone

- Annual days of use

#### References and Efficiency Standards

##### Petitions and Rulings

None

##### Relevant Standards and Reference Sources

- ENERGY STAR® Commercial Ice Maker Key Product Criteria Version 3.0, https://www.energystar.gov/products/commercial_food_service_equipment/commercial_ice_makers/key_product_criteria, Accessed August 2020.

### Vacuum-Sealing & Packaging Machines Measure Overview

TRM Measure ID: NR-MS-VS

Market Sector: Commercial

Measure Category: Miscellaneous

Applicable Building Types: Supermarket, Grocery, Food Store

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: M&V

#### Measure Description

This measure involves the replacement of always-on commercial electric vacuum-sealing and packaging machines with on-demand commercial electric vacuum-sealing and packaging machines. Packaging machines consist of a heating bar and heating platform. The heating bar is used to cut the wrapping film as it meets the heating bar. The heating platform is used to heat up the wrapping film. When the wrapping film is heated, the film sticks to the package and seals the product.

##### Eligibility Criteria

Eligible vacuum-sealing and packaging machines must use either a mechanical or optical control system. A mechanical system applies downward pressure onto a larger heating element platform, engaging a switch that activates a heating element until the switch is disengaged (or for a maximum of three seconds). An optical system uses an optical eye to detect that an item is being sealed. The eye is placed in the front center of a large heating element. When a package is set on the heating element, light is reflected into the eye, engaging the heating element until it is removed (or for a maximum of three seconds).

The measure is restricted to supermarket, grocery, and other food store building types.

##### Baseline Condition

The baseline is a conventional (always-on) packaging machine. With conventional machines, both heating elements are kept at a constant temperature of 280°F.

##### High-efficiency Condition

The high-efficiency condition is an on-demand packaging machine. On-demand machines are similar but have a more powerful heating platform, which is defaults to off and is switched on/off by a controller.

##### Savings Algorithms and Input Variables

Southern California Edison (SCE) and the Food Service Technology Center (FSTC) conducted a field study to evaluate and compare energy savings and demand reduction potential between baseline and on-demand package sealers in supermarkets. The study included four supermarket chains, with three sites selected for each chain. Each test site operated approximately 20 hours per day. Package sealers were located in deli, meat, and or produce departments. Power data was measured in 10-second intervals over a six-week monitoring period. A low sample interval was chosen to accurately capture the pulsing of the heating elements.

The study estimated demand savings by averaging power draw during the peak hours from 2-5 PM to account for the cycling of the larger heating element on the on-demand unit. This measure uses 10-minute average load shape to estimate coincidence factors consistent with the Texas peak definition. This approach is more consistent with the 15-minute interval data typically used in calculated demand and energy charges by utilities. Demand savings are calculated by dividing energy savings by 8,760 and multiplying against the coincidence factor.

##### Deemed Energy and Demand Savings Tables

Table 131: Vacuum-sealing & Packaging Machines – Deemed Energy and Demand Savings

| Building Type | kWh/machine | Summer kW/ machine | Winter kW/ machine |
| --- | --- | --- | --- |
| Supermarkets, Grocery, & Food Stores | 1,568 | 0.06 | 0.06 |

##### Claimed Peak Demand Savings

Refer to Volume 1, Section 4 for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

The estimated useful life (EUL) for vacuum-sealing and packaging machines is 10 years, based on the University of California Useful Life Indices.

#### Program Tracking Data and Evaluation Requirements

The below list of primary inputs and contextual data is recommended to be specified and tracked by the program database to inform the evaluation and apply the savings properly.

- Building type

- Number of packaging machines

- Packaging machine manufacturer and model

#### References and Efficiency Standards

##### Petitions and Rulings

##### Relevant Standards and Reference Sources

## Nonresidential: Refrigeration

### Door Heater Controls Measure Overview

TRM Measure ID: NR-RF-HC

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Any commercial retail facility such as supermarkets, grocery stores, hotels, restaurants, and convenience stores.

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of door heater controls for glass-door refrigerated cases with anti-sweat heaters (ASH). A door heater controller senses dew point (DP) temperature in the store and modules power supplied to the heaters accordingly. DP inside a building is primarily dependent on the moisture content of outdoor ambient air. Because the outdoor DP varies between climate zones, weather data from each climate zone must be analyzed to obtain a DP profile. The reduced heating results in a reduced cooling load. The savings are on a per-linear foot of display case basis.

##### Eligibility Criteria

The efficient equipment must be a standard-heat configuration door heater control utilized in an eligible commercial retail facility on glass-door refrigerated cases for the purpose of dynamically controlling humidity.

##### Baseline Condition

The baseline efficiency case is a cooler or a freezer door heater that operates 8,760 hours per year without any controls.

##### High-efficiency Condition

Eligible high efficiency equipment is a cooler or a freezer door heater connected to a heater control system, which controls the door heaters by measuring the ambient humidity and temperature of the store, calculating the dew point (DP) temperature, and using pulse width modulation to control the anti-sweat door heater based on specific algorithms for freezer and cooler doors.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

The energy savings from the installation of anti-sweat heater controls are a result of both the decrease in length of time the heater is running (kWhASH) and the reduction in load on the refrigeration (kWhrefrig). These savings are calculated using the following procedures:

Indoor dew point (Td-in) can be calculated from outdoor dew point (Td-out) per climate zone using the following equation:

tTd-in=0.005379×tTd-out2+0.1717952×Ttd-out+19.87006

Equation 115

The baseline assumes door heaters are running on an 8,760-hour operating schedule. In the post-retrofit case, the duty for each hourly reading is calculated by assuming a linear relationship between indoor DP and duty cycle for each bin reading. It is assumed that the door heaters will be all off (duty cycle of 0%) at 42.89ºF DP and all on (duty cycle of 100%) at 52.87ºF DP for a typical supermarket. Between these values, the door heaters’ duty cycle changes proportionally:

Door Heater ON%= tTd-in-All OFF setpt 42.89°FAll ON setpt 52.87℉-All OFF setpt 42.89°F

Equation 116

The controller only changes the run-time of the heaters, so the instantaneous door heater power (kWASH) as a resistive load remains constant per linear foot of door heater at:

For medium temperature (coolers):

kWASH = 0.109 per door or 0.0436 per linear foot of door

For low temperature (freezers):

kWASH = 0.191 per door or 0.0764 per linear foot of door

Equation 117

Door heater energy consumption for each hour of the year is a product of power and run-time:

kWhASH-Hourly=kWASH×Door Heater ON% ×1Hour

Equation 118

kWhASH= kWhASH-Hourly

Equation 119

To calculate energy savings from the reduced refrigeration load using average system efficiency and assuming that 35 percent of the anti-sweat heat becomes a load on the refrigeration system, the cooling load contribution from door heaters can be given by:

QASHton-hrs=0.35×kWASH×3,413Btuhr12,000Btuton×Door Heater ON%

Equation 120

The compressor power requirements are based on calculated cooling load and energy-efficiency ratios obtained from manufacturers' data. The compressor analysis is limited to the cooling load imposed by the door heaters, not the total cooling load of the refrigeration system.

For medium temperature refrigerated cases, the saturated condensing temperature (SCT) is calculated as the design dry-bulb temperature plus 15 degrees. For low-temperature refrigerated cases, the SCT is the design dry-bulb temperature plus 10 degrees. The EER for both medium- and low-temperature applications is a function of SCT and part load ratio (PLR) of the compressor. PLR is the ratio of total cooling load to compressor capacity and is assumed to be a constant of 1/1.15 or approximately 0.87.

For medium temperature compressors, the following equation is used to determine the EERMT [Btu/hr/watts], which are shown in Table 132.

EERMT=a+b×SCT+c×PLR+d×SCT2+e×PLR2+f×SCT×PLR+g×SCT3+h×PLR3+i×SCT×PLR2+j×SCT2×PLR

Equation 121

Where:

a	=	3.75346018700468

b	=	-0.049642253137389

c	=	29.4589834935596

d	=	0.000342066982768282

e 	=	-11.7705583766926

f 	=	-0.212941092717051

g	=	-1.46606221890819 x 10-6

h	=	6.80170133906075

i	=	-0.020187240339536

j	=	0.000657941213335828

PLR	=	1/1.15 = 0.87

SCT	=	TDB + 15

For low temperature compressors, the following equation is used to determine the EERLT [Btu/hr/watts]:

EERLT=a+b×SCT+c×PLR+d×SCT2+e×PLR2+f×SCT×PLR+g×SCT3+h×PLR3+i×SCT×PLR2+j×SCT2×PLR

Equation 122

Where:

a	=	9.86650982829017

b	=	-0.230356886617629

c 	=	22.905553824974

d	=	0.00218892905109218

e	=	-2.48866737934442

f	=	-0.248051519588758

g	=	-7.57495453950879 x 10-6

h	=	2.03606248623924

i	=	-0.0214774331896676

j	=	0.000938305518020252

PLR	=	1/1.15 = 0.876956521739

SCT	=	TDB +10

Table 132: Coefficients by Climate Zone

| Climate Zone and Representative City | Summer Design TDB | SCTMT | SCTLT | EERMT | EERLT |
| --- | --- | --- | --- | --- | --- |
| Zone 1: Amarillo | 96 | 111 | 106 | 6.44 | 4.98 |
| Zone 2: Dallas-Ft. Worth | 100 | 115 | 110 | 6.05 | 4.67 |
| Zone 3: Houston | 96 | 111 | 106 | 6.44 | 4.98 |
| Zone 4: McAllen | 100 | 115 | 110 | 6.05 | 4.67 |
| Zone 5: El Paso | 101 | 116 | 111 | 5.95 | 4.59 |

Where:

TDB	=	Dry Bulb Temperature

Energy used by the compressor to remove heat imposed by the door heaters for each hourly reading is determined based on calculated cooling load and EER, as outlined below:

kWhrefrig-hourly=QASH×12EER

Equation 123

kWhrefrig= kWhrefrig-Hourly

Equation 124

Total annual energy consumption (direct door heaters and indirect refrigeration) is the sum of all hourly reading values:

kWhtotal=kWhrefrig+kWhASH

Equation 125

Total energy savings is a result of the baseline and post-Retrofit case:

Annual Energy Savings kWh=kWhtotal-baseline+-kWhtotal-post

Equation 126

While there might be instantaneous demand savings because of the cycling of the door heaters, peak demand savings will only be due to the reduced refrigeration load. Peak demand savings is calculated by the following equation:

Peak Demand Savings=kWhrefrig-baseline-kWhrefrig-post8,760

Equation 127

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of anti-sweat door heater controls are deemed values based on city/climate zone and refrigeration temperature. The following table provides these deemed values.

Table 133: Deemed Energy and Demand Savings Values by Location and Refrigeration Temperature

| Climate Zone and Representative City | Medium Temperature |  | Low Temperature |  |
| --- | --- | --- | --- | --- |
|  | Annual Energy Savings [kWh/ft] | Peak Demand Savings [kW/ft] | Annual Energy Savings [kWh/ft] | Peak Demand Savings [kW/ft] |
| Zone 1: Amarillo | 364 | 0.007 | 668 | 0.015 |
| Zone 2: Dallas | 249 | 0.005 | 457 | 0.011 |
| Zone 3: Houston | 180 | 0.003 | 330 | 0.007 |
| Zone 4: McAllen | 137 | 0.003 | 251 | 0.006 |
| Zone 5: El Paso | 405 | 0.008 | 745 | 0.018 |

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 12 years per the PUCT approved Texas EUL filing (Docket No. 36779). It is also consistent with the DEER 2014 EUL update (EUL ID—GrocDisp-ASH).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Regional climate zone

- Refrigeration temperature

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40669—Provides energy and demand savings and measure specifications. Attachment A: https://interchange.puc.texas.gov/Documents/40669_7_736774.PDF. Accessed 11/13/2019. 
https://interchange.puc.texas.gov/Documents/40669_7_736775.PDF. Accessed 11/13/2019.

- PUCT Docket 36779—Provides EUL for Anti-Sweat Heater Controls

##### Relevant Standards and Reference Sources

- DEER 2014 EUL update

### ECM Evaporator Fan Motors Measure Overview

TRM Measure ID: NR-RF-FM

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Any commercial retail facility such as supermarkets, grocery stores, hotels, restaurants, and convenience stores

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the replacement of existing evaporator fan motors with electronically commutated motors (ECMs) in cooler and freezer display cases. ECMs can provide up to 65 percent reduction in fan energy use with higher efficiencies, automatic variable-speed drive, lower motor operating temperatures, and less maintenance.

##### Eligibility Criteria

All ECMs must be suitable, size-for-size replacements of evaporator fan motors.

##### Baseline Condition

The baseline efficiency case is an existing shaded pole evaporator fan motor in a refrigerated case.

##### High-efficiency Condition

Eligible high-efficiency equipment is an electronically commutated motor which replaces an existing evaporator fan motor.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

The energy savings from the installation of ECMs are a result of savings due to the increased efficiency of the fan and the reduction of heat produced from the reduction of fan operation. The energy and demand savings are calculated using the following equations:

Cooler

DemandkW=N ×ΔkWpeak per unit

Equation 128

ΔkWpeak per unit=Wbase- Wee/1000×LF×DCEvapCooler×1+1COPcooler

Equation 129

EnergykWh=N×∆kWhper unit

Equation 130

∆kWhper unit=ΔkWpeak per unit×Hours×1-%OFF

Equation 131

Freezer

DemandkW=N ×ΔkWpeak per unit

Equation 132

ΔkWpeak per unit=Wbase- Wee/1000×LF×DCEvapFreezer×1+1COPfreezer

Equation 133

EnergykWh=N×∆kWhper unit

Equation 134

∆kWhper unit=ΔkWpeak per unit×Hours×1-%OFF

Equation 135

Where:

N	=	Number of motors replaced

Wbase	=	Input wattage of existing/baseline evaporator fan motor

Wee	=	Input wattage of new energy efficient evaporator fan motor

LF	=	Load factor of evaporator fan motor

DCEvapCool	=	Duty cycle of evaporator fan motor for cooler

DCEvapFreezer	=	Duty cycle of evaporator fan motor for freezer

COPcooler	=	Coefficient of performance of compressor in the cooler

COPfreezer	=	Coefficient of performance of compressor in the freezer

Hours	=	The annual operating hours are assumed to be 8,760 for coolers and 8,273 for walk-in freezers (see Table 134)

%OFF	=	The percentage of time that the evaporator fan motors are off. If the facility does not have evaporator fan controls %OFF = 0, and if the facility has evaporator fan controls %OFF = 46%.

Table 134: Deemed Variables for Energy and Demand Savings Calculations

| Variable | Deemed Values |
| --- | --- |
| Wbase | See Table 135 |
| Wee | See Table 135 |
| LF | 0.9 |
| DCEvapCooler | 100% |
| DCEvapFreezer | 94.4% |
| COPcooler | See Table 136 |
| COPfreezer | See Table 136 |
| Hours | 8760 or 8273 |
| %OFF | 0 or 46% |

Table 135: Motor Sizes, Efficiencies, and Input Watts

| Motor Eff. and Power Table |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal Motor Size | Motor Output (W) | Shaded Pole Eff | Shaded Pole Input (W) | PSC Eff | PSC Input (W) | ECM Eff. | ECM Input (W) |
| (1-14W) | 9 | 18% | 50 | 41% | 22 | 66% | 14 |
| 1/40 HP (16-23W) | 19.5 | 21% | 93 | 41% | 48 | 66% | 30 |
| 1/20 HP (37W) | 37 | 26% | 142 | 41% | 90 | 66% | 56 |
| 1/15 HP (49W) | 49.0 | 26% | 188 | 41% | 120 | 66% | 74 |
| 1/4 HP | 186.5 | 33% | 559 | 41% | 455 | 66% | 283 |
| 1/3 HP | 248.7 | 35% | 714 | 41% | 607 | 66% | 377 |

Table 136: Compressor Coefficient of Performance Based on Climate and Refrigeration Type (COPcooler or COPfreezer)

| Climate Zone | Summer Design T Dry Bulb Temperature | COPcooler | COPfreezer |
| --- | --- | --- | --- |
| Zone 1: Amarillo | 98.6 | 1.88 | 1.46 |
| Zone 2: Dallas-Fort Worth | 101.4 | 1.77 | 1.37 |
| Zone 3: Houston | 97.5 | 1.89 | 1.46 |
| Zone 4: Corpus Christi | 96.8 | 1.77 | 1.37 |
| Zone 5: El Paso | 101.1 | 1.74 | 1.35 |

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of ECMs are calculated using a deemed algorithm based on climate zone, refrigeration temperature, and whether the motors have controls, and are therefore not associated with deemed energy nor demand tables.

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 15 years as defined by the DEER 2014 EUL update (EUL ID—GrocDisp-FEvapFanMtr & GrocWlkIn-WEvapFanMtr).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Regional climate zone

- Building type

- Motor efficiency

- Motor power rating

- Evaporator fan control type

- Refrigeration temperature

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40669—Provides energy and demand savings and measure specifications

##### Relevant Standards and Reference Sources

- DEER 2014 EUL update.

### Electronic Defrost Controls Measure Overview

TRM Measure ID: NR-RF-DC

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Any commercial retail facility such as supermarkets, grocery stores, hotels, restaurants, and convenience stores

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of electronic defrost controls. The controls sense whether a defrost cycle is required in a refrigerated case and skips it if it is unnecessary.

##### Eligibility Criteria

Not applicable.

##### Baseline Condition

The baseline efficiency case is a refrigerated case without defrost controls or with an evaporator fan defrost system that uses a time clock mechanism to initiate electronic resistance defrost.

##### High-efficiency Condition

Eligible high-efficiency equipment is an evaporator fan defrost system with electronic defrost controls.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

The energy savings from the installation of electronic defrost controls are a result of savings due to the increase in operating efficiency and the reduced heat from a reduction in the number of defrosts. The energy and demand savings are calculated using the following equations:

Energy kWh=ΔkWhdefrost+ΔkWhheat

Equation 136

ΔkWhdefrost=kWdefrost×DRF×Hours

Equation 137

ΔkWhheat= ΔkWhdefrost ×0.28×Eff

Equation 138

Peak Demand kW=ΔkWhHours

Equation 139

Where:

ΔkWhdefrost	=	Energy savings resulting from an increase in operating efficiency due to the addition of electronic defrost controls

ΔkWhheat	=	Energy savings due to the reduced heat from reduced number of defrosts

kWdefrost	=	Load of electric defrost

Hours	=	Number of hours defrost occurs over a year without defrost controls

DRF	=	Defrost reduction factor—percent reduction in defrosts required per year

0.28	=	Conversion of kW to tons; 3,413 Btuh/kW divided by 12,000 Btuh/ton

Eff	=	Estimated efficiency based on climate and refrigeration temperature (i.e. low temperature or medium temperature)

Table 137: Deemed Variables for Energy and Demand Savings Calculations

| Climate Zone | DRF | EffMT | EffLT |
| --- | --- | --- | --- |
| Zone 1: Amarillo | 35% | 1.86 | 2.41 |
| Zone 2: Dallas-Ft. Worth |  | 1.98 | 2.57 |
| Zone 3: Houston |  | 1.86 | 2.41 |
| Zone 4: Corpus Christi |  | 1.98 | 2.57 |
| Zone 5: El Paso |  | 2.02 | 2.61 |

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of Defrost Controls are calculated using a deemed algorithm based on climate zone and refrigeration temperature and are therefore not associated with deemed energy nor demand tables.

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 10 years.

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Hours that defrost occurs over a year without defrost controls

- Load of electric defrost

- Refrigeration temperature (low temperature or medium temperature)

- Climate zone (Amarillo, Dallas-Fort Worth, El Paso, Houston, or McAllen)

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket No. 40669 provides energy and demand savings and measure specifications

##### Relevant Standards and Reference Sources

Not applicable.

### Evaporator Fan Controls Measure Overview

TRM Measure ID: NR-RF-FC

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Any commercial retail facility such as supermarkets, grocery stores, hotels, restaurants, and convenience stores

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of evaporator fan controls. As walk-in cooler and freezer evaporators often run continuously, this measure consists of a control system that turns the fan on only when the unit’s thermostat is calling for the compressor to operate.

##### Eligibility Criteria

Not applicable.

##### Baseline Condition

The baseline efficiency case is an existing shaded pole evaporator fan motor with no temperature controls, running 8,760 annual hours.

##### High-efficiency Condition

Eligible high-efficiency equipment will be regarded as an energy management system (EMS) or other electronic controls to modulate evaporator fan operation based on the temperature of the refrigerated space.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

The energy savings from the installation of evaporator fan controls are a result of savings due to the reduction in the operation of the fan. The energy and demand savings are calculated using the following equations:

Energy kWh=ΔkW×8760

Equation 140

Peak Demand kW=kWevap×nfans-kWcirc×1-DCcomp×DCevap×BF

Equation 141

Where:

kWevap	=	Connected load kW of each evaporator fan

kWcirc	=	Connected load kW of the circulating fan

nfans	=	Number of evaporator fans

DCcomp	=	Duty cycle of the compressor

DCevap	=	Duty cycle of the evaporator fan

BF	=	Bonus factor for reducing cooling load from replacing the evaporator fan with a lower wattage circulating fan when the compressor is not running

8760	=	Annual hours per year

Table 138: Deemed Variables for Energy and Demand Savings Calculations

| Variable | Deemed Values |
| --- | --- |
| kWevap | 0.123 kW |
| kWcirc | 0.035 kW |
| DCcomp | 50% |
| DCevap | Cooler: 100% Freezer: 94.4% |
| BF | Low Temp: 1.5 Medium Temp: 1.3 High Temp: 1.2 |

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of Evaporator Fan Controls are calculated using a deemed algorithm based on the temperature of the refrigerated case and duty cycle of the compressor and evaporator fan and are therefore not associated with deemed energy nor demand tables.

##### Measure Life and Lifetime Savings.

The EUL has been defined for this measure as 16 years per the PUCT approved Texas EUL filing (Docket No. 36779). This is consistent with the DEER 2014 EUL update (EUL ID—GrocWlkIn-WEvapFMtrCtrl).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Number of evaporator fans controlled

- Refrigeration type

- Refrigeration temperature

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket No. 40669 provides energy and demand savings and measure specifications

- PUCT Docket No. 36779 provides approved EUL for Evaporator Fan Controls

##### Relevant Standards and Reference Sources

- DEER 2014 EUL update

### Night Covers for Open Refrigerated Display Cases Measure Overview

TRM Measure ID: NR-RF-NC

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Any commercial retail facility such as supermarkets, grocery stores, hotels, restaurants, and convenience stores

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of night covers on the otherwise open vertical (multi-deck) and horizontal (or coffin-type) low-temperature and medium-temperature display cases to decrease the cooling load of the case during the night. It is recommended that these film-type covers have small, perforated holes to decrease the build-up of moisture.

##### Eligibility Criteria

Any suitable material sold as a night cover

##### Baseline Condition

The baseline efficiency case is an open low-temperature or medium-temperature refrigerated display case (vertical or horizontal) that is not equipped with a night cover.

##### High-efficiency Condition

Eligible high-efficiency equipment is considered any suitable material sold as a night cover. The cover must be applied for a period of at least 6 hours per day (i.e., continuous overnight use). Vertical strip curtains may be in use 24 hours per day.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

The following outlines the assumptions and approach used to estimate demand and energy savings resulting from the installation of night covers on open low- and medium-temperature, vertical and horizontal display cases. Heat transfer components of the display case include infiltration (convection), transmission (conduction), and radiation. The calculations assume that installing night covers on open display cases will only reduce the infiltration load on the case. At 75 ºF dry bulb temperature and 55% relative humidity, infiltration affects cooling load in the following ways:

- Infiltration accounts for approximately 80 percent of the total cooling load of open vertical (or multi-deck) display cases.

- Infiltration accounts for approximately 24 percent of the total cooling load of open horizontal (coffin or tub style) display cases.

Installing night covers for a period of 6 hours per night can reduce the cooling load due to infiltration by:

- 8% on vertical cases (and furthermore reduce the compressor power requirement by 9%)

- 50% on horizontal cases.

The energy savings due to the reduced infiltration load when night covers are installed will vary based on the outdoor temperature and climate zone. As a result, the energy savings must be determined for each climate zone and typical outdoor temperatures when the covers are applied.

Once the infiltration load for each type of case is determined, the following steps are taken to determine the compressor power requirements and energy savings. It is important to reiterate that heat transfer in display cases occurs due to convection, conduction, and radiation. The analysis presented here, though, is limited to the cooling load imposed by convection (infiltration) only and not the total cooling load of a particulate display case.

- In the base case, it is assumed that no night covers are installed on the cases and the infiltration cooling load for each bin can be given by:

QbaselineInfiltrationton-_hours=QbaselineInfiltrationBtuh×Bin-_hours12,000 Btuton

Equation 142

The compressor power requirements are based on calculated cooling load and energy-efficiency ratios (EER) obtained from manufacturers’ data.

- Determine the saturated condensing temperature (SCT):

For medium temperature (MT):

SCT=TDBDBadj+15

Equation 143

For low temperature (LT):

SCT=TDBDBadj+10

Equation 144

Where:

TDB	=	Summer design dry-bulb temperature (ºF), based on climate zone of ambient or space where the compressor/condensing units reside. Table 139 lists these summer design dry-bulb temperatures by climate zone.

Table 139: Summer Design Dry Bulb Temperatures by Climate Zone

| Climate Zone and Representative City | TDB |
| --- | --- |
| Zone 1: Amarillo | 96 |
| Zone 2: Dallas-Ft. Worth |  |
| Zone 3: Houston | 96 |
| Zone 4: McAllen | 100 |
| Zone 5: El Paso | 101 |

- Determine the EER for both medium temperature and low temperature applications.

- Compressor performance curves were obtained from a review of manufacturer data for reciprocating compressors as a function of SCT, cooling load, and cooling capacity of compressor.

- Part-load ratio (PLR) is the ratio of total cooling load to compressor capacity. It indicates the percentage of compressor capacity needed to remove the total cooling load. It is calculated by the following equation:

PLR=QcoolingQcapacity

Equation 145

Where:

PLR	=	Part load ratio

Qcooling 	=	Cooling load

Qcapacity	=	Total compressor capacity

Qcapacity=Qcooling×1.15

Equation 146

PLR=11.15≈=0.87

Equation 147

To simplify the analysis, it is assumed that PLR remains constant at 1/1.15 for the post-retrofit condition .

The energy efficiency ratio (EER) is a measure of how efficient a cooling system operates at a particular temperature. It is defined as the ratio of useful energy transfer to the work input. For refrigeration systems, it is the ratio of heat removed by the compressor (Btu/h) to the input power (Watts). The higher the EER the greater the efficiency of the system.

For medium temperature compressors, the following equation is used to determine the EERMT (Btu/hr/watts). The equation uses SCT (from step 2), and a PLR of 0.87 (from step 3b).

EERMT=a+b×SCT+c×PLR+d×SCT2+ e×PLR2+f×SCT×PLR+g×SCT3+h×PLR3+i×SCT×PLR2+j×SCT2×PLR

Equation 148

Where:

a	=	3.75346018700468

b 	=	-0.049642253137389

c 	= 	29.4589834935596

d	=	 0.000342066982768282

e	=	 -11.7705583766926

f	=	 -0.212941092717051

g	=	 -1.46606221890819 x 10-6

h	=	 6.80170133906075

i	=	 -0.020187240339536

j	=	 0.000657941213335828

For low temperature compressors, the following equation is used to determine the EERLT (Btu/hr/watts). The equation uses SCT (from step 2), and a PLR of 0.87 (from step 3b).

EERLT=a+b×SCT+c×PLR+d×SCT2+ e×PLR2+f×SCT×PLR+g×SCT3+h×PLR3+i×SCT×PLR2+j×SCT2×PLR

Equation 149

Where:

a 		=	 9.86650982829017

b		=	 -0.230356886617629

c		=	 22.905553824974

d		=	 0.00218892905109218

e		=	 -2.48866737934442

f		=	 -0.248051519588758

g		=	 -7.57495453950879 x 10-6

h		=	 2.03606248623924

i		=	 -0.0214774331896676

j		=	 0.00938305518020252

Convert EER to kW/ton

kWton=12EER

Equation 150

Energy used by the compressor to remove heat imposed due to infiltration in the base case for each bin reading is determined based on the calculated cooling load and EER, as outlined below.

kWhbaseline-_refrig-_bin=Qbaseline-iInfiltration[ton-_hours]×kWton

Equation 151

Total annual baseline refrigeration energy consumption is the sum of all bin values.

kWhbaseline-_refrig= kWhbaseline-_refrig-_bin

Equation 152

In the post-retrofit case, it is assumed that night covers are installed on the cases during the nights from midnight to 6:00 AM. During the day, the cases are uncovered and the total cooling load for each bin can be given by:

Qpost-rRetrofitton-_hours=Qbaseline-iInfiltration Btuh×Daytimebin-_hrs12,000 Btuhton+ (Qbaseline-iInfiltration Btuh-Qreduced-iInfiltration Btuh)×Nighttimebin-_hrs12,000 Btuhton

Equation 153

These steps are repeated in the post-retrofit case to calculate the post-retrofit energy and demand usage.

The energy savings were determined as the difference between the baseline energy use and post-retrofit energy use:

∆kWhtotal=kWhtotalBaseline-kWhtotalPostRetrofit

Equation 154

##### Deemed Energy and Demand Savings Tables

The energy and demand savings of night covers are based on PG&E Night Covers Work Paper. PG&E modeled the infiltration load of refrigerator cases without night covers and refrigerators with night covers to derive the energy savings. The PG&E report estimated savings for several climate zones. The climate zone (Amarillo, Texas) was chosen to represent the entire state. The deemed energy and demand savings are shown below.

Table 140: Modeled Deemed Savings for Night Covers for Texas (per Linear Foot)

| Measure | Energy Savings [kWh/ft] | Demand Savings [kW/ft] |
| --- | --- | --- |
| Night Covers on Vertical Low-temperature Cases | 45 | 0 |
| Night Covers on Horizontal Low-temperature Cases | 23 | 0 |
| Night Covers on Vertical Medium-temperature Cases | 35 | 0 |
| Night Covers on Horizontal Medium-temperature Cases | 17 | 0 |

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 5 years in the DEER 2014 EUL update (EUL ID—GrocDisp-DispCvrs) .

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Display case type

- Refrigeration temperature

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40669 provides energy and demand savings and measure specifications: https://interchange.puc.texas.gov/Documents/40669_7_736774.PDF. Accessed 11/13/2019.

##### Relevant Standards and Reference Sources

- DEER 2014 EUL update

### Solid and Glass Door Reach-Ins Measure Overview

TRM Measure ID: NR-RF-RI

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Any commercial retail facility such as supermarkets, grocery stores, hotels, restaurants, and convenience stores

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of ENERGY STAR® or CEE certified solid and glass door reach-in refrigerators and freezers, which are significantly more efficient than non- ENERGY STAR® units. The high-efficiency criteria, developed by ENERGY STAR®, relate the volume of the appliance in cubic feet to its daily energy consumption

##### Eligibility Criteria

Solid- or glass-door reach-in vertical refrigerators and freezers must meet ENERGY STAR® minimum efficiency requirements (See Table 142).

The following products are excluded from the ENERGY STAR® eligibility criteria:

- Residential refrigerators and freezers

- Chef base or griddle stands, prep tables, service over counter equipment, horizontal open equipment, vertical open equipment, semi-vertical open equipment, remote condensing equipment, convertible temperature equipment, and ice cream freezers

##### Baseline Condition

The baseline efficiency case is a regular vertical refrigerator or freezer with anti-sweat heaters on doors that meets federal standards. The baseline daily kWh for solid door and glass door commercial reach-in refrigerators and freezers are shown in Table 141.

Table 141: Baseline Energy Consumption,

| Baseline Standards | Refrigerator Daily Consumption (kWh) | Freezer Daily Consumption (kWh) |
| --- | --- | --- |
| Solid Door | 0.10V + 2.04 | 0.40V + 1.38 |
| Glass Door | 0.12V + 3.34 | 0.75V + 4.10 |

##### High-efficiency Condition

Eligible high-efficiency equipment for solid- or glass-door reach-in refrigerators and freezers must meet the ENERGY STAR® minimum efficiency requirements, as shown in Table 142 below:

Table 142: Efficient Energy Consumption Requirements

| Door Type | Product Volume (cubic feet) | Refrigerator Daily Consumption (kWh) | Freezer Daily Consumption (kWh) |
| --- | --- | --- | --- |
| Vertical Solid Door | 0 < V < 15 | 0.022V + 0.97 | 0.21V + 0.9 |
|  | 15 ≤ V < 30 | 0.066V + 0.31 | 0.12V + 2.248 |
|  | 30 ≤ V < 50 | 0.04V + 1.09 | 0.285V - 2.703 |
|  | V ≥ 50 | 0.024V + 1.89 | 0.142V + 4.445 |
| Vertical Glass Door | 0 < V < 15 | 0.095V + 0.445 | 0.232V + 2.36 |
|  | 15 ≤ V < 30 | 0.05V + 1.12 |  |
|  | 30 ≤ V < 50 | 0.076V + 0.34 |  |
|  | V ≥ 50 | 0.105V - 1.111 |  |

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

The energy and demand savings of solid- and glass-door reach-in refrigerators and freezers are calculated using values in Table 141 and Table 142, based on the volume of the units.

The savings calculations are specified as:

Energy kWh=kWhbase-kWhee×365

Equation 155

Peak Demand kW=∆kWh8760×CF

Equation 156

Where:

kWhbase	=	Baseline maximum daily energy consumption in kWh, based on volume (V) of unit, found in Table 141.

kWhee	=	Efficient maximum daily energy consumption in kWh, based on volume (V) of unit, found in Table 142.

V	=	Chilled or frozen compartment volume [ft3] (as defined in the Association of Home Appliance Manufacturers Standard HRF-1-1979)

365	=	Days per year

8760	=	Hours per year

CF	=	Summer peak coincidence factor (1.0)

##### Deemed Energy and Demand Savings Tables

Table 143: Deemed Energy and Demand Savings

| Refrigerator or Freezer | Door Type | Product Volume Range (cubic feet) | Average Product Volume | Energy Savings (kWh) | Demand Savings (kW) |
| --- | --- | --- | --- | --- | --- |
| Refrigerator | Vertical Solid Door | 0 < V < 15 | 8.54 | 16 | 0.002 |
|  |  | 15 ≤ V < 30 | 21.00 | 892 | 0.102 |
|  |  | 30 ≤ V < 50 | 41.53 | 1,256 | 0.143 |
|  |  | V ≥ 50 | 67.19 | 1,919 | 0.219 |
|  | Vertical Glass Door | 0 < V < 15 | 8.84 | 1,137 | 0.130 |
|  |  | 15 ≤ V < 30 | 21.30 | 1,355 | 0.155 |
|  |  | 30 ≤ V < 50 | 42.76 | 1,782 | 0.203 |
|  |  | V ≥ 50 | 68.93 | 2,002 | 0.229 |
| Freezer | Vertical Solid Door | 0 < V < 15 | 7.76 | 713 | 0.081 |
|  |  | 15 ≤ V < 30 | 19.99 | 1,726 | 0.197 |
|  |  | 30 ≤ V < 50 | 43.13 | 3,301 | 0.377 |
|  |  | V ≥ 50 | 66.86 | 5,177 | 0.591 |
|  | Vertical Glass Door | 0 < V < 15 | 5.98 | 1,766 | 0.202 |
|  |  | 15 ≤ V < 30 | 19.49 | 4,321 | 0.493 |
|  |  | 30 ≤ V < 50 | 42.29 | 8,630 | 0.985 |
|  |  | V ≥ 50 | 65.89 | 13,093 | 1.495 |

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 12 years, per the PUCT Texas EUL filing (Docket No. 36779). This is consistent with the 2014 DEER EUL update.

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Baseline unit volume

- Baseline unit door type (solid or glass)

- Baseline unit temperature (refrigerator or freezer)

- Post-retrofit unit volume

- Post-retrofit unit door type (solid or glass)

- Post-retrofit unit temperature (refrigerator or freezer)

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40669 provides energy and demand savings and measure specifications

- PUCT Docket 36779 provides EUL estimates for commercial refrigerators and freezers.

##### Relevant Standards and Reference Sources

- ENERGY STAR® Commercial Refrigerators and Freezers. http://www.energystar.gov/index.cfm?fuseaction=find_a_product.showProductGroup&pgw_code=CRF. Accessed 08/20/2013.

- Association of Home Appliance Manufacturers. HRF-1: Household Refrigerators, Combination Refrigerator-Freezers, and Household Freezers.

### Strip Curtains for Walk-In Refrigerated Storage Measure Overview

TRM Measure ID: NR-RF-SC

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Any commercial retail facility such as supermarkets, grocery stores, hotels, restaurants and, convenience stores

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: M&V analysis

#### Measure Description

This measure refers to the installation of infiltration barriers (strip curtains or plastic swinging doors) on walk-in coolers or freezers. These units impede heat transfer from adjacent warm and humid spaces into walk-ins when the main door is opened, reducing the cooling load. This results in a reduced compressor run-time, reducing energy consumption. This assumes that a walk-in door is open 2.5 hours per day every day, and strip curtains cover the entire doorframe.

##### Eligibility Criteria

Strip curtains or plastic swinging doors installed on walk-in coolers or freezers.

##### Baseline Condition

The baseline efficiency case is a refrigerated walk-in space with nothing to impede airflow from the refrigerated space to adjacent warm and humid space when the door is opened.

##### High-efficiency Condition

Eligible high-efficiency equipment in a polyethylene strip curtain added to the walk-in cooler or freezer. Any suitable material sold as a strip cover for a walk-in unit is eligible if it covers the entire doorway.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Savings are derived from an M&V study.

##### Deemed Energy and Demand Savings Tables

The energy and demand savings for strip curtains are based on the assumption that the walk-in door is open 2.5 hours per day, every day, and the strip curtain covers the entire doorframe, and are shown below in Table 144.

Table 144: Deemed Energy and Demand Savings for Freezers and Coolers

| Savings | Coolers | Freezers |
| --- | --- | --- |
| Energy [kWh] | 422 | 2,974 |
| Demand [kW] | 0.05 | 0.35 |

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 4 years, per the PUCT Texas EUL filing (Docket No. 36779) and by the DEER 2014 EUL update (EUL ID—GrocWlkIn-StripCrtn).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Unit temperature (refrigerator or freezer)

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40669 provides energy and demand savings and measure specifications

- PUCT Docket 36779 provides EUL estimates for commercial refrigerators and freezers

##### Relevant Standards and Reference Sources

- DEER 2014 EUL update

### Zero-Energy Doors for Refrigerated Cases Measure Overview

TRM Measure ID: NR-RF-ZE

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Any commercial retail facility such as supermarkets, grocery stores, hotels, restaurants, and convenience stores

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This document presents the deemed savings methodology for the installation of zero-energy doors for refrigerated cases. These new zero-energy door designs eliminate the need for anti-sweat heaters to prevent the formation of condensation on the glass surface by incorporating heat reflective coatings on the glass, gas inserted between the panes, non-metallic spacers to separate glass panes, and/or non-metallic frames.

##### Eligibility Criteria

This measure cannot be used in conjunction with anti-sweat heat (ASH) controls. It is not eligible to be installed on cases above 0ºF.

##### Baseline Condition

The baseline efficiency case is a standard vertical reach-in refrigerated case with anti-sweat heaters on the glass surface of the doors.

##### High-efficiency Condition

Eligible high-efficiency equipment is the installation of special doors that eliminate the need for anti-sweat heaters, for low-temperature cases only (below 0 ºF). Doors must have either heat-reflective treated glass, be gas-filled, or both.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

The energy savings from the installation of zero energy doors are a result of eliminating the heater (kWhASH) and the reduction in load on the refrigeration (kWhrefrig). These savings are calculated using the following procedures.

td-in=0.005379×td-out2+0.171795×td-out+19.87006

The baseline assumes door heaters are running on an 8,760-hour operating schedule. In the post-retrofit case, it is assumed that the door heaters will be all off (duty cycle of 0 percent).

The instantaneous door heater power (kWASH) as a resistive load remains constant is per linear foot of door heater at:

For medium temperature:

kWAsh = 0.109 per door or 0.0436 per linear foot of door

For low temperature:

kWAsh = 0.191 per door or 0.0764 per linear foot of door

Door heater energy consumption for each hour of the year is a product of power and run-time:

kWhASH-Hourly=kWASH×Door Heater ON% ×1Hour

Equation 157

kWhASH= kWhASH-Hourly

Equation 158

To calculate energy savings from the reduced refrigeration load using average system efficiency and assuming that 35 percent of the anti-sweat heat becomes a load on the refrigeration system, the cooling load contribution from door heaters can be given by:

QASHton-hrs=0.35×kWASH×3413Btuhr12000Btuton×Door Heater ON%

Equation 159

The compressor power requirements are based on calculated cooling load and energy-efficiency ratios obtained from manufacturers' data. The compressor analysis is limited to the cooling load imposed by the door heaters, not the total cooling load of the refrigeration system.

For medium temperature refrigerated cases, the saturated condensing temperature (SCT) is calculated as the design dry-bulb temperature plus 15 degrees. For low temperature refrigerated cases, the SCT is the design dry-bulb temperature plus 10 degrees. The EER for both medium- and low-temperature applications is a function of SCT and part load ratio (PLR) of the compressor. PLR is the ratio of total cooling load to compressor capacity and is assumed to be a constant of 1/1.15 or approximately 0.87.

For medium temperature compressors, the following equation is used to determine the EERMT [Btu/hr/watts]. These values are shown in Table 132.

EERMT=a+b×SCT+c×PLR+d×SCT2+e×PLR2+f×SCT×PLR+g×SCT3+h×PLR3+i×SCT×PLR2+j×SCT2×PLR

Equation 160

Where:

a	=	3.75346018700468

b	=	-0.049642253137389

c	=	29.4589834935596

d	=	0.000342066982768282

e 	=	-11.7705583766926

f 	=	-0.212941092717051

g	=	-1.46606221890819 x 10-6

h	=	6.80170133906075

I	=	-0.020187240339536

j	=	0.000657941213335828

PLR	=	0.87

SCT	=	TDB + 15

For low temperature compressors, the following equation is used to determine the EERLT [Btu/hr/watts]:

EERLT=a+b×SCT+c×PLR+d×SCT2+e×PLR2+f×SCT×PLR+g×SCT3+h×PLR3+i×SCT×PLR2+j×SCT2×PLR

Equation 161

Where:

a	=	9.86650982829017

b	=	-0.230356886617629

c 	=	22.905553824974

d	=	0.00218892905109218

e	=	-2.4886737934442

f	=	-0.248051519588758

g	=	-7.57495453950879 x 10-6

h	=	2.03606248623924

i	=	-0.0214774331896676

j	=	0.000938305518020252

PLR	=	0.87

SCT	=	TDB +10

Table 145: Coefficients by Climate Zone

| Climate Zone | TDB | Td-out | SCTMT | SCTLT | EERMT | EERLT |
| --- | --- | --- | --- | --- | --- | --- |
| Zone 1: Amarillo | 98.6 | 67.2 | 113.6 | 108.6 | 6.18 | 4.74 |
| Zone 2: Dallas-Ft. Worth | 101.4 | 75.4 | 116.4 | 111.4 | 5.91 | 4.56 |
| Zone 3: Houston | 97.5 | 78.0 | 112.5 | 107.5 | 6.29 | 4.86 |
| Zone 4: Corpus Christi | 96.8 | 79.1 | 111.8 | 106.8 | 6.36 | 4.91 |
| Zone 5: El Paso | 101.1 | 66.3 | 116.1 | 111.1 | 5.94 | 4.58 |

Where:

TDB	=	Dry Bulb Temperature

Td-out	=	Outdoor Dew Point

Energy used by the compressor to remove heat imposed by the door heaters for each hourly reading is determined based on calculated cooling load and EER, as outlined below:

kWhrefrig-hourly=QASH×12EER

Equation 162

kWhrefrig= kWhrefrig-Hourly

Equation 163

Total annual energy consumption (direct door heaters and indirect refrigeration) is the sum of all hourly reading values:

kWhtotal=kWhrefrig+kWhASH

Equation 164

Total energy savings is a result of the baseline and post-Retrofit case:

Annual Energy Savings kWh=kWhtotal-baseline+-kWhtotal-post

Equation 165

While there might be instantaneous demand savings because of the cycling of the door heaters, peak demand savings will only be due to the reduced refrigeration load. Peak demand savings is calculated by the following equation:

Peak Demand Savings=kWhrefrig-baseline-kWhrefrig-post8760

Equation 166

Table 146: Deemed Energy and Demand Savings Values by Climate Zone and Refrigeration Temperature

| Climate Zone | Medium Temperature |  | Low Temperature |  |
| --- | --- | --- | --- | --- |
|  | Annual Energy Savings [kWh/ft] | Peak Demand Savings [kW/ft] | Annual Energy Savings [kWh/ft] | Peak Demand Savings [kW/ft] |
| Zone 1: Amarillo | 1,139 | 0.130 | 2,092 | 0.239 |
| Zone 2: Dallas-Ft. Worth | 1,148 | 0.131 | 2,111 | 0.241 |
| Zone 3: Houston | 1,136 | 0.130 | 2,084 | 0.238 |
| Zone 4: Corpus Christi | 1,134 | 0.129 | 2,080 | 0.237 |
| Zone 5: El Paso | 1,147 | 0.131 | 2,109 | 0.241 |

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 12 years per the PUCT approved Texas EUL filing (Docket No. 36779) and the DEER 2014 EUL update (EUL ID—GrocDisp-ZeroHtDrs).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Refrigeration temperature range

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40669 provides energy and demand savings and measure specifications

- PUCT Docket 36779 provides EUL values for Zero Energy Doors

##### Relevant Standards and Reference Sources

- DEER 2014 EUL update

### Door Gaskets for Walk-In and Reach-In Coolers and Freezers Measure Overview

TRM Measure ID: NR-RF-DG

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Any commercial retail facility such as supermarkets, convenience stores, restaurants, and, refrigerated warehouses

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: M&V, engineering algorithms, and estimates

      - Measure Description

This measure applies to the installation of door gaskets on walk-in and reach-in coolers and freezers to reduce the refrigeration load associated with the infiltration of non-refrigerated air into the refrigerated space. Additionally, the reduction in moisture entering the refrigerated space also helps prevent frost on the cooling coils. Frost build-up adversely impacts the coil’s heat transfer effectiveness, reduces air passage (lowering heat transfer efficiency), and increases energy use during the defrost cycle. Therefore, replacing defective door gaskets reduces compressor run time, reducing energy consumption and improving the overall effectiveness of heat removal from a refrigerated cabinet.

        - Eligibility Criteria

Door gaskets must be installed on walk-in and reach-in coolers or freezers. The most common applications for this measure are refrigerated coolers or freezers in supermarkets, convenience stores, restaurants, and refrigerated warehouses.

        - Baseline Condition

The baseline standard for this measure is a walk-in or reach-in cooler or freezer with worn-out, defective door gaskets. An average baseline gasket efficacy of 90 percent is assumed for this measure.

        - High-efficiency Condition

The efficient condition for this measure is a new, better-fitting gasket. Tight fitting gaskets inhibit infiltration of warm, moist air into the cold refrigerated space, reducing the cooling load. A decrease in moisture entering the refrigerated space also prevents frost on cooling coils.

      - Energy and Demand Savings Methodology

The energy savings assumptions are based on DEER 2005 analysis performed by Southern California Edison (SCE) and an evaluation of a Pacific Gas and Electric (PG&E) direct install refrigeration measures for program year 2006-2008., The results from the PG&E evaluation were used as the foundation for establishing the energy savings for the refrigeration gasket measures. The energy savings achievable for new gaskets replacing baseline gaskets were found during this study to be dependent almost entirely on the leakage through the baseline gaskets. Therefore, the energy savings attributable to door gaskets were derived for various scenarios regarding baseline gasket efficacies and are shown in Table 147 below.

Table 147: Energy Savings Achievable for New Gaskets Replacing Baseline Gaskets of Various Efficacies (per Linear Foot of Installed Door Gasket)

| Refrigerator Type | Baseline 0% Efficacy (kWh/ft) | Baseline 50% Efficacy (kWh/ft) | Baseline 90% Efficacy (kWh/ft) | Baseline 100% Efficacy (kWh/ft) |
| --- | --- | --- | --- | --- |
| Cooler | 30 | 15 | 3 | 0 |
| Freezer | 228 | 114 | 23 | 0 |

As the PG&E analysis was performed in California with different climate zones as compared to those in Texas, an analysis was conducted to develop an adjustment factor to associate the savings in the table above to Texas anticipated results. The PG&E study could not be used to determine these effects, as insufficient climate zones were researched. Therefore, the SCE study was utilized as savings in this study were determined for each of the 16 climate zones in California and were similar to those assessed within the PG&E results at 90 percent efficacy. A comparison was completed between the SCE energy savings and the typical meteorological year 3 (TMY3) data to establish a cooling degree day (CDD) correlations across the 16 California climate zones.  provides a summary comparison for coolers and  for freezers. The resulting correlations are strong, with an R2 of 0.85 for coolers and an R2 of 0.88 for freezers, respectively.

Figure 3: Comparison of Projected Annual Energy Savings to Cooling Degree Days for All 16 California Climate Zones for Reach-in Display Cases (Coolers)

Figure 4: Comparison of Projected Annual Energy Savings to Cooling Degree Days for All 16 California Climate Zones for Reach-in Display Cases (Freezers)

These correlations were used to adjust the energy savings and TMY3 CDDs in California to TMY3 CDDs in Texas to determine an average energy savings of 7.4 and 20.0 kWh/linear feet for coolers and freezers in Texas. Comparing the average energy savings between California and Texas, the CDD adjustment results in a 113 percent adjustment factor for coolers and a 117 percent adjustment factor for freezers. For simplicity, an average adjustment factor of 115 percent  (the midpoint of 113% and 117% TX vs. CA Energy Savings values) was applied to the PG&E results at 90 percent efficacy (as shown in Table 147 above), resulting in Texas-based annual energy savings values for coolers of 3.5 kWh/linear feet and freezers of 26.5 kWh/linear feet. These results are summarized in Table 148 below.

Table 148: Energy Savings Achievable for New Gaskets Replacing Baseline Gaskets of Various Efficacies (per Linear Foot of Installed Door Gasket)

| Refrigerator Type | CA CZ1-CZ16 Average Savings (kWh/ft) | CA Average Savings Normalized to TX by CDD (kWh/ft) | TX vs. CA Energy Savings | Average CDD Adjustment Factor | PG&E Baseline 90% Efficacy (kWh/ft) | TX Baseline 90% Efficacy (kWh/ft) |
| --- | --- | --- | --- | --- | --- | --- |
| Cooler | 6.5 | 7.4 | 113% | 115% | 3 | 3.5 |
| Freezer | 17.1 | 20.0 | 117% |  | 23 | 26.5 |

Because the walk-in or reach-in cooler or freezer is kept at a constant temperature, the demand savings are estimated as the total energy savings divided evenly over the full year (8760 hours).

        - Savings Algorithms and Input Variables

The energy and demand algorithms and associated input variables are listed below:

Energy Savings kWh=ΔkWhft×L

Equation 167

Demand Savings kW=kWhSavings8760×L

Equation 168

Where:

ΔkWh/ft	=	Annual energy savings per linear foot of gasket (see Table 149)

L 	=	Total gasket length (ft)

        - Deemed Energy and Demand Savings Tables

Table 149: Deemed Energy and Demand Savings per Linear Foot of Installed Door Gasket

| Refrigerator Type | ΔkW/ft | ΔkWh/ft |
| --- | --- | --- |
| Walk-in or Reach-in Cooler | 0.0004 | 3.5 |
| Walk-in or Reach-in Freezer | 0.0030 | 26.5 |

##### Claimed Peak Demand Savings

Because the walk-in or reach-in cooler or freezer is kept at a constant temperature, the demand savings are estimated as the total energy savings divided evenly over the full year (8760 hours).

##### Measure Life and Lifetime Savings

The EUL for this measure is 4 years, according to the California Database of Energy Efficiency Resources (EUL ID – GrocDisp-FixtDrGask).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Building type (convenience store, supermarket, restaurant, refrigerated warehouse)

- Refrigerator type (walk-in or reach-in cooler or freezer)

- Total length of installed gasket (ft.)

- Presence of existing gasket (yes/no)

- Optional (if applicable): length of ineffective baseline gasket (feet), general description of baseline gasket condition (e.g., good, moderate, poor, non-existent), and primary reason for baseline gasket ineffectiveness (partial tear, torn and dislocated, rotted/dry, poor fit/shrink, missing, or other)

      - References and Efficiency Standards

        - Petitions and Rulings

- Docket No. 48265. Petition of AEP Texas Inc., CenterPoint Energy Houston Electric, LLC, El Paso Electric Company, Entergy Texas, Inc., Oncor Electric Delivery Company LLC, Southwestern Electric Power Company, Southwestern Public Service Company, and Texas-New Mexico Power Company. Petition to Approve Deemed Savings for New Nonresidential Door Air Infiltration, Nonresidential Door Gaskets, And Residential ENERGY STAR Connected Thermostats. Public Utility Commission of Texas.

        - Relevant Standards and Reference Sources

Not applicable.

## Nonresidential: Miscellaneous

### Vending Machine Controls Measure Overview

TRM Measure ID: NR-MS-VC

Market Sector: Commercial

Measure Category: Miscellaneous

Applicable Building Types: All building types applicable

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: M&V

#### Measure Description

This section presents the deemed savings methodology for the installation of vending machine controls to reduce energy usage during periods of inactivity. These controls reduce energy usage by powering down the refrigeration and lighting systems when the control device signals that there is no human activity near the machine. If no activity or sale is detected over the manufacturer’s programmed time duration, the device safely de-energizes the compressor, condenser fan, evaporator fan, and any lighting. For refrigerated machines, it will power up occasionally to maintain cooling to meet the machine’s thermostat set point. When activity is detected, the system returns to full power. The energy and demand savings are determined on a per-vending machine basis.

##### Eligibility Criteria

Not applicable.

##### Baseline Condition

Eligible baseline equipment is a 120-volt single phase refrigerated beverage or non-refrigerated snack vending machine. Refrigerated beverage vending machines manufactured and purchased prior to August 31, 2012. Refrigerated beverage vending machines manufactured after this date must already comply with federal standard maximum daily energy consumption requirements. The current federal standard further reduced these maximum consumption values, effective January 8, 2019.

##### High-efficiency Condition

Eligible equipment is a refrigerated vending machine or non-refrigerated snack machine (including warm beverage machines) without any controls. It is assumed that the display lighting has not been permanently disabled.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Not applicable

##### Deemed Energy and Demand Savings Tables

Energy and demand savings for different sized vending machines are deemed values, pieced together from different sources and studies, outlined in the following tables.

Table 150: Vending Machine Controls – Refrigerated Cold Drink Unit Deemed Savings

| Climate Zone | kWh Savings | Summer kW Savings | Winter kW Savings |
| --- | --- | --- | --- |
| Zone 1: Amarillo | 1,612 | 0.023 | 0.060 |
| Zone 2: Dallas |  | 0.021 | 0.063 |
| Zone 3: Houston |  | 0.022 | 0.060 |
| Zone 4: Corpus Christi |  | 0.022 | 0.064 |
| Zone 5: El Paso |  | 0.015 | 0.068 |

Table 151: Vending Machine Controls – Refrigerated Reach-in Unit Deemed Savings

| Climate Zone | kWh Savings | Summer kW Savings | Winter kW Savings |
| --- | --- | --- | --- |
| Zone 1: Amarillo | 1,086 | 0.026 | 0.069 |
| Zone 2: Dallas |  | 0.024 | 0.073 |
| Zone 3: Houston |  | 0.026 | 0.068 |
| Zone 4: Corpus Christi |  | 0.026 | 0.074 |
| Zone 5: El Paso |  | 0.017 | 0.078 |

Table 152: Vending Machine Controls – Non-refrigerated Snack Unit Deemed Savings

| Climate Zone | kWh Savings | Summer kW Savings | Winter kW Savings |
| --- | --- | --- | --- |
| Zone 1: Amarillo | 387 | 0.005 | 0.013 |
| Zone 2: Dallas |  | 0.004 | 0.013 |
| Zone 3: Houston |  | 0.005 | 0.013 |
| Zone 4: Corpus Christi |  | 0.005 | 0.014 |
| Zone 5: El Paso |  | 0.003 | 0.014 |

##### Measure Life and Lifetime Savings

The EUL has been defined for this measure as 5 years per the PUCT approved Texas EUL filing (Docket No. 36779) and the DEER 2014 EUL update (EUL ID—Plug-VendCtrler).

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Vending machine type - refrigerated cold drink unit, refrigerated reach-in unit, or non-refrigerated snack unit with lighting

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40669—Provides energy and demand savings and measure specifications. Appendix A: https://interchange.puc.texas.gov/Documents/40669_3_735684.PDF. Accessed 11/14/2019.

- PUCT Docket 36779—Provides EUL for Vending Machine Controls.

##### Relevant Standards and Reference Sources

- Chappell, C., Hanzawi, E., Bos, W., Brost, M., and Peet, R. (2002). "Does It Keep the Drinks Cold and Reduce Peak Demand? An Evaluation of a Vending Machine Control Program," 2002 ACEEE Summer Study on Energy Efficiency in Buildings Proceedings, pp. 10.47-10.56. https://aceee.org/files/proceedings/2002/data/papers/SS02_Panel10_Paper05.pdf. Accessed 11/14/2019.

- DEER 2014 EUL update.

### Lodging Guest Room Occupancy Sensor Controls Measure Overview

TRM Measure ID: NR-MS-LC

Market Sector: Commercial

Measure Category: HVAC, Indoor Lighting

Applicable Building Types: Hotel/motel guest rooms, schools/colleges (dormitory)

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Energy modeling

#### Measure Description

This measure, commonly referred to as a guest room energy management (GREM) system, captures the potential energy and demand savings resulting from occupancy sensor control of HVAC and lighting in unoccupied hotel/motel guest rooms. Hotel and motel guest room occupancy schedules are highly variable, and guests often leave HVAC equipment and lighting on when they leave the room. Installation of occupancy controls can reduce the unnecessary energy consumption in unoccupied guest rooms. Savings have also been developed for the use of this measure in college dormitories.

##### Eligibility Criteria

To be eligible for HVAC savings, controls must be capable of either a 5ºF or 10ºF temperature offset. To be eligible for lighting savings, at least 50 percent of all the lighting fixtures in a guest room—both hardwired and plug-load lighting—must be actively controlled.

##### Baseline Condition

The baseline condition is a guest room or dorm room without occupancy controls.

##### High-efficiency Condition

The high-efficiency condition is a guest room or dorm room with occupancy controls. The occupancy sensors can control either the HVAC equipment only or the HVAC equipment and the interior lighting (including plug-in lighting).

The occupancy-based control system must include, but not be limited to, infrared sensors, ultrasonic sensors, door magnetic strip sensors, and/or card-key sensors. The controls must be able to either completely shut-off the HVAC equipment serving the space and/or place it into an unoccupied temperature setback/setup mode.

#### Energy and Demand Savings Methodology

Energy and demand savings are deemed values based on energy simulation runs performed using EnergyPro Version 5. Building prototype models were developed for a hotel, motel, and dormitory building types. The base case for each prototype model assumed a uniform temperature setting and was calibrated to a baseline energy use. Occupancy patterns based on both documented field studies and prototypical ASHRAE 90.1-1999 occupancy schedules were used in the energy simulation runs to create realistic vacancy schedules. The prototype models were then adjusted to simulate an occupancy control system, which was compared to the baseline models.

##### Savings Algorithms and Inputs

A building simulation approach was used to produce savings estimates.

##### Deemed Energy and Demand Savings Tables

Energy and demand savings are provided by region, for HVAC-only, HVAC + lighting control configurations, and for three facility types: motel guest rooms, hotel guest rooms, and dormitory rooms.

Table 153: Deemed Energy and Demand Savings for Motel per Guest Room, by Region

| Representative City (Region) | Heat Pump |  |  |  | Electric Resistance Heat |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | HVAC-Only |  | HVAC and Lighting |  | HVAC-Only |  | HVAC and Lighting |  |
|  | kW | kWh | kW | kWh | kW | kWh | kW | kWh |
| 5-Degree Setup/Setback Offset |  |  |  |  |  |  |  |  |
| Amarillo (Panhandle) | 0.059 | 267 | 0.075 | 380 | 0.059 | 341 | 0.075 | 441 |
| Dallas (North) | 0.076 | 315 | 0.091 | 443 | 0.076 | 365 | 0.091 | 485 |
| Houston (South) | 0.082 | 324 | 0.097 | 461 | 0.082 | 351 | 0.097 | 484 |
| McAllen (Valley) | 0.086 | 354 | 0.103 | 500 | 0.086 | 369 | 0.103 | 513 |
| El Paso (West) | 0.063 | 251 | 0.078 | 379 | 0.063 | 283 | 0.078 | 406 |
| 10-Degree Setup/Setback Offset |  |  |  |  |  |  |  |  |
| Amarillo (Panhandle) | 0.111 | 486 | 0.126 | 598 | 0.111 | 627 | 0.126 | 726 |
| Dallas (North) | 0.146 | 559 | 0.161 | 686 | 0.146 | 640 | 0.161 | 761 |
| Houston (South) | 0.151 | 559 | 0.166 | 695 | 0.151 | 602 | 0.166 | 735 |
| McAllen (Valley) | 0.163 | 617 | 0.179 | 761 | 0.163 | 650 | 0.179 | 792 |
| El Paso (West) | 0.118 | 432 | 0.133 | 561 | 0.118 | 482 | 0.133 | 607 |

Table 154: Deemed Energy and Demand Savings for Hotel per Guest Room, by Region

| Representative City (Region) | Heat Pump |  |  |  | Electric Resistance Heat |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | HVAC-Only |  | HVAC and Lighting |  | HVAC-Only |  | HVAC and Lighting |  |
|  | kW | kWh | kW | kWh | kW | kWh | kW | kWh |
| 5-Degree Setup/Setback Offset |  |  |  |  |  |  |  |  |
| Amarillo (Panhandle) | 0.053 | 232 | 0.072 | 439 | 0.053 | 303 | 0.072 | 530 |
| Dallas (North) | 0.073 | 258 | 0.093 | 452 | 0.073 | 303 | 0.093 | 505 |
| Houston (South) | 0.074 | 242 | 0.094 | 430 | 0.074 | 260 | 0.094 | 450 |
| McAllen (Valley) | 0.081 | 260 | 0.102 | 451 | 0.081 | 267 | 0.102 | 459 |
| El Paso (West) | 0.056 | 178 | 0.075 | 360 | 0.056 | 196 | 0.075 | 380 |
| 10-Degree Setup/Setback Offset |  |  |  |  |  |  |  |  |
| Amarillo (Panhandle) | 0.102 | 426 | 0.121 | 568 | 0.102 | 557 | 0.121 | 684 |
| Dallas-Fort Worth (North) | 0.134 | 452 | 0.154 | 617 | 0.134 | 517 | 0.154 | 676 |
| Houston (South) | 0.136 | 423 | 0.156 | 599 | 0.136 | 446 | 0.156 | 621 |
| McAllen (Valley) | 0.149 | 467 | 0.169 | 652 | 0.149 | 483 | 0.169 | 667 |
| El Paso (West) | 0.106 | 312 | 0.126 | 479 | 0.106 | 338 | 0.126 | 501 |

Table 155: Deemed Energy and Demand Savings for Dormitories per Room, by Region

| Representative City (Region) | Heat Pump |  |  |  | Electric Resistance Heat |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | HVAC-Only |  | HVAC and Lighting |  | HVAC-Only |  | HVAC and Lighting |  |
|  | kW | kWh | kW | kWh | kW | kWh | kW | kWh |
| 5-Degree Setup/Setback Offset |  |  |  |  |  |  |  |  |
| Amarillo (Panhandle) | 0.034 | 136 | 0.061 | 319 | 0.034 | 152 | 0.061 | 316 |
| Dallas (North) | 0.048 | 214 | 0.076 | 425 | 0.048 | 223 | 0.076 | 428 |
| Houston (South) | 0.051 | 242 | 0.078 | 461 | 0.051 | 244 | 0.078 | 462 |
| McAllen (Valley) | 0.053 | 265 | 0.081 | 492 | 0.053 | 266 | 0.081 | 492 |
| El Paso (West) | 0.031 | 110 | 0.059 | 327 | 0.031 | 110 | 0.059 | 326 |
| 10-Degree Setup/Setback Offset |  |  |  |  |  |  |  |  |
| Amarillo (Panhandle) | 0.073 | 261 | 0.084 | 404 | 0.073 | 289 | 0.084 | 417 |
| Dallas (North) | 0.078 | 293 | 0.105 | 505 | 0.078 | 304 | 0.105 | 511 |
| Houston (South) | 0.081 | 326 | 0.108 | 543 | 0.081 | 328 | 0.108 | 545 |
| McAllen (Valley) | 0.088 | 368 | 0.114 | 591 | 0.088 | 370 | 0.114 | 593 |
| El Paso (West) | 0.045 | 151 | 0.060 | 448 | 0.045 | 153 | 0.060 | 450 |

##### Claimed Peak Demand Savings

Refer to Volume 1, Section 4 for further details on peak demand savings and methodology.

##### Measure Life and Lifetime Savings

Estimated useful life (EUL) is 10 years based on the value for retrofit energy management system (EMS) HVAC control from the Massachusetts Joint Utility Measure Life Study. This value is also consistent with the EUL for lighting control and HVAC control measures in PUCT Docket Nos. 36779 and 40668.

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Climate zone

- HVAC system and equipment type

- Heating type (heat pump, electric resistance)

- Temperature offset category (5 or 10 degrees F)

- Control type (HVAC-only, HVAC and lighting)

- Building type (hotel, motel, dormitory)

- Number of rooms

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 40668—Provides deemed energy and demand savings values under “Guestroom, Dormitory and Multi-family Occupancy Controls for HVAC and Lighting Systems,” page 25 and Attachment pages A-46 through A-58.

- PUCT Docket 36779—Provides EULs for commercial measures.

##### Relevant Standards and Reference Sources

- ASHRAE Standard 90.1-1999

- Measure Life Study. Prepared for The Massachusetts Joint Utilities by ERS. November 17, 2005.

- Codes and Standards Enhancement Initiative (CASE): Guest Room Occupancy Controls, 2013 California Building Energy Efficiency Standards. October 2011.

### Pump-Off Controllers Measure Overview

TRM Measure ID: NR-MS-PC

Market Sector: Commercial

Measure Category: Controls

Applicable Building Types: Industrial

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Field study, engineering algorithms, and estimates

#### Measure Description

Pump-off controllers (POC) are micro-processor-based devices that continuously monitor pump down conditions (i.e., when the fluid in the well bore is insufficient to warrant continued pumping). These controllers are used to shut down the pump when the fluid falls below a certain level and “fluid pounding” occurs. POCs save energy by optimizing the pump run-times to match the flow conditions of the well.

##### Eligibility Criteria

The POC measure is only available as a retrofit measure for existing wells (wells with an existing API number prior to September 11th, 2014) with rod pumps using 15 hp or larger motors operating on time clock controls or less efficient devices. These cannot be integrated with a variable frequency drive and only apply to POCs using load cells, which measure the weight on the rod string for greater precision. Additionally, the POC must control a conventional well (above ground or vertical, with a standard induction motor of 480V or less).

##### Baseline Condition

The baseline condition is an existing conventional well (with an API number prior to September 11, 2014) with rod pumps operating on time clock controls or less efficient control devices.

##### High-Efficiency Condition

The efficient condition is the same well, retrofitted with a pump-off controller.

#### Energy and Demand Savings Methodology

Two main sources were referenced to develop the savings methods for the POC measure: Electrical Savings in Oil Production (SPE 16363), which identified a relationship between volumetric efficiency and pump run times and the 2006-2008 Evaluation Report for PG&E Fabrication, Process, and Manufacturing Contract Group, which showed a reduction in savings from the SPE 16363 paper. These two methods were the basis of the current savings calculations and deemed inputs listed below. To develop Texas-specific stipulated values, field and metering data will be collected when there is sufficient uptake in the measure and used to calibrate and update the savings calculation methods and input variables for a future version of the TRM.

##### Savings Algorithms and Inputs

The energy and demand algorithms and associated input variables are listed below:

Energy Savings kWh=kWavg*TimeClock%On-POC%On*8760

Equation 169

Demand Savings kW=EnergySavings8760

Equation 170

The inputs for the energy and peak coincident demand savings are listed below:

kWavg=HP×0.746×LFMESME

Equation 171

POC%On=RunConstant+RunCoefficient×VolumetricEfficiency%×TimeClock%On×100100

Equation 172

Where:

kWavg		=		The demand used by each rod pump

HP 		=		Rated pump motor horsepower

0.746		=		Conversion factor from hp to kW

LF 		=	 Motor load factor—ratio of average demand to maximum demand, see Table 156

ME		=	Motor efficiency, based on NEMA Standard Efficiency Motor, see Table 157

SME		=		Mechanical efficiency of sucker rod pump, see Table 156

TimeClock%On		=		Stipulated baseline timeclock setting, see Table 156

Runconstant, Runcoefficient	=		8.336, 0.956. Derived from SPE 16363

VolumetricEfficiency%	=	Average well gross production divided by theoretical production (provided on rebate application)

##### Deemed Energy and Demand Savings Tables

Table 156: Deemed Variables for Energy and Demand Savings Calculations

| Variable | Stipulated/ Deemed Values |
| --- | --- |
| LF (Load Factor) | 25% |
| ME (motor efficiency) | See Table 2-137 |
| SME (pump mechanical efficiency) | 95% |
| Timeclock%On | 65% |

Table 157: NEMA Premium Efficiency Motor Efficiencies

| Motor Horsepower | Nominal Full Load Efficiency |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Open Motors (ODP) |  |  | Enclosed Motors (TEFC) |  |  |
|  | 6 poles | 4 poles | 2 poles | 6 poles | 4 poles | 2 poles |
|  | 1200 rpm | 1800 rpm | 3600 rpm | 1200 rpm | 1800 rpm | 3600 rpm |
| 15 | 91.7% | 93.0% | 90.2% | 91.7% | 92.4% | 91.0% |
| 20 | 92.4% | 93.0% | 91.0% | 91.7% | 93.0% | 91.0% |
| 25 | 93.0% | 93.6% | 91.7% | 93.0% | 93.6% | 91.7% |
| 30 | 93.6% | 94.1% | 91.7% | 93.0% | 93.6% | 91.7% |
| 40 | 94.1% | 94.1% | 92.4% | 94.1% | 94.1% | 92.4% |
| 50 | 94.1% | 94.5% | 93.0% | 94.1% | 94.5% | 93.0% |
| 60 | 94.5% | 95.0% | 93.6% | 94.5% | 95.0% | 93.6% |
| 75 | 94.5% | 95.0% | 93.6% | 94.5% | 95.4% | 93.6% |
| 100 | 95.0% | 95.4% | 93.6% | 95.0% | 95.4% | 94.1% |
| 125 | 95.0% | 95.4% | 94.1% | 95.0% | 95.4% | 95.0% |
| 150 | 95.4% | 95.8% | 94.1% | 95.8% | 95.8% | 95.0% |
| 200 | 95.4% | 95.8% | 95.0% | 95.8% | 96.2% | 95.4% |

##### Claimed Peak Demand Savings

Because the operation of the POC coincident with the peak demand period is uncertain, a simple average of the total savings over the full year (8760 hours) is used, as shown in Equation 170.

##### Measure Life and Lifetime Savings

The EUL for this measure is 15 years.

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Motor manufacturer

- Motor model number

- Rated motor horsepower

- Motor type (TEFC or ODP)

- Rated motor RPM

- Baseline control type and timeclock percent on time (or actual on-time schedule)

- Volumetric efficiency

- Field data on actual energy use and post-run times

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 42551—Provides energy and demand savings calculations and EUL

##### Relevant Standards and Reference Sources

- Bullock, J.E. “SPE 16363 Electrical Savings in Oil Production”, (paper presented at the Society of Petroleum Engineers California Regional Meeting held in Ventura, California, April 8-10, 1987).

- 79 FR 30933. Full-load Efficiencies for General Purpose Electric Motors [Subtype I]

- 2006-2008 Evaluation Report for PG&E Fabrication, Process and Manufacturing Contract Group. CALMAC Study ID: CPU0017.01. Itron, Inc. Submitted to California Public Utilities Commission. February 3, 2010.

- Comprehensive Process and Impact Evaluation of the (Xcel Energy) Colorado Motor and Drive Efficiency Program, FINAL. Tetra Tech. March 28, 2011.

### ENERGY STAR® Pool Pumps Measure Overview

TRM Measure ID: NR-MS-PP

Market Sector: Commercial

Measure Category: Appliances

Applicable Building Types: Commercial

Fuels Affected: Electricity

Decision/Action Type(s): Retrofit, new construction

Program Delivery Type(s): Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This measure involves the replacement of a single-speed pool pump with an ENERGY STAR® certified variable speed pool pump.

##### Eligibility Criteria

This measure applies to all commercial applications, indoor or outdoor, with a pump size up to 3 hp; larger sizes should be implemented through a custom program. Motor-only retrofits are not eligible. Ineligible pump products include waterfall, integral cartridge filter, integral sand filter, storable electric spa, and rigid electric spa.

Multi-speed pool pumps are not permitted. The multi-speed pump uses an induction motor that functions as two motors in one, with full-speed and half-speed options. Multi-speed pumps may enable significant energy savings. However, if the half-speed motor is unable to complete the required water circulation task, the larger motor will operate exclusively. Having only two speed-choices limits the ability of the pump motor to fine-tune the flow rates required for maximum energy savings. The default pump curves provided in the ENERGY STAR® Pool Pump Savings Calculator indicate that the motor operating at half-speed will be unable to meet the minimum turnover requirements for commercial pool operation as mandated by Texas Administrative Code.

##### Baseline Condition

The baseline condition is a 1 to 3 horsepower (hp) standard efficiency single-speed pool pump.

##### High-efficiency Condition

The high-efficiency condition is a 1 to 3 hp ENERGY STAR® certified variable speed pool pump.

#### Energy and Demand Savings Methodology

Savings for this measure are based on methods and input assumptions from the ENERGY STAR® Pool Pump Savings Calculator.

##### Savings Algorithms and Input Variables

Energy Savings Algorithms

Energy savings for this measure were derived using the ENERGY STAR® Pool Pump Savings Calculator with Texas selected as the applicable location, so Texas-specific assumptions were used.

kWhSavings=kWhconv-kWhES

Equation 173

Where:

kWhconv	= 	Conventional single-speed pool pump energy (kWh)

kWhES	= 	ENERGY STAR® variable speed pool pump energy (kWh)

Algorithms to calculate the above parameters are defined as:

kWhconv=PFRconv×60×hoursconv×daysEFconv×1000

Equation 174

kWhES=kWhHS+kWhLSgal×turnday×daysEFES×1000

Equation 175

kWhHS=PFRHS×60×hoursHS×daysEFHS×1000

kWhLS=PFRLS×60×hoursLS×daysEFLS×1000

Where:

hours	=	Pump daily operating hours (Table 158)

days	=	Operating days per year = Year-Round Operation: 365 days; Seasonal Operation: 7 months x 30.4 days/month = 212.8 days (default)

PFRconv	=	Conventional single-speed pump flow rate [gal/min] (Table 158)

EFconv	=	Conventional single-speed pump energy factor [gal/W·hr] (Table 158)

gal	=	The volume of the pool in gallons, (Table 159).

turnday	=	Turnovers per day, number of times the volume of the pool is run through the pump per day, (Table 159).

EFES	=	ENERGY STAR® weighted energy factor [gal/W·hr] (Table 159)

60	=	Constant to convert between minutes and hours

1,000	=	Constant to convert from kilowatts to watts

Table 158: Conventional Pool Pumps Assumptions

| New Rated Pump HP | hours, limited hours | hours, 24/7 Operation | PFRconv (gal/min) | EFconv (gal/W·h) |
| --- | --- | --- | --- | --- |
| ≤ 1.25 | 12 | 24 | 75.5000 | 2.5131 |
| 1.25 < hp ≤ 1.75 |  |  | 78.1429 | 2.2677 |
| 1.75 < hp ≤ 2.25 |  |  | 88.6667 | 2.2990 |
| 2.25 < hp ≤ 2.75 |  |  | 93.0910 | 2.1812 |
| 2.75 < hp ≤ 3 |  |  | 101.6667 | 1.9987 |

Table 159: ENERGY STAR® Pool Pumps Assumptions

| New Rated Pump HP | Turnovers/day limited hours | Turnovers/day 24/7 Operation | Gallons |  |  | EFES (gal/W·h) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ≤ 1.25 | 5.4 | 5.4 | 20,000 |  |  | 8.7 |  |  |
| 1.25 < hp ≤ 1.75 | 5.6 | 5.6 | 20,000 |  |  | 8.9 |  |  |
| 1.75 < hp ≤ 2.25 | 5.8 | 5.8 | 22,000 |  |  | 9.3 |  |  |
| 2.25 < hp ≤ 2.75 | 5.4 | 5.4 | 25,000 |  |  | 7.4 |  |  |
| 2.75 < hp ≤ 3 | 5.2 | 5.2 | 28,000 |  |  | 7.1 |  |  |

Demand Savings Algorithms

kWSavings=kWhconvhoursconv-kWhHS+kWhLShoursHS+hoursLSkWhconv-kWhEShours×DFdays

Equation 176

Where:

hours	=	Pump daily operating hours (Table 158)

days	=	Operating days per year = Year-Round Operation: 365 days; Seasonal Operation: 7 months x 30.4 days/month = 212.8 days (default)

DF	=	Demand Factor from Table 160

Table 160: Demand Factors

| Operation | Summer DF | Winter DF |
| --- | --- | --- |
| 24/7 Operation | 1.0 | 1.0 |
| Seasonal/Limited Hours | 1.0 | 0.5 |

##### Deemed Energy Savings Tables

Table 161: ENERGY STAR® Variable Speed Pool Pump Energy Savings

| New Rated Pump HP | Year-Round Operation |  | Seasonal Operation (7 months) |
| --- | --- | --- | --- |
|  | 24/7 Operation | Limited Hours |  |
|  | kWh Savings | kWh Savings | kWh Savings |
| ≤ 1.25 | 11,259 | 5,630 | 3,282 |
| 1.25 < hp ≤ 1.75 | 13,518 | 6,759 | 3,941 |
| 1.75 < hp ≤ 2.25 | 15,263 | 7,632 | 4,449 |
| 2.25 < hp ≤ 2.75 | 15,773 | 7,887 | 4,598 |
| 2.75 < hp ≤ 3 | 19,250 | 9,625 | 5,612 |

##### Deemed Summer Demand Savings Tables

Table 162: ENERGY STAR® Variable Speed Pool Pump Summer Demand Savings

| New Rated Pump (HP) | Year-Round Operation. 24/7 or Limited Hours Demand Savings (kW) | Seasonal Operation Demand Savings (kW) |
| --- | --- | --- |
| ≤ 1.25 | 1.285 | 0.749 |
| 1.25 < hp ≤ 1.75 | 1.543 | 0.900 |
| 1.75 < hp ≤ 2.25 | 1.742 | 1.016 |
| 2.25 < hp ≤ 2.75 | 1.801 | 1.050 |
| 2.75 < hp ≤ 3 | 2.198 | 1.281 |

##### Deemed Winter Demand Savings Tables

Table 163: ENERGY STAR® Variable Speed Pool Pump Winter Demand Savings

| New Rated Pump HP | Year-Round Operation. 24/7 Demand Savings (kW) | Year-Round Limited Hours Demand Savings (kW) | Seasonal Operation Demand Savings (kW) |
| --- | --- | --- | --- |
| ≤ 1.25 | 1.285 | 0.643 | 0.375 |
| 1.25 < hp ≤ 1.75 | 1.543 | 0.772 | 0.450 |
| 1.75 < hp ≤ 2.25 | 1.742 | 0.871 | 0.508 |
| 2.25 < hp ≤ 2.75 | 1.801 | 0.900 | 0.525 |
| 2.75 < hp ≤ 3 | 2.198 | 1.099 | 0.641 |

##### Claimed Peak Demand Savings

Table 164: ENERGY STAR® Variable Speed Pool Pump Claimed Demand Savings

| New Rated Pump (HP) | Year-Round Operation. 24/7 or Limited Hours Demand Savings (kW) | Seasonal Operation Demand Savings (kW) |
| --- | --- | --- |
| ≤ 1.25 | 1.285 | 0.749 |
| 1.25 < hp ≤ 1.75 | 1.543 | 0.900 |
| 1.75 < hp ≤ 2.25 | 1.742 | 1.016 |
| 2.25 < hp ≤ 2.75 | 1.801 | 1.050 |
| 2.75 < hp ≤ 3 | 2.198 | 1.281 |

##### Additional Calculators and Tools

ENERGY STAR® Pool Pump Savings Calculator, updated May 2020, can be found on the ENERGY STAR® website at https://www.energystar.gov/productfinder/downloads/Pool_Pump_Calculator_2020.05.05_FINAL.xlsx.

##### Measure Life and Lifetime Savings

According to DEER 2014, the estimated useful life for this measure is 10 years.

#### Program Tracking Data and Evaluation Requirements

Primary inputs and contextual data that should be specified and tracked by the program database to inform the evaluation and apply the savings properly are:

- For all projects

  - Pool pump rated horsepower

  - Climate zone

  - Proof of purchase including quantity, make, and model information

  - Copy of ENERGY STAR® certification

  - Facility operation type: 24/7, year-round limited hours, seasonal.

- For a significant sample of projects where attainable (e.g., those projects that are selected for inspection, not midstream or retail programs)

  - Items listed above for all projects

  - Decision/action type: early retirement, replace-on-burnout, or new construction

  - Rated horsepower of existing pool pump

  - Existing and new pump operating hours

#### References and Efficiency Standards

##### Petitions and Rulings

- PUCT Docket 47612—Provides deemed savings for ENERGY STAR® pool pumps

##### Relevant Standards and Reference Sources

- The applicable version of the ENERGY STAR® specifications and requirements for pool pumps

### Computer Power Management Measure Overview

TRM Measure ID: NR-MS-CP

Market Sector: Commercial

Measure Category: Miscellaneous

Applicable Building Types: All building types applicable

Fuels Affected: Electricity

Decision/Action Type: Retrofit

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed value (per machine)

Savings Methodology: Algorithms

#### Measure Description

This measure presents deemed savings for implementation of computer power management strategies. Computer power management includes the use of operational settings that automate the power management features of computer equipment, including automatically placing equipment into a low power mode during periods of inactivity. This may be done either with built-in features integral to the computer operating system or through an add-on software program. Typically, this measure is implemented across an entire network of computers.

##### Eligibility Criteria

To be eligible for this measure, computers must not have any automatic sleep or other low power setting in place. Both conventional and ENERGY STAR® computer equipment are eligible for this measure. Applicable building types include offices and schools.

##### Baseline Condition

The baseline conditions are the estimated number of hours that the computer spends in active, sleep, and off modes before the power settings are actively managed. Operating hours may be estimated from metering, or the default hours provided in the calculation of deemed savings may be used. The default baseline hours are taken from the ENERGY STAR® modeling study assumptions contained in the Low Carbon IT Savings Calculator, and assume baseline computer settings never enter sleep mode, and 60% of computers are turned off each night.

##### High-Efficiency Condition

The efficient conditions are the estimated number of hours that the computer spends in active, sleep, and off modes after the power settings are actively managed. Operating hours may be estimated from metering, or the default hours provided in the calculation of deemed savings may be used. The default efficient hours are taken from the ENERGY STAR® modeling study assumptions contained in the Low Carbon IT Savings Calculator and assume managed computer settings enter sleep mode after 15 minutes of inactivity, and 80% of computers are turned off each night.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

kWhsavings=Wactivehrsactivepre- hrsactivepost +Wsleephrssleeppre- hrssleeppost +Woffhrsoffpre- hrsoffpost 1,000

Equation 177

kWsavings=kWhsavings×PWPLS

Equation 178

Where:

Wactive 	=	total wattage of the equipment, including computer and monitor, in active/idle mode; see Table 165

hrsactivepre 	=	annual number of hours the computer is in active/idle mode before computer management software is installed; see Table 166

hrsactivepost	=	annual number of hours the computer is in active/idle mode after computer management software is installed; see Table 166

Wsleep	=	total wattage of the equipment, including computer and monitor, in sleep mode; see Table 165

hrssleeppre	=	annual number of hours the computer is in sleep mode before computer management software is installed; see Table 166

hrssleeppost	=	annual number of hours the computer is in sleep mode after computer management software is installed; see Table 166

Woff	=	total wattage of the equipment, including computer and monitor, in off mode; see Table 165

hrsoffpre	=	annual number of hours the computer is in off mode before computer management software is installed; see Table 166

hrsoffpost	=	annual number of hours the computer is in off mode after computer management software is installed; see Table 166

1,000 	=	Conversion factor: 1 kW / 1,000 W

PWPLS 	=	Probability weighted peak load share; see Table 167

Table 165: Computer Power Management - Equipment Wattages

| Equipment | Wactive | Wsleep | Woff |
| --- | --- | --- | --- |
| Conventional Monitor | 18.3 | 0.30 | 0.30 |
| Conventional Computer | 48.11 | 2.31 | 0.96 |
| Conventional Notebook (including display) | 14.82 | 1.21 | 0.61 |
| ENERGY STAR Monitor | 15.0 | 0.26 | 0.26 |
| ENERGY STAR Computer | 27.11 | 1.80 | 0.81 |
| ENERGY STAR Notebook (including display) | 8.61 | 0.89 | 0.46 |

Table 166: Computer Power Management – Operating Hours

| Building Activity Type | hrsactivepre | hrsactivepost | hrssleeppre | hrssleeppost | hrsoffpre | hrsoffpost |
| --- | --- | --- | --- | --- | --- | --- |
| Typical office (8 hours/day, 5 days/week, 22 non-work days/year) | 4,650 | 1,175 | 0 | 2,105 | 4,110 | 5,480 |
| Typical school (8 hours/day, 5 days/week, 113 non-school days/year) | 4,213 | 727 | 0 | 1,970 | 4,547 | 6,063 |

Table 167: Computer Power Management – Probability Weighted Peak Load Share, All Activity Types

| Climate Zone | Summer PWPLS | Winter PWPLS |
| --- | --- | --- |
| 1 | 0.108 | 0.018 |
| 2 | 0.104 | 0.020 |
| 3 | 0.110 | 0.020 |
| 4 | 0.103 | 0.023 |
| 5 | 0.125 | 0.047 |

##### Deemed Energy and Demand Savings Tables

Energy and demand savings are deemed values for conventional and ENERGY STAR® equipment, based on the input assumptions listed in Table 165, Table 166, and Table 167. The following tables provide these deemed values.

Table 168: Computer Power Management - Deemed Energy Savings Values, All Climate Zones

| Equipment | Office or School kWh |
| --- | --- |
| Conventional LCD Monitor | 62.6 |
| Conventional Computer | 161.4 |
| Conventional Notebook | 48.2 |
| ENERGY STAR® Monitor | 51.3 |
| ENERGY STAR® Computer | 89.5 |
| ENERGY STAR® Notebook | 27.5 |

Table 169: Computer Power Management - Deemed Demand Savings Values, Office or School

| Equipment | Zone 1 |  | Zone 2 |  | Zone 3 |  | Zone 4 |  | Zone 5 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Summer kW | Winter kW | Summer kW | Winter kW | Summer kW | Winter’ kW | Summer kW | Winter kW | Summer kW | Winter kW |
| Conventional LCD Monitor | 0.007 | 0.001 | 0.006 | 0.001 | 0.007 | 0.001 | 0.006 | 0.001 | 0.008 | 0.003 |
| Conventional Computer | 0.017 | 0.003 | 0.017 | 0.003 | 0.018 | 0.003 | 0.017 | 0.004 | 0.020 | 0.008 |
| Conventional Notebook | 0.005 | 0.001 | 0.005 | 0.001 | 0.005 | 0.001 | 0.005 | 0.001 | 0.006 | 0.002 |
| ENERGY STAR® Monitor | 0.006 | 0.001 | 0.005 | 0.001 | 0.006 | 0.001 | 0.005 | 0.001 | 0.006 | 0.002 |
| ENERGY STAR® Computer | 0.010 | 0.002 | 0.009 | 0.002 | 0.010 | 0.002 | 0.009 | 0.002 | 0.011 | 0.004 |
| ENERGY STAR® Notebook | 0.003 | 0.000 | 0.003 | 0.001 | 0.003 | 0.001 | 0.003 | 0.001 | 0.003 | 0.001 |

##### Measure Life and Lifetime Savings

The EUL of this measure is based on the useful life of the computer equipment which is being controlled, 3 years.

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Type of equipment

  - Conventional or ENERGY STAR®

  - Monitor, computer, or notebook

#### References and Efficiency Standards

##### Petitions and Rulings

This section is not applicable

##### Relevant Standards and Reference Sources

This section is not applicable

### Premium Efficiency Motors Measure Overview

TRM Measure ID: NR-MS-PM

Market Sector: Commercial

Measure Category: Miscellaneous

Applicable Building Types: Commercial

Fuels Affected: Electricity

Decision/Action Type: Replace-on-burnout, early retirement, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

Currently a wide variety of NEMA premium efficiency motors from 1 to 500 horsepower (hp) are available. Deemed saving values for demand and energy savings associated with this measure must be for electric motors with an equivalent operating period (hours x load factor) over 1,000 hours.

##### Eligibility Criteria

To qualify for early retirement, the premium efficiency unit must replace an existing, full-size unit with a maximum age of 16 years. To determine the remaining useful life of an existing unit, see Table 174. To receive early retirement savings, the unit to be replaced must be functioning at the time of removal.

##### Baseline and High-efficiency Conditions

###### New Construction or Replace-on-Burnout

EISA 2007 Sec 313 adopted new federal standards for motors manufactured in the United States from December 19, 2010 to before June 1, 2016, with increased efficiency requirements for 250-500 hp motors as of June 1, 2016. These standards replace legislation commonly referred to as EPAct 1992 (the Federal Energy Policy Act of 1992). The standards can also be found in section 431.25 of the Code of Federal Regulations (10 CFR Part 431).

With these changes, motors ranging from one to 500 hp bearing the “NEMA Premium" trademark will align with national energy efficiency standards and legislation. The Federal Energy Management Program (FEMP) adopted NEMA MG 1-2006 Revision 1 2007 in its Designated Product List for federal customers.

Additionally, NEMA premium standards include general purpose electric motors, subtype II (i.e., motors ranging from 1-200 hp and 200-500 hp) including:

- U-frame motors

- Design C motors

- Close-coupled pump motors

- Footless motors

- Vertical solid shaft normal thrust (tested in a horizontal configuration)

- 8-pole motors

- All poly-phase motors up to 600 volts (minus 230/460 volts, covered EPAct-92)

Under these legislative changes, 200-500 hp and subtype II motor baselines will be based on the minimum efficiency allowed under the Federal Energy Policy Act of 1992 (EPAct) (see Table 173) and are thus no longer equivalent to pre-1992/pre-EPAct defaults.

###### Early Retirement

The baseline for early retirement projects is the nameplate efficiency of the existing motor to be replaced, if known. If the nameplate is illegible and the in-situ efficiency cannot be determined, then the baseline should be based on the minimum efficiency allowed under the Federal Energy Policy Act of 1992 (EPAct), as listed in

Table 175.

NEMA premium efficiency motor levels continue to be industry standard for minimum-efficiency levels. The savings calculations assume that the minimum motor efficiency for replacement motors for both replace-on-burnout and early retirement projects exceeds that listed in Table 173.

For early retirement, the maximum age of eligible equipment is capped at the expected 75 percent of the equipment failure (17 years). ROB savings should be applied when age of the unit exceeds 75 percent failure age. This cap prevents early retirement savings from being applied to projects where the age of the equipment greatly exceeds the estimated useful life of the measure. 1-200 hp motors manufactured as of December 19, 2010 and 250-500 hp motors manufactured as of June 1, 2016 are not eligible for early retirement.

Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

Actual motor operating hours are expected to be used to calculate savings. Short and/or long-term metering can be used to verify estimates. If metering is not possible, interviews with facility operators and review of operations logs should be conducted to obtain an estimate of actual operating hours. If there is not sufficient information to accurately estimate operating hours, then the annual operating hours in Table 170 or Table 171 can be used.

###### New Construction or Replace-on-Burnout

Energy Savings Algorithms

kWhsavings, ROB=hp×0.746 ×LF × 1ηbaseline, ROB-1ηpost× Hrs

Equation 179

Demand Savings Algorithms

HVAC Applications:

kWsavings,ROB=kWhsavings,ROBHrs× CF

Equation 180

Industrial Applications:

kWsavings,ROB=kWhsavings,ROB8,760 hours

Equation 181

Where:

hp	=	Nameplate horsepower data of the motor

0.746 	=	hp-to-kWh conversion Factor (kW/hp)

LF 	=	Estimated load factor (if unknown, see Table 170 or Table 171)

ηbaseline,ROB	=	Assumed original motor efficiency (Table 173)

ηpost	=	Efficiency of the newly installed motor

Hrs	=	Estimated annual operating hours (if unknown, see Table 170 or Table 171)

CF	=	Coincidence Factor (see Table 170)

kWhsavings, ROB 	= 	Total energy savings for a new construction or ROB project

kWsavings, ROBER 	=	Total demand savings for a new construction or ROB project

Table 170: Premium Efficiency Motors – HVAC Assumptions by Building Type

| Building Type | Load Factor | CF | HVAC Fan Hours |
| --- | --- | --- | --- |
| Hospital | 0.75 | 1.00 | 8,760 |
| Large Office (>30k SqFt) |  |  | 4,424 |
| Small Office (≤30k SqFt) |  |  | 4,006 |
| K-12 School |  |  | 4,173 |
| College |  |  | 4,590 |
| Retail |  |  | 5,548 |
| Restaurant (Fast Food) |  |  | 6,716 |
| Restaurant (Sit-Down) |  |  | 5,256 |

Table 171: Premium Efficiency Motors – Industrial Assumptions by Building Type

| Industrial Processing | Load Factor | Hours |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Chem | Paper | Metals | Petroleum Refinery | Food Production | Other |
| 1-5 hp | 0.54 | 4,082 | 3,997 | 4,377 | 1,582 | 3,829 | 2,283 |
| 6-20 hp | 0.51 | 4,910 | 4,634 | 4,140 | 1,944 | 3,949 | 3,043 |
| 21-50 hp | 0.60 | 4,873 | 5,481 | 4,854 | 3,025 | 4,927 | 3,530 |
| 51-100 hp | 0.54 | 5,853 | 6,741 | 6,698 | 3,763 | 5,524 | 4,732 |
| 101-200 hp | 0.75 | 5,868 | 6,669 | 7,362 | 4,170 | 5,055 | 4,174 |
| 201-500 hp | 0.58 | 5,474 | 6,975 | 7,114 | 5,311 | 3,711 | 5,396 |
| 501-1,000 hp |  | 7,495 | 7,255 | 7,750 | 5,934 | 5,260 | 8,157 |
| > 1,000 hp |  | 7,693 | 8,294 | 7,198 | 6,859 | 6,240 | 2,601 |

Table 172: Rewound Motor Efficiency Reduction Factors

| Motor Horsepower | Efficiency Reduction Factor |
| --- | --- |
| < 40 | 0.010 |
| ≥ 40 | 0.005 |

Table 173: Premium Efficiency Motors – New Construction and Replace-on-Burnout Baseline Efficiencies by Motor Size409,

| hp | Open Motors: ηbaseline, ROB |  |  | Closed Motors: ηbaseline, ROB |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 6-Pole | 4-Pole | 2-Pole | 6-Pole | 4-Pole | 2-Pole |
| 1 | 82.5 | 85.5 | 77.0 | 82.5 | 85.5 | 77.0 |
| 1.5 | 86.5 | 86.5 | 84.0 | 87.5 | 86.5 | 84.0 |
| 2 | 87.5 | 86.5 | 85.5 | 88.5 | 86.5 | 85.5 |
| 3 | 88.5 | 89.5 | 85.5 | 89.5 | 89.5 | 86.5 |
| 5 | 89.5 | 89.5 | 86.5 | 89.5 | 89.5 | 88.5 |
| 7.5 | 90.2 | 91.0 | 88.5 | 91.0 | 91.7 | 89.5 |
| 10 | 91.7 | 91.7 | 89.5 | 91.0 | 91.7 | 90.2 |
| 15 | 91.7 | 93.0 | 90.2 | 91.7 | 92.4 | 91.0 |
| 20 | 92.4 | 93.0 | 91.0 | 91.7 | 93.0 | 91.0 |
| 25 | 93.0 | 93.6 | 91.7 | 93.0 | 93.6 | 91.7 |
| 30 | 93.6 | 94.1 | 91.7 | 93.0 | 93.6 | 91.7 |
| 40 | 94.1 | 94.1 | 92.4 | 94.1 | 94.1 | 92.4 |
| 50 | 94.1 | 94.5 | 93.0 | 94.1 | 94.5 | 93.0 |
| 60 | 94.5 | 95.0 | 93.6 | 94.5 | 95.0 | 93.6 |
| 75 | 94.5 | 95.0 | 93.6 | 94.5 | 95.4 | 93.6 |
| 100 | 95.0 | 95.4 | 93.6 | 95.0 | 95.4 | 94.1 |
| 125 | 95.0 | 95.4 | 94.1 | 95.0 | 95.4 | 95.0 |
| 150 | 95.4 | 95.8 | 94.1 | 95.8 | 95.8 | 95.0 |
| 200 | 95.4 | 95.8 | 95.0 | 95.8 | 96.2 | 95.4 |
| 250 | 95.8 | 95.8 | 95.0 | 95.8 | 96.2 | 95.8 |
| 300 | 95.8 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 350 | 95.8 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 400 | n/a | 95.8 | 95.8 | n/a | 96.2 | 95.8 |
| 450 | n/a | 96.2 | 96.2 | n/a | 96.2 | 95.8 |
| 500 | n/a | 96.2 | 96.2 | n/a | 96.2 | 95.8 |

###### Early Retirement

Annual energy (kWh) and peak demand (kW) savings must be calculated separately for two time periods:

- The estimated remaining life of the equipment that is being removed, designated the remaining useful life (RUL), and

- The remaining time in the EUL period (EUL - RUL)

Annual energy and peak demand savings are calculated by weighting the early retirement and replace-on-burnout savings by the RUL of the unit and the remainder of the EUL period, as outlined in the Volume 3 appendices.

Where:

RUL	= 	Remaining useful life (see Table 174); if unknown, assume the age of the replaced unit is equal to the EUL resulting in a default RUL of 2.0 years.

EUL	= 	Estimated useful life = 15 years

Table 174: Remaining Useful Life (RUL) of Replaced Motor

| Age of Replaced Motor (years) | RUL (years) | Age of Replaced Motor (years) | RUL (years) |
| --- | --- | --- | --- |
| 1 | 13.9 | 10 | 5.0 |
| 2 | 12.9 | 11 | 4.2 |
| 3 | 11.9 | 12 | 3.6 |
| 4 | 10.9 | 13 | 3.0 |
| 5 | 9.9 | 14 | 2.5 |
| 6 | 8.9 | 15 | 2.0 |
| 7 | 7.9 | 16 | 1.0 |
| 8 | 6.9 | 17 | 0.0 |
| 9 | 5.9 |

Derivation of RULs

Premium Efficiency Motors have an estimated useful life of 15 years. This estimate is consistent with the age at which approximately 50 percent of the motors installed in a given year will no longer be in service, as described by the survival function for a general fan or air compressor application in Figure 5.

Figure 5: Survival Function for Premium Efficiency Motors

The method to estimate the remaining useful life (RUL) of a replaced system uses the age of the existing system to re-estimate the projected unit lifetime based on the survival function shown in Figure 5. The age of the motor being replaced is found on the horizontal axis, and the corresponding percentage of surviving motors is determined from the chart. The surviving percentage value is then divided in half, creating a new estimated useful lifetime applicable to the current unit age. Then, the age (year) that corresponds to this new percentage is read from the chart. RUL is estimated as the difference between that age and the current age of the system being replaced.

For example, assume a motor being replaced is 15 years old (the estimated useful life). The corresponding percent surviving value is approximately 50 percent. Half of 50 percent is 25 percent. The age corresponding to 25 percent on the chart is approximately 17 years. Therefore, the RUL of the motor being replaced is (17 – 15) = 2 years.

Energy Savings Algorithms

For the RUL time period:

kWhsavings,RUL=hp×0.746×LF × 1ηbaseline,ER-1ηpost× Hrs

Equation 182

For the remaining time in the EUL period, calculate annual savings as you would for a replace-on-burnout project.

kWhsavings, EUL=hp×0.746 ×LF × 1ηbaseline, ROB-1ηpost× Hrs

Equation 183

It follows that total lifetime energy savings for early retirement projects are then determined by adding the savings calculated under the two preceding equations:

kWh savings,ER= kWhsavings,RUL ×RUL+ kWhsavings, EUL ×(EUL-RUL)

Equation 184

Demand Savings Algorithms

To calculate demand savings for the early retirement of a motor, a similar methodology is used as for replace-on-burnout installations, with separate savings calculated for the remaining useful life of the unit, and the remainder of the EUL as outlined in the section above.

For the RUL time period:

HVAC Applications:

kWsavings,RUL=kWhsavings,RULHrs ×CF

Equation 185

Industrial Applications:

kWsavings,RUL=kWhsavings,RUL8,760 hours

Equation 186

For the remaining time in the EUL period, calculate annual savings as you would for a replace-on-burnout project:

HVAC Applications:

kWsavings,EUL=kWhsavings,EULHrs ×CF

Equation 187

Industrial Applications:

kWsavings,EUL=kWhsavings,EUL8,760 hours

Equation 188

Annual deemed peak demand savings are calculated by weighting the early retirement and replace-on-burnout savings by the RUL of the unit and the remainder of the EUL period, as outlined in the Volume 3 appendices.

kW savings,ER= kWsavings,RUL ×RUL+ kWsavings, EUL ×(EUL-RUL)

Equation 189

Where:

ηbaseline,ER	 =	Assumed original motor efficiency for remaining EUL time period (

Table 175 or Table 176)

kWhsavings, RUL =	Energy savings for RUL time period in an ER project

kWhsavings, EUL =	Energy savings for remaining EUL time period in an ER project

kWsavings, RUL	 =	Demand savings for RUL time period in an ER project

kWsavings, EUL	 =	Demand savings for remaining EUL time period in an ER project

kWhsavings, ER	 =	Total energy savings for an ER project

kWsavings, ER	 =	Total demand savings for an ER project

Table 175: Premium Efficiency Motors – Early Retirement Baseline Efficiencies by Motor Size for 1-200 hp Motors Manufactured Prior to December 19, 2010

| hp | Open Motors: ηbaseline, ER |  |  | Closed Motors: ηbaseline, ER |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 6-Pole | 4-Pole | 2-Pole | 6-Pole | 4-Pole | 2-Pole |
| 1 | 80.0 | 82.5 | 75.5 | 80.0 | 82.5 | 75.5 |
| 1.5 | 84.0 | 84.0 | 82.5 | 85.5 | 84.0 | 82.5 |
| 2 | 85.5 | 84.0 | 84.0 | 86.5 | 84.0 | 84.0 |
| 3 | 86.5 | 86.5 | 84.0 | 87.5 | 87.5 | 85.5 |
| 5 | 87.5 | 87.5 | 85.5 | 87.5 | 87.5 | 87.5 |
| 7.5 | 88.5 | 88.5 | 87.5 | 89.5 | 89.5 | 88.5 |
| 10 | 90.2 | 89.5 | 88.5 | 89.5 | 89.5 | 89.5 |
| 15 | 90.2 | 91.0 | 89.5 | 90.2 | 91.0 | 90.2 |
| 20 | 91.0 | 91.0 | 90.2 | 90.2 | 91.0 | 90.2 |
| 25 | 91.7 | 91.7 | 91.0 | 91.7 | 92.4 | 91.0 |
| 30 | 92.4 | 92.4 | 91.0 | 91.7 | 92.4 | 91.0 |
| 40 | 93.0 | 93.0 | 91.7 | 93.0 | 93.0 | 91.7 |
| 50 | 93.0 | 93.0 | 92.4 | 93.0 | 93.0 | 92.4 |
| 60 | 93.6 | 93.6 | 93.0 | 93.6 | 93.6 | 93.0 |
| 75 | 93.6 | 94.1 | 93.0 | 93.6 | 94.1 | 93.0 |
| 100 | 94.1 | 94.1 | 93.0 | 94.1 | 94.5 | 93.6 |
| 125 | 94.1 | 94.5 | 93.6 | 94.1 | 94.5 | 94.5 |
| 150 | 94.5 | 95.0 | 93.6 | 95.0 | 95.0 | 94.5 |
| 200 | 94.5 | 95.0 | 94.5 | 95.0 | 95.0 | 95.0 |

Table 176: Premium Efficiency Motors – Early Retirement Baseline Efficiencies by Motor Size for 250-500 hp Motors Manufactured Prior to June 1, 2016

| hp | Open Motors: ηbaseline, ER |  |  | Closed Motors: ηbaseline, ER |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 6-Pole | 4-Pole | 2-Pole | 6-Pole | 4-Pole | 2-Pole |
| 250 | 95.4 | 95.4 | 94.5 | 95.0 | 95.0 | 95.4 |
| 300 | 95.4 | 95.4 | 95.0 | 95.0 | 95.4 | 95.4 |
| 350 | 95.4 | 95.4 | 95.0 | 95.0 | 95.4 | 95.4 |
| 400 | n/a | 95.4 | 95.4 | n/a | 95.4 | 95.4 |
| 450 | n/a | 95.8 | 95.8 | n/a | 95.4 | 95.4 |
| 500 | n/a | 95.8 | 95.8 | n/a | 95.8 | 95.4 |

##### Deemed Energy and Demand Savings Tables

##### This section is not applicable

##### Measure Life and Lifetime Savings

The median estimated useful life (EUL) for premium efficiency motors is 15 years.

#### Program Tracking Data and Evaluation Requirements

Primary inputs and contextual data that should be specified and tracked by the program database to inform the evaluation and apply the savings properly are:

- Number of units installed

- The project type of the installation (new construction, replace-on-burnout, or early retirement)

- Horsepower

- Estimated annual operating hours and estimated load factor

- Number of poles in and horsepower of original motor

- Newly installed motor efficiency

- Description of motor service

- Photograph demonstrating functionality of existing equipment and/or customer responses to survey questionnaire documenting the condition of the replaced unit and their motivation for measure replacement for early retirement eligibility determination (early retirement only)

#### References and Efficiency Standards

##### Petitions and Rulings

This section is not applicable

##### Relevant Standards and Reference Sources

- Federal Energy Policy Act of 1992 (EPAct)

  - Defaults prior to EPAct 1992 from the DOE’s MotorMaster+ database (circa 1992)

- 2007 Energy Independence and Security Act (EISA)

- The applicable version of the Technical Support Document for electric motors

### Central Domestic Hot Water (DHW) Controls Measure Overview

TRM Measure ID: NR-MS-DC

Market Sector: Commercial

Measure Category: Miscellaneous

Applicable Building Types: Multifamily, lodging, nursing homes, dormitories, prisons, offices, and education

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

##### Central domestic hot water (DHW) systems with recirculation pumps distribute hot water continuously throughout the building to the end-users. DHW pump controls save energy by reducing the operating hours of the circulation pumps and reducing thermal losses throughout the distribution system.

##### Eligibility Criteria

This measure applies to commercial and lodging applications with a central DHW system that includes a pump to circulate hot water through the distribution loop. To be eligible for these deemed savings, the control strategy must include operating the pump only when the hot water circulation loop temperature drops below a specific value, and there is hot water demand called by an end-user.

##### Baseline Condition

The baseline condition is a new or existing central DHW system with a circulation pump that operates continuously.

##### High-efficiency Condition

The measure requires the installation of a pump controller with a combination temperature and demand control method.

#### Energy and Demand Savings Methodology

Savings for central DHW controls come from circulation pump controller runtime reduction and thermal distribution loss reduction. Pump runtime savings apply to all projects, while thermal distribution loss reduction applies only to lodging sites with an electrically fueled water heater.

##### Savings Algorithms and Input Variables

Circulation Pump Savings Algorithm

Annual Pump Energy Savings kWh=kWpump×Pump%On_base-Pump%On_eff×Hours

Equation 190

Pump Demand Savings kW=Annual Pump Energy Savings ×PLS

Equation 191

Where:

kWpump		=		The demand used by the circulation pump, obtained from the project site. If unknown, assume 0.075 kW.

Pump%On_base		=		Baseline pump operation as percentage of time, 100%.

Pump%On_eff		=		Efficient pump operation as percentage of time, 7%.

Hours		=		Hours per year, 8760.

PLS		=		Probability weighted peak load share, Table 177.

Table 177: Central DHW Controls - Probability Weighted Peak Load Share

| Building Type | Commercial |  | Lodging |  |
| --- | --- | --- | --- | --- |
| Climate Zone | Summer Peak | Winter Peak | Summer Peak | Winter Peak |
| Zone 1 | 0.00016 | 0.00011 | 0.00012 | 0.00015 |
| Zone 2 | 0.00017 | 0.00011 | 0.00012 | 0.00014 |
| Zone 3 | 0.00016 | 0.00011 | 0.00012 | 0.00015 |
| Zone 4 | 0.00016 | 0.00011 | 0.00012 | 0.00015 |
| Zone 5 | 0.00018 | 0.00011 | 0.00012 | 0.00014 |

Thermal Distribution Savings Algorithm

Annual Thermal Energy Savings kWh=# Units ×kWhreference ×HDDAdjustment

Equation 192

Thermal Demand Savings kW=Annual Thermal Energy Savings ×PLS

Equation 193

Where:

# Units		=		The number of dwelling units at the project site.

kWhreference		=		Annual kWh energy savings from reference study, Table 178.

HDDAdjustment		=		Climate adjustment for Texas heating degree days, Table 179.

PLS		=		Probability weighted peak load share, Table 177.

Table 178: Central DHW Controls - Reference kWh by Water Heater and Building Type

| Water Heater Type | Electric Resistance |  | Heat Pump |  |
| --- | --- | --- | --- | --- |
| Building Type | Low Rise | High Rise | Low Rise | High Rise |
| kWh Reference | 539 | 332 | 211 | 130 |

Table 179: Central DHW Controls - HDD Adjustment Factors

| Climate Zone | HDD Adjustment |
| --- | --- |
| Zone 1 | 1.9 |
| Zone 2 | 1.1 |
| Zone 3 | 0.7 |
| Zone 4 | 0.5 |
| Zone 5 | 1.1 |

##### Deemed Energy Savings Tables

Table 180 presents the energy savings (kWh) for a range of pump sizes for all climate zones. The deemed savings are provided for convenience, but the algorithm may be used for pump sizes that differ from the assumed wattage listed in the tables.

Table 180: Central DHW Controls – Annual kWh Circulation Pump Savings

| Pump Size (watts) | Assumed Wattage | Annual Pump kWh Savings |
| --- | --- | --- |
| £ 50 | 50 | 407 |
| 50 < watts < 100 | 75 | 611 |
| 100 £ watts < 150 | 125 | 1,018 |
| ≥ 150 | 150 | 1,222 |

Table 181 presents the thermal energy savings (kWh) per dwelling unit for all climate zones. Thermal energy savings only apply to lodging building types where lodging takes place (multifamily, hotels, nursing homes, dormitories, prisons, and similar). For commercial applications, please follow a custom approach.

Table 181: Central DHW Controls - Annual kWh Thermal Distribution Savings per Dwelling Unit

| Climate Zone | Electric Resistance |  | Heat Pump |  |
| --- | --- | --- | --- | --- |
|  | Low Rise | High Rise | Low Rise | High Rise |
| Zone 1 | 1,007 | 620 | 395 | 243 |
| Zone 2 | 566 | 349 | 222 | 137 |
| Zone 3 | 372 | 229 | 146 | 90 |
| Zone 4 | 249 | 153 | 98 | 60 |
| Zone 5 | 590 | 364 | 231 | 143 |

##### Deemed Summer and Winter Demand Savings Tables

The following tables present the peak demand impacts for all climate zones.

Table 182: Central DHW Controls - Peak Demand kW Circulation Pump Savings

| Pump Size | Climate Zone | Commercial |  | Lodging |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Summer Peak kW | Winter Peak kW | Summer Peak kW | Winter Peak kW |
| £ 50 | Zone 1 | 0.065 | 0.045 | 0.049 | 0.061 |
|  | Zone 2 | 0.069 | 0.045 | 0.049 | 0.057 |
|  | Zone 3 | 0.065 | 0.045 | 0.049 | 0.061 |
|  | Zone 4 | 0.065 | 0.045 | 0.049 | 0.061 |
|  | Zone 5 | 0.073 | 0.045 | 0.049 | 0.057 |
| 50 < watts < 100 | Zone 1 | 0.098 | 0.067 | 0.073 | 0.092 |
|  | Zone 2 | 0.104 | 0.067 | 0.073 | 0.086 |
|  | Zone 3 | 0.098 | 0.067 | 0.073 | 0.092 |
|  | Zone 4 | 0.098 | 0.067 | 0.073 | 0.092 |
|  | Zone 5 | 0.110 | 0.067 | 0.073 | 0.086 |
| 100 £ watts < 150 | Zone 1 | 0.163 | 0.112 | 0.122 | 0.153 |
|  | Zone 2 | 0.173 | 0.112 | 0.122 | 0.143 |
|  | Zone 3 | 0.163 | 0.112 | 0.122 | 0.153 |
|  | Zone 4 | 0.163 | 0.112 | 0.122 | 0.153 |
|  | Zone 5 | 0.183 | 0.112 | 0.122 | 0.143 |
| ≥ 150 | Zone 1 | 0.196 | 0.134 | 0.147 | 0.183 |
|  | Zone 2 | 0.208 | 0.134 | 0.147 | 0.171 |
|  | Zone 3 | 0.196 | 0.134 | 0.147 | 0.183 |
|  | Zone 4 | 0.196 | 0.134 | 0.147 | 0.183 |
|  | Zone 5 | 0.220 | 0.134 | 0.147 | 0.171 |

Table 183: Central DHW Controls - Peak Demand kW Thermal Savings per Dwelling Unit

| Climate Zone | Summer Peak |  |  |  | Winter Peak |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Electric Resistance |  | Heat Pump |  | Electric Resistance |  | Heat Pump |  |
|  | Low Rise | High Rise | Low Rise | High Rise | Low Rise | High Rise | Low Rise | High Rise |
| Zone 1 | 0.12 | 0.07 | 0.05 | 0.03 | 0.15 | 0.09 | 0.06 | 0.04 |
| Zone 2 | 0.07 | 0.04 | 0.03 | 0.02 | 0.08 | 0.05 | 0.03 | 0.02 |
| Zone 3 | 0.04 | 0.03 | 0.02 | 0.01 | 0.06 | 0.03 | 0.02 | 0.01 |
| Zone 4 | 0.03 | 0.02 | 0.01 | 0.01 | 0.04 | 0.02 | 0.01 | 0.01 |
| Zone 5 | 0.07 | 0.04 | 0.03 | 0.02 | 0.08 | 0.05 | 0.03 | 0.02 |

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Additional Calculators and Tools

This section is not applicable.

##### Measure Life and Lifetime Savings

The estimated useful life (EUL) for central DHW controls is 15 years.

#### Program Tracking Data and Evaluation Requirements

It is required that the following list of primary inputs and contextual data be specified and tracked by the program database to inform the evaluation and apply the savings properly:

- Climate zone

- Circulation pump wattage

- Building type: Commercial or lodging

- Building size: Low rise or high rise

- Water heater type: Electric resistance or heat pump

- If lodging, number of lodging units at project site

#### References and Efficiency Standards

##### Petitions and Rulings

This section is not applicable.

##### Relevant Standards and Reference Sources

- DEER 2014 EUL update.

### High Speed Doors for Cold Storage Measure Overview

TRM Measure ID: NR-RF-HS

Market Sector: Commercial

Measure Category: Refrigeration

Applicable Building Types: Commercial

Fuels Affected: Electricity

Decision/Action Type: Retrofit or new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Algorithms

Savings Methodology: Algorithms

#### Measure Description

This measure presents deemed savings for installation of high speed doors for cold storage facilities. High speed automatic doors differ from regular automatic doors by increasing their closing speed. High speed doors can save energy over regular automatic and manual doors by shortening the duration that the door to the cold storage area is open.

##### Eligibility Criteria

Eligible equipment includes high speed doors with a minimum opening rate of 32 inches per second, a minimum closing rate of 24 inches per second, and a means to automatically reclose the door, as defined by the Door and Access Systems Manufacturers’ Association, International (DASMA). The high speed doors must be installed for access to a cold storage area either from exterior conditions, such as a loading dock, or from a conditioned area, such as a non-refrigerated warehouse.

##### Baseline Condition

The baseline condition is a manual or non-high speed automatic door installed for access to a cold storage area.

##### High-efficiency Condition

The efficient condition is a high speed door installed for access to a cold storage area.

#### Energy and Demand Savings Methodology

##### Savings are calculated based on a reduction in heat gain from airflow across the door opening area. The algorithms below are modeled after equations 14 and 16 in Chapter 24: Refrigerated-Facility Loads of the 2018 ASHRAE Handbook—Refrigeration to calculate heat load associated with infiltration air exchange. This measure does not account for associated motor load or efficiencies; if the new high speed door includes an efficient motor, reference the motor measure for savings.

##### Savings Algorithms and Input Variables

kWh savings=w×h1.5×energy factorCOP ×3,412

Equation 194

energy factor=hours ×3790×qsA×1Rs×∆Dt×Df×∆E

Equation 195

kW savings=w×h1.5×demand factorCOP ×3,412

Equation 196

demand factor=3790×qsA×1Rs×∆Dt×Df×∆E

Equation 197

Where:

w		= 	width of the door opening, ft

h		= 	height of the door opening, ft

energy factor	= 	the outcome of Equation 195 based on climate zone and cold storage application, see Table 184 and Table 185

demand factor	= 	the outcome of Equation 197 based on climate zone and cold storage application, see Table 186,

Table 185: High Speed Doors – Energy Factors for Door to Conditioned Area

| Cold Room Temperature | -20°F | 0°F | 20°F | 40°F |
| --- | --- | --- | --- | --- |
| All Zones | 783,056 | 518,199 | 322,435 | 230,311 |

Table 186: High Speed Doors – Summer and Winter Demand Factors for Door to Conditioned Area

| Cold Room Temperature | All Temperatures |
| --- | --- |
| All Climate Zones | 1.0 |

Table 187 and Table 188

hours		= 	operating hours, 3,798

3790		=	constant

qsA		= 	sensible heat load of infiltration air per square foot of door opening, ton/ft2, see

Table 189

Rs		= 	Sensible heat ratio of the infiltration air heat gain, see Table 190

∆Dt		= 	change in percent of time the doorway is open, 0.33

Df		= 	Doorway flow factor, varies based on Temperature delta between cold room and infiltration air, 0.8 for delta T ≥ 20°F, 1.1 for delta T < 20°F

∆E		= 	change in door effectiveness, 0.2

COP		= 	coefficient of performance, assume 2.8 COP

3,412		= 	conversion factor

Table 184: High Speed Doors – Energy Factors for Door to Unconditioned Area

| Cold Room Temperature | -20°F | 0°F | 20°F | 40°F |
| --- | --- | --- | --- | --- |
| Zone 1 | 849,911 | 576,602 | 324,007 | 122,795 |
| Zone 2 | 1,025,489 | 719,712 | 432,092 | 209,695 |
| Zone 3 | 1,179,743 | 837,151 | 562,418 | 420,336 |
| Zone 4 | 1,240,984 | 887,904 | 603,598 | 464,913 |
| Zone 5 | 902,050 | 614,930 | 343,300 | 142,285 |

Table 185: High Speed Doors – Energy Factors for Door to Conditioned Area

| Cold Room Temperature | -20°F | 0°F | 20°F | 40°F |
| --- | --- | --- | --- | --- |
| All Zones | 783,056 | 518,199 | 322,435 | 230,311 |

Table 186: High Speed Doors – Summer and Winter Demand Factors for Door to Conditioned Area

| Cold Room Temperature | All Temperatures |
| --- | --- |
| All Climate Zones | 1.0 |

Table 187: High Speed Doors – Summer Demand Factors for Door to Unconditioned Area

| Cold Room Temperature | -20°F | 0°F | 20°F | 40°F |
| --- | --- | --- | --- | --- |
| Zone 1 | 278.94 | 208.20 | 141.49 | 90.96 |
| Zone 2 | 293.09 | 218.30 | 153.62 | 101.07 |
| Zone 3 | 293.09 | 218.30 | 153.62 | 101.07 |
| Zone 4 | 264.79 | 192.03 | 131.39 | 76.81 |
| Zone 5 | 278.94 | 208.20 | 141.49 | 90.96 |

Table 188: High Speed Doors – Winter Demand Factors for Door to Unconditioned Area

| Cold Room Temperature | -20°F | 0°F | 20°F | 40°F |
| --- | --- | --- | --- | --- |
| Zone 1 | 40.43 | - | - | - |
| Zone 2 | 40.43 | - | - | - |
| Zone 3 | 80.85 | 36.38 | 22.23 | - |
| Zone 4 | 80.85 | 36.38 | 22.23 | - |
| Zone 5 | 80.85 | 36.38 | - | - |

Table 189: High Speed Doors – qsA, Sensible Heat Load of Infiltration Air

| Applicable Climate Zones | Z1-2, winter peak | Z3-5, winter peak | Z1, annual | Z2, Z5, annual | Z3-4, annual | Z4, summer peak | Z1, Z5, summer peak | Z2-3, summer peak |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Infiltration Air Temperature | 15°F | 30°F | 63°F | 70°F | 75°F | 96°F | 99°F | 103°F |
| Cold Room Temperature |  |  |  |  |  |  |  |  |
| -20°F | 0.2 | 0.40 | 0.85 | 0.94 | 1.02 | 1.31 | 1.38 | 1.45 |
| 0°F | - | 0.18 | 0.55 | 0.62 | 0.68 | 0.95 | 1.03 | 1.08 |
| 20°F | - | 0.08 | 0.30 | 0.35 | 0.42 | 0.65 | 0.70 | 0.76 |
| 40°F | - | - | 0.13 | 0.17 | 0.30 | 0.38 | 0.45 | 0.50 |

Table 190: High Speed Doors – Rs, Sensible Heat Ratio of Infiltration Air

|  | For Energy Factor, Unconditioned Space |  |  |  | For Energy Factor, Conditioned Space | For Demand Factor, Conditioned and Unconditioned Space |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Cold Room Temperature | -20°F | 0°F | 20°F | 40°F | All Temperatures | Summer, all Temperatures | Winter, all Temperatures |
| Zone 1 | 0.77 | 0.73 | 0.71 | 0.81 | 1.0 | 1.0 | 1.0 |
| Zone 2 | 0.70 | 0.66 | 0.62 | 0.62 |  |  |  |
| Zone 3 | 0.66 | 0.62 | 0.57 | 0.55 |  |  |  |
| Zone 4 | 0.63 | 0.58 | 0.53 | 0.50 |  |  |  |
| Zone 5 | 0.80 | 0.77 | 0.78 | 0.92 |  |  |  |

##### Deemed Energy and Demand Savings Tables

There are no deemed savings tables for this measure. Please refer to the savings algorithms above.

##### Measure Life and Lifetime Savings

#### The estimated useful life (EUL) for this measure is 5 years based on published manufacturer warranty duration.

#### Program Tracking Data and Evaluation Requirements

The following primary inputs and contextual data should be specified and tracked within the program database to inform the evaluation and apply the savings properly.

- Climate Zone

- Cold Room Temperature

- Doorway opening location – conditioned or unconditioned

- Width and height of door

#### References and Efficiency Standards

##### Petitions and Rulings

This section is not applicable.

##### Relevant Standards and Reference Sources

This section is not applicable.

### Showerhead Temperature Sensitive Restrictor Valves Measure Overview

TRM Measure ID: NR-MS-SV

Market Sector: Commercial

Measure Category: Miscellaneous

Applicable Building Types: Lodging

Fuels Affected: Electricity, gas

Decision/Action Type(s): Retrofit, new construction

Program Delivery Type(s): Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This measure consists of installing a temperature sensitive restrictor valve (TSRV) between the existing shower arm and showerhead. The valve restricts hot water flow through the showerhead once the water reaches a set temperature (generally 95˚F) to prevent water from going down the drain prior to the user entering the shower, thereby eliminating behavioral waste.

##### Eligibility Criteria

These deemed savings are for temperature sensitive restrictor valves installed in new construction or as a retrofit measure in commercial lodging applications. To use deemed savings, the fuel type of the water heater must be electricity or gas.

##### Baseline Condition

The baseline condition is the commercial lodging shower arm and standard (2.5 gpm) showerhead without a temperature sensitive restrictor valve installed.

##### High-efficiency Condition

The high-efficiency condition is a temperature sensitive restrictor valve installed on a commercial lodging shower arm and showerhead with either a standard (2.5 gpm) or low-flow (2.0, 1.75, or 1.5 gpm) showerhead.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

###### Estimated Hot Water Usage Reduction

To determine gallons of behavioral waste (defined as hot water that goes down the drain before the user enters the shower) per year, the following formula was used:

Annual Showerhead Behavioral Waste= SHFR×BW×nS×365 daysyear×OCCnOnSH

Equation 198

Where:

SHFR 	= 	Showerhead flow rate, gallons per minute (gpm) (see Table 191)

BW	= 	Behavioral waste, minutes per shower (see Table 191)

nS	= 	Number of showers per occupied room per day (see Table 191)

365	= 	Constant to convert days to years (see Table 191)

OccCPCP	= 	Occupancy rate (see Table 191)

nSH	= 	Number of showerheads per room (see Table 191)

Applying the formula to the values used for Texas from Table 191 returns the following values for baseline behavioral waste in gallons per showerhead per year:

Showerhead 2.5 GPM:2.5× 1.7420.783×1.7560.72×365×0.6592.791.01.68=1,838854 gal

Showerhead 2.0 GPM:2.0×1.7420.783×1.7560.72×365× 0.6592.791.01.68=1,471683 gal

Showerhead 1.75 GPM:1.75×1.7420.783×1.7560.72×365×0.6592.791.01.68=1,287598 gal

Showerhead 1.5 GPM:1.5×1.7420.783×1.7560.72×365×0.6592.791.01.68=1,103513 gal

Gallons of hot water saved per year can be found by multiplying the baseline behavioral waste gallons per year by the percent of hot water from Table 191.

Gallons of hot water saved per year= Annual Behavioral Waste×HW%

Equation 199

Where:

HW% 	= 	Hot water percentage (see Table 191)

Gallons of hot water saved per year 2.5 GPM: 1,838854× 0.825=1,516705 gal

Gallons of hot water saved per year 2.0 GPM: 1,471683× 0.825=1,213563 gal

Gallons of hot water saved per year 1.75 GPM: 1,287598× 0.825=1,062493 gal

Gallons of hot water saved per year 1.5 GPM: 1,103513× 0.825=910423 gal

Table 191: Showerhead TSRVs – Hot Water Usage Reduction

| Description | 2.5 gpm | 2.0 gpm | 1.75 gpm | 1.5 gpm |
| --- | --- | --- | --- | --- |
| Average behavioral waste (minutes per shower) | 1.742 |  |  |  |
| Showers/occupied room/day | 1.756 |  |  |  |
| Occupancy rate | 65.9% |  |  |  |
| Showerheads/room | 1.0 |  |  |  |
| Behavioral waste/showerhead/year (gal) | 1,838 | 1,471 | 1,287 | 1,103 |
| Percent hot water | 80-85%, or 82.5% on average |  |  |  |
| Hot water saved/year (gal) | 1,516 | 1,213 | 1,062 | 910 |

##### Energy Savings Algorithms

Energy savings for this measure are calculated as follows:

Energy Savings per TSRV= ρ×CP×V×(TSetPoint-TSupplyAverage)RE×Conversion Factor

Equation 200

Where:

ρρ 	= 	Water density, 8.33 lbs/gallon

CPCP	= 	Specific heat of water, 1 Btu/lb°F

VV 	= 	Gallons of hot water saved per year per showerhead (see Table 191)

TSetPointTSetPoint 	= 	Water heater setpoint: 120°F

TSupplyTSupply 	= 	Average supply water temperature (see Table 192)

RERE 	= 	Recovery Efficiency (or in the case of heat pump water heaters, COP). If unknown, use 0.98 as a default for electric resistance water heaters, 2.2 for heat pump water heaters, or 0.8 for gas hot water heaters.

Conversion FactorConversionFactor	 = 	3,412 Btu/kWh for electric or 100,000 Btu/therm for gas

##### Demand Savings Algorithms

Demand savings are calculated by substituting the average supply temperature for the average seasonal temperature, multiplying by a coincidence factor equivalent to the daily fraction hot water use during the weighted peak hour for each climate zone (see Volume 1, Section 4), and dividing by 365 days/year.

Demand Savings per TSRV= ρ×CP×V×(TSetPoint-TSupplySeasonal)RE×Conversion Factor×365×CFRatioannual kWhPeakseasonalkW

Equation 201

Where:

TSupplySeasonalTSupplySeasonal 	= 	Seasonal supply water temperature (see Table 192)

CFRatioannual kWhPeakseasonalkW = 	Peak coincidence factor (see Table 193)

Table 192: Showerhead TSRVs – Water Mains Temperatures

| Climate Zone | Water Mains Temperature (°F) |  |  |  |
| --- | --- | --- | --- | --- |
|  | TSupplyAverage |  | TSupplySeasonal |  |
|  |  |  | Summer | Winter |
| Climate Zone 1: Panhandle | 62.9 | 73.8 |  | 53.7 |
| Climate Zone 2: North | 71.8 | 84.0 |  | 60.6 |
| Climate Zone 3: South | 74.7 | 84.5 |  | 65.5 |
| Climate Zone 4: Valley | 77.2 | 86.1 |  | 68.5 |
| Climate Zone 5: West | 70.4 | 81.5 |  | 60.4 |

Table 193: Showerhead TSRVs – Peak Coincidence Factors

| Climate Zones | Summer |  | Winter |
| --- | --- | --- | --- |
| Climate Zone 1: Panhandle | 0.039 |  | 0.073 |
| Climate Zone 2: North | 0.035 |  | 0.075 |
| Climate Zone 3: South | 0.038 |  | 0.080 |
| Climate Zone 4: Valley | 0.038 |  | 0.068 |
| Climate Zone 5: West | 0.028 |  | 0.069 |

=0.000274=0.000274=0.000110=0.000110

Figure 6: Showerhead TSRVs – Shower, Bath, and Sink Hot Water Use Profile

Source: Building America Performance Analysis Procedures for Existing Homes.

##### Deemed Energy Savings Tables

There are no lookup tables available for this measure. See engineering algorithms in the previous section for calculating energy and demand savings.

##### Deemed Summer Demand Savings Tables

There are no lookup tables available for this measure. See engineering algorithms in the previous section for calculating energy and demand savings.

##### Deemed Winter Demand Savings Tables

There are no lookup tables available for this measure. See engineering algorithms in the previous section for calculating energy and demand savings.

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Additional Calculators and Tools

This section is not applicable.

##### Measure Life and Lifetime Savings

The estimated useful life (EUL) for this measure is established at 10 years.

This value is consistent with the EUL reported for a low-flow showerhead in the 2014 California Database for Energy Efficiency Resources (DEER).

#### Program Tracking Data and Evaluation Requirements

Primary inputs and contextual data that should be specified and tracked by the program database to inform the evaluation and apply the savings properly are:

- Climate zone

- Flow rate in gallons per minute (gpm) of showerhead installed

- Water heater type (e.g., heat pump, electric resistance)

- DHW Recovery efficiency (RE) or COP, if available

### Tub Spout and Showerhead Temperature Sensitive Restrictor Valves Measure Overview

TRM Measure ID: NR-MS-TV

Market Sector: Commercial

Measure Category: Miscellaneous

Applicable Building Types: Lodging

Fuels Affected: Electricity, gas

Decision/Action Type(s): Retrofit, new construction

Program Delivery Type(s): Prescriptive

Deemed Savings Type: Deemed savings calculation

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

This measure consists of replacing existing tub spouts and showerheads with an automatically diverting tub spout and showerhead system with a temperature sensitive restrictor valve (TSRV) between the existing shower arm and showerhead. The tub spout will contain temperature sensitive restrictor technology that will cause the tub spout to automatically engage the anti-leak diverter once the water reaches a set temperature (generally 95˚F). The water will divert to a showerhead with a normally closed valve that will prevent the hot water from going down the drain prior to the user entering the shower, thereby eliminating behavioral waste and tub spout leakage waste.

##### Eligibility Criteria

These deemed savings are for tub spout and showerhead systems with temperature sensitive restrictor technology installed in new construction or as a retrofit measure in commercial lodging applications. To use these deemed savings, the fuel type of the water heater must be electricity or gas.

##### Baseline Condition

The baseline condition is the commercial loding tub spout with a standard diverter and a standard (2.5 gpm) showerhead.

##### High-efficiency Condition

The high-efficiency condition is an anti-leak, automatically diverting tub spout system with temperature sensitive restrictor technology installed on a commercial loding shower arm and showerhead with a standard (2.5 gpm) or low-flow (2.0, 1.75, or 1.5 gpm) showerhead.

#### Energy and Demand Savings Methodology

##### Savings Algorithms and Input Variables

###### Estimated Hot Water Usage Reduction

This system provides savings in two parts: elimination of behavioral waste (hot water that goes down the drain prior to the user entering the shower) and elimination of tub spout diverter leakage.

Part 1: To determine baseline gallons of behavioral waste per year, the following formula was used:

Annual Showerhead Behavioral Waste=%WUESH×SHFR×BW×nS×365 daysyear×OCCnOnSH

Equation 202

Annual Tub Spout Behavioral Waste=%WUETS×TSFR×BW×nS×365 daysyear×OCCnOnSH

Equation 203

Where:

%WUESH 	= 	Showerhead percentage of warm-up events (see Table 194)

%WUETS 	= 	Tub spout percentage of warm-up events (see Table 194)

SHFR 	= 	Showerhead flow rate, gallons per minute (gpm) (see Table 194)

TSFR 	= 	Tub spout flow rate, gallons per minute (gpm) (see Table 194)

BW	= 	Behavioral waste, minutes per shower (see Table 194)

nS	= 	Number of showers per occupied room per day (see Table 194)

365	= 	Constant to convert days to years (see Table 194)

OCC	= 	Occupancy rate (see Table 194)

nSH		= 	Number of showerheads per room (see Table 194)

Applying the formula to the values from Table 194 returns the following values:

Showerhead (1.5 GPM): 0.6×1.5×1.7420.783×1.7560.72×365×0.6592.791.01.68=662308

Showerhead (1.75 GPM): 0.6×1.75×1.7420.783×1.7560.72×365×0.6592.791.01.68=772359

Showerhead (2.0 GPM): 0.6×2.0×1.7420.783×1.7560.72×365×0.6592.791.01.68=882410

Showerhead (2.5 GPM): 0.6×2.5×1.7420.783×1.7560.72×365×0.6592.791.01.68=1,103513

Tub Spout 5.0 GPM: 0.4×5.0×1.7420.783×1.7560.72×365×0.6592.791.01.68=1,471683

Part 2: To determine baseline gallons of diverter leakage per year, the following formula was used:

Annual Diverter Waste=DLR×tS×nS×365 daysyear×OCCnOnSH

Equation 204

Where:

DLR 	= 	Diverter leakage rate (gpm) (see Table 194)

tS 	= 	Shower time (min/shower) (see Table 194)

Applying the formula to the values used for Texas from Table 194 returns the following values:

Diverter (0.8 GPM): 0.8×7.85.68×1.7560.72×365×0.6592.791.01.68=2,6341,983

Part 3: To determine gallons of water saved per year can be found by multiplying the total waste by the percent of hot water from Table 194.

Gallons of hot water saved=SHBW+TSBW×HW%SH,TS+DW×HW%D

Equation 205

Where:

SHBW 	= 	Showerhead behavioral waste (gal)

TSBW 	= 	Tub spout behavioral waste (gal)

DW 	= 	Diverter waste (gal)

HW%SH,TS 	= 	Showerheads and tub spout hot water percentage (see Table 194)

HW%D 	= 	Diverter hot water percentage (see Table 194)

Applying the formula to the values from Table 194 returns the following values:

Total Annual Waste 1.5 gpm:662308+1,471683×0.825+2,6341,983×0.737=3,7002,279

Total Annual Waste 1.75 gpm:772359+1,471683×0.825+2,6341,983×0.737=3,7912,321

Total Annual Waste 2.0 gpm:882410+1,471683×0.825+2,6341,983×0.737=3,8822,363

Total Annual Waste 2.5 gpm:1,103513+1,471683×0.825+2,6341,983×0.737=4,0642,448

Table 194: Tub Spout/Showerhead TSRVs – Hot Water Usage Reduction

| Description | Part 1- Behavioral Waste |  | Part 2—Diverter Leakage | Part 3—Total |
| --- | --- | --- | --- | --- |
|  | Showerhead Warm-up | Tub spout Warm-up |  |  |
| Baseline showerhead flow rate (gpm) | 1.5, 1.75, 2.0, or 2.5 | N/A |  |  |
| Tub spout flow rate (gpm) | N/A | 5.0 | N/A |  |
| Percent of warm-up events | 60% | 40% | N/A |  |
| Average behavioral waste (minutes per shower) | 1.742 |  | N/A |  |
| Average diverter leakage rate (gpm) | N/A |  | 0.80 | N/A |
| Average shower time (minutes) | N/A |  | 7.8 | N/A |
| Showers/occupied room/day | 1.756 |  |  |  |
| Occupancy rate | 65.9% |  |  |  |
| Showerheads/room | 1.0 |  |  |  |
| Gallons behavioral waste per tub spout/showerhead per year (1.5 gpm) | 662 | 1,471 | 2,634 | 4,766 |
| Gallons behavioral waste per tub spout/showerhead per year (1.75 gpm) | 772 |  |  | 4,877 |
| Gallons behavioral waste per tub spout/showerhead per year (2.0 gpm) | 882 |  |  | 4,987 |
| Gallons behavioral waste per tub spout/showerhead per year (2.5 gpm) | 1,103 |  |  | 5,207 |
| Percent hot water | 80-85%, or 82.5% average |  | 73.7% | N/A |
| Gallons hot water saved per year (1.5 gpm) | N/A |  |  | 3,700 |
| Gallons hot water saved per year (1.75 gpm) | N/A |  |  | 3,791 |
| Gallons hot water saved per year (2.0 gpm) | N/A |  |  | 3,882 |
| Gallons hot water saved per year (2.5 gpm) | N/A |  |  | 4,064 |

##### Energy Savings Algorithms

Energy savings for this measure are calculated as follows:

Energy Savings per TS System= ρ×CP×V×(TSetPoint-TSupplyAverage)RE×Conversion Factor

Equation 206

Where:

ρρ 	= 	Water density, 8.33 lbs/gallon

CPCP	= 	Specific heat of water, 1 Btu/lb°F

VV 	= 	Gallons of hot water saved per year per showerhead (see Table 194)

TSetPointTSetPoint 	= 	Water heater setpoint: 120°F

TSupplyTSupply 	= 	Average supply water temperature (see

Table 195)

RERE 	= 	Recovery Efficiency (or in the case of heat pump water heaters, COP). If unknown, use 0.98 as a default for electric resistance water heaters, 2.2 for heat pump water heaters, or 0.8 for gas hot water heaters.

Conversion FactorConversionFactor	 = 	3,412 Btu/kWh for electric or 100,000 Btu/therm for gas

##### Demand Savings Algorithms

Demand savings are calculated by substituting the average supply temperature for the average seasonal temperature, multiplying by a coincidence factor equivalent to the daily fraction hot water use during the weighted peak hour for each climate zone (see Volume 1, Section 4), and dividing by 365 days/year.

Demand Savings per TS System= ρ×CP×V×(TSetPoint-TSupplySeasonal)RE×Conversion Factor×365×CFRatioannual kWhPeakseasonalkW

Equation 207

Where:

TSupplySeasonalTSupplySeasonal 	= 	Seasonal supply water temperature (see

Table 195)

CFRatioannual kWhPeakseasonalkW = 	Peak coincidence factor (see Table 196)

Table 195: Tub Spout/Showerhead TSRVs – Water Mains Temperatures

| Climate Zone | Water Mains Temperature (°F) |  |  |  |
| --- | --- | --- | --- | --- |
|  | TSupplyAverage |  | TSupplySeasonal |  |
|  |  |  | Summer | Winter |
| Climate Zone 1: Panhandle | 62.9 | 73.8 |  | 53.7 |
| Climate Zone 2: North | 71.8 | 84.0 |  | 60.6 |
| Climate Zone 3: South | 74.7 | 84.5 |  | 65.5 |
| Climate Zone 4: Valley | 77.2 | 86.1 |  | 68.5 |
| Climate Zone 5: West | 70.4 | 81.5 |  | 60.4 |

Table 196: Tub Spout/Showerhead TSRVs – Peak Coincidence Factors

| Climate Zones |  | Summer | Winter |  |
| --- | --- | --- | --- | --- |
| Climate Zone 1: Panhandle |  | 0.039 | 0.073 |  |
| Climate Zone 2: North |  | 0.035 | 0.075 |  |
| Climate Zone 3: South |  | 0.038 | 0.080 |  |
| Climate Zone 4: Valley |  | 0.038 | 0.068 |  |
| Climate Zone 5: West |  | 0.028 | 0.069 |  |

0.1 365=0.0002740.1365=0.0002740.04 365=0.0001100.04365=0.000110

Figure 7: Tub Spout/Showerhead TSRVs – Shower, Bath, and Sink Hot Water Use Profile

Source: Building America Performance Analysis Procedures for Existing Homes.

##### Deemed Energy Savings Tables

There are no lookup tables available for this measure. See engineering algorithms in the previous section for calculating energy and demand savings.

##### Deemed Summer Demand Savings Tables

There are no lookup tables available for this measure. See engineering algorithms in the previous section for calculating energy and demand savings.

##### Deemed Winter Demand Savings Tables

There are no lookup tables available for this measure. See engineering algorithms in the previous section for calculating energy and demand savings.

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Additional Calculators and Tools

This section is not applicable.

##### Measure Life and Lifetime Savings

The estimated useful life (EUL) for this measure is established at 10 years.

This value is consistent with the EUL reported for a low-flow showerhead in the 2014 California Database for Energy Efficiency Resources (DEER).

#### Program Tracking Data and Evaluation Requirements

Primary inputs and contextual data that should be specified and tracked by the program database to inform the evaluation and apply the savings properly are:

- Climate zone

- Flow rate in gallons per minute (GPM) of showerhead installed

- Water heater type (e.g., heat pump, electric resistance)

- DHW Recovery Efficiency (RE) or COP, if available

### ENERGY STAR® Electric Vehicle Supply Equipment (EVSE) Measure Overview

TRM Measure ID: NR-MS-EV

Market Sector: Commercial

Measure Category: Appliance

Applicable Business Types: All

Fuels Affected: Electricity

Decision/Action Type: Retrofit, new construction

Program Delivery Type: Prescriptive

Deemed Savings Type: Look-up tables

Savings Methodology: Engineering algorithms and estimates

#### Measure Description

##### This measure applies to the installation of ENERGY STAR® certified Level 2 electric vehicle supply equipment (EVSE) at a commercial site. EVSE is the infrastructure that enables plug-in electric vehicles (PEV) to charge onboard batteries. Level 2 EVSE require 240-volt electrical service. This measure provides deemed savings for the energy efficiency improvement of an ENERGY STAR EVSE over a standard or non-ENERGY STAR EVSE.

##### Eligibility Criteria

##### Eligible equipment includes an ENERGY STAR certified Level 2 EVSE installed in a commercial application, which includes public, multifamily, workplace, and fleet locations. Public locations are sites where an EVSE is intended to be used by the public or visitors to the site. This includes locations such as retail, education, municipal, hospitality, and other similar locations. For the purposes of this measure, multifamily sites are public locations. Workplace locations include sites where an EVSE is intended to be used by employees to charge their personal vehicles when reporting to the workplace site. Fleet locations include sites where an EVSE is intended to be used to charge a fleet of company vehicles. The EVSE may be installed for use on either an all-battery electric vehicle (BEV) or a plug-in hybrid electric vehicle (PHEV). Savings estimates for this measure are based on studies of light duty vehicles; EVSE for charging heavy duty vehicles should pursue custom M&V.

##### Baseline Condition

The baseline condition is a non-ENERGY STAR certified Level 2 EVSE.

##### High-efficiency Condition

#### The high-efficiency EVSE must be an ENERGY STAR® certified Level 2 EVSE.

#### Energy and Demand Savings Methodology

Savings for EVSE come from efficiency gains of the ENERGY STAR equipment during operating modes when the vehicle is plugged in but not charging and when not plugged in. Deemed savings are calculated according to the following algorithms.

##### Savings Algorithms and Input Variables

ENERGY STAR Idle Consumption kWh=hrsplug×Wplug+hrsunplug_C×Wunplug×daysC+hrsunplug_NC×Wunplug×daysNC1000

Equation 208

Baseline Idle Consumption kWh=ENERGY STAR Idle Consumption0.6

Equation 209

Annual Energy Savings kWh=Baseline Idle Consumption-ENERGY STAR Idle Consumption

Equation 210

Demand Savings kW=Annual Energy Savings (kWh) hrsunplug_C×daysC+hrsunplug_NC×daysNCAnnual Energy Savings ×PLSPDPF

Equation 211

Where:

hrsplug		=	Hours per day the vehicle is plugged into the EVSE and not charging,  2.8 hrs.

Wplug		=	Wattage of the EVSE when the vehicle is plugged into the EVSE but not charging, 6.9 W.

hrsunplug_C	=	Hours per day the vehicle is not plugged into the EVSE on a charging day, 19.0 hrs.

hrsunplug_NC	=	Hours per day the vehicle is not plugged into the EVSE on a non-charge day, 24 hrs.

Wunplug		=	Wattage of the EVSE when the vehicle is not plugged into the EVSE, 3.3 W.

daysC		=	Number of charging days per year, 204 days.

daysNC		=	Number of non-charging days per year, 161 days.

1000		=	conversion from Wh to kWh

0.6		=	Efficiency adjustment factor

PDPF		=	Peak demand probability factor, Table 197

Table 197: EVSE Peak Demand Probability Factors

| Location Type | Public |  | Workplace |  | Fleet |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Summer PDPF | Winter PDPF | Summer PDPF | Winter PDPF | Summer PDPF | Winter PDPF |
| Climate Zone 1 | 0.46526 | 0.46032 | 0.87484 | 0.75271 | 0.27206 | 0.44421 |
| Climate Zone 2 | 0.45808 | 0.47380 | 0.86213 | 0.75558 | 0.22867 | 0.42040 |
| Climate Zone 3 | 0.46134 | 0.42544 | 0.87173 | 0.68222 | 0.26507 | 0.34306 |
| Climate Zone 4 | 0.46892 | 0.49816 | 0.87553 | 0.77324 | 0.25862 | 0.50077 |
| Climate Zone 5 | 0.42680 | 0.51324 | 0.80969 | 0.92091 | 0.15042 | 0.57715 |

Deemed Energy Savings Tables

Table 198 presents the deemed annual energy savings per EVSE.

Table 198: EVSE Annual Energy Savings

Annual Energy Savings (kWh) (All Location Types)

19.7

##### Deemed Summer and Winter Demand Savings Tables

##### Table 199 presents the deemed summer and winter peak kW savings per EVSE.

Table 199: EVSE Peak Demand Savings

| Location Type | Public |  | Workplace |  | Fleet |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Summer Peak kW | Winter Peak kW | Summer Peak kW | Winter Peak kW | Summer Peak kW | Winter Peak kW |
| Zone 1 | 0.0012 | 0.0012 | 0.0022 | 0.0019 | 0.0008 | 0.0012 |
| Zone 2 | 0.0012 | 0.0012 | 0.0022 | 0.0019 | 0.0006 | 0.0012 |
| Zone 3 | 0.0012 | 0.0011 | 0.0022 | 0.0017 | 0.0007 | 0.0010 |
| Zone 4 | 0.0012 | 0.0013 | 0.0022 | 0.0020 | 0.0007 | 0.0014 |
| Zone 5 | 0.0011 | 0.0013 | 0.0021 | 0.0023 | 0.0004 | 0.0016 |

##### Claimed Peak Demand Savings

Refer to Volume 1, Appendix B: Peak Demand Reduction Documentation for further details on peak demand savings and methodology.

##### Additional Calculators and Tools

This section is not applicable.

##### Measure Life and Lifetime Savings

The estimated useful life (EUL) for an EVSE is assumed to be 10 years.

#### Program Tracking Data and Evaluation Requirements

It is required that the following list of primary inputs and contextual data be specified and tracked by the program database to inform the evaluation and apply the savings properly:

- Climate zone

- Location Type: Public, Workplace, or Fleet

- EVSE make and model number

- Vehicle year, make, and model

- Estimated number of miles driven per day

#### References and Efficiency Standards

##### Petitions and Rulings

- This section not applicable.

##### Relevant Standards and Reference Sources

- The applicable version of the ENERGY STAR® specifications and requirements for electric vehicle supply equipment.

###### Measure Life Calculations for Dual Baseline Measures

The following appendix describes the method to calculate savings for any dual baseline measure, including all early retirement measures. This supersedes the previous Measure Life Savings found in PUCT Dockets 40083 and 40885 and is revised to clarify the understanding of the measure life calculations and reduce any misrepresentation of net present value (NPV) of early retirement projects.

Option 1 provides reduced savings claimed over the full EUL. Option 2 provides higher savings claimed over a reduced EUL. The lifetime savings are the same for both options 1 and 2. Option 1 calculations were originally provided in Docket [43681].

Option 1—Weighting Savings and Holding Measure Life Constant

Step 1: Determine the measure life for first-tier (FT) and second-tier (ST) components of the calculated savings:

First Tier FT Period=MLFT=RUL

Equation 216

Second Tier ST Period= MLST=EUL-RUL

Equation 217

Where:

RUL	=	The useful life corresponding with the first tier-savings. For early retirement projects, RUL is the remaining useful life determined from lookup tables based on the age of the replaced unit (or default age when actual age is unknown)

EUL	=	The useful life corresponding with the second-tier savings. For early retirement projects, EUL is the estimated useful life as specified in applicable measure from Texas TRM (or approved petition)

Step 2: Calculate the FT demand and energy savings and the ST demand and energy savings:

∆kWFT=kWreplaced-kWinstalled

Equation 218

∆kWST=kWbaseline-kWinstalled

Equation 219

∆kWhFT=kWhreplaced-kWhinstalled

Equation 220

∆kWhST=kWhbaseline-kWhinstalled

Equation 221

Where:

ΔkWFT	=	First-tier demand savings

ΔkWST	=	Second-tier demand savings

kWreplaced	=	Demand of the first-tier baseline system, usually the retired system

kWbaseline	=	Demand of the second-tier baseline system, usually the baseline ROB system

kWinstalled	=	Demand of the replacement system

ΔkWhFT	=	First-tier energy savings

ΔkWhST	=	Second-tier energy savings

kWhreplaced	=	Energy Usage of the first-tier baseline system, usually the retired system491

kWhbaseline	=	Energy Usage of the second-tier baseline system, usually the baseline ROB system492

kWhinstalled	=	Energy Usage of the replacement system493

Step 3: Calculate the avoided capacity and energy cost contributions of the total NPV for both the ER and ROB components:

NPVFT, kW=ACkW×1+ed-e×1-1+e1+dMLFT×∆kWFT

Equation 222

NPVST, kW=ACkW×1+ed-e×1-1+e1+dMLST×1+eMLFT1+dMLFT×∆kWST

Equation 223

NPVFT, kWh=ACkWh×1+ed-e×1-1+e1+dMLFT×∆kWhFT

Equation 224

NPVST, kWh=ACkWh×1+ed-e×1-1+e1+dMLST×1+eMLFT1+dMLFT×∆kWhST

Equation 225

Where:

NPVFT, kW	=	Net Present Value (kW) of first-tier projects

NPVST, kW	=	Net Present Value (kW) of second-tier projects

NPVFT, kWh	=	Net Present Value (kWh) of first-tier projects

NPVST, kWh	=	Net Present Value (kWh) of second-tier projects

e	=	Escalation Rate

d 	= 	Discount rate weighted average cost of capital (per utility) 494

ACkW 	=	Avoided cost per kW ($/kW) 494

ACkWh 	=	Avoided cost per kWh ($/kWh) 494

MLFT	=	First-tier Measure Life (calculated in Equation 216)

MLST	=	Second-tier measure life (calculated in Equation 217)

Step 4: Calculate the total capacity and energy cost contributions to the total NPV:

NPVTotal, kW=NPVFT,kW+NPVST,kW

Equation 226

NPVTotal, kWh=NPVFT,kWh+NPVST,kWh

Equation 227

Where:

NPVTotal, kW	=	Total capacity contributions to NPV of both first-tier and second-tier component

NPVTotal, kWh	=	Total energy contributions to NPV of both first-tier and second-tier component

Step 5: Calculate the capacity and energy cost contributions to the NPV without weighting by demand and energy savings for a scenario using the original EUL:

NPVEUL, kW=ACkW×1+ed-e×1-1+e1+dEUL

Equation 228

NPVEUL, kWh=ACkWh×1+ed-e×1-1+e1+dEUL

Equation 229

Where:

NPVEUL, kW	=	Capacity contributions to NPV without weighting, using original EUL

NPVEUL, kWh	=	Energy contributions to NPV without weighting, using original EUL

Step 6: Calculate the weighted demand and energy savings by dividing the combined capacity and energy cost contributions from the ER and ROB scenarios by the non-savings weighted capacity and energy cost contributions from the single EUL scenario. These weighted savings are claimed over the original measure EUL:

Weighted kW=NPVTotal. kWNPVWEUL, kW=1+ed*1-1+e1+dRUL*kWretired-kWinstalled+1+ed*1-1+e1+dEUL-RUL*1+eEUL1+dEUL*kWbaseline-kWinstalled1+ed*1-1+e1+dEUL*kWretired-kWinstalled

Equation 230

Weighted kWh=NPVTotal. kWhNPWEUL, kWh=1+ed*1-1+e1+dRUL*kWhretired-kWhinstalled+1+ed*1-1+e1+dEUL-RUL*1+eEUL1+dEUL*kWhbaseline-kWhinstalled1+ed*1-1+e1+dEUL*kWhretired-kWhinstalled

Equation 231

Where:

Weighted kW	=	Weighted lifetime demand savings

Weighted kWh	=	Weighted lifetime energy savings

NPVTotal, kW	=	Total capacity contributions to NPV of both ER and ROB component, calculated in Equation 226

NPVTotal, kWh	=	Total energy contributions to NPV of both ER and ROB component, calculated in Equation 227

NPVEUL, kW	=	Capacity contributions to NPV without weighting, using original EUL, calculated in Equation 228

NPVEUL, kWh	=	Energy contributions to NPV without weighting, using original EUL, calculated in Equation 229

Option 2—Weighting Measure Life and Holding First Year Savings Constant

Repeat Step 1 through Step 4 from Option 1.

Step 5: Reverse calculate the EUL for the capacity and energy contributions to the NPV for a scenario using the first-tier savings:

EULkW=lnNPVTotal,kW×d-eΔkWFT×ACkW×1+eln1+e1+d

Equation 232

EULkWh=lnNPVTotal,kWh×d-eΔkWhFT×ACkWh×1+eln1+e1+d

Equation 233

Where:

EULkW	=	EUL for capacity contribution to NPV using first-tier savings

EULkWh	=	EUL for energy contribution to NPV using first-tier savings

Step 6: Confirm that capacity EUL and energy EUL are equivalent. First-tier savings are claimed over this weighted EUL.

Delamping energy savings are eligible if done in conjunction with T-8 lamp and electronic ballast retrofits.

Maintained by Frontier/EUMMOT: http://texasefficiency.com/index.php/regulatory-filings/lighting.

While CEE stopped qualifying ballasts in January 2015, the NEMA Premium Electronic Ballast Program has continued to be maintained and is consistent with the prior CEE specifications for high performance lamps and ballasts, tested in accordance with ANSI C82 Standards.

DLC test lab requirements: https://www.designlights.org/solid-state-lighting/qualification-requirements/testing-lab-requirements/.

Equivalent to the L70 rated life requirement for all categories as specified in DesignLights ConsortiumTM (DLC) technical requirements v3.0, representing the point at which the minimum L70 was raised to 50,000 hours for all product categories. https://www.designlights.org/solid-state-lighting/qualification-requirements/past-technical-requirements/version-3-0-released-june-23-2015/.

Equivalent to the rated life requirement for all lamps as specified in the ENERGY STAR® lamps specification v2.1. https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Lamps%20V2.1%20Final%20Specification.pdf.

IECC 2015, Section C405.4.1.

“Energy Conservation Program: Definition for General Service Lamps”, Department of Energy. 9/5/2019. https://www.federalregister.gov/documents/2019/09/05/2019-18940/energy-conservation-program-definition-for-general-service-lamps.

Energy Independence and Security Act of 2007. https://www.govinfo.gov/content/pkg/PLAW-110publ140/pdf/PLAW-110publ140.pdf.

Changes to the DOE Federal standards for electronic ballasts effective November 2014 met both the CEE performance specification and the NEMA Premium requirements, so CEE discontinued their specification and qualifying product lists. A legacy ballast list from January 2015 is still available.

For non-operating fixtures, the baseline demand may be adjusted by using values from the Standard Wattage Table. The number of non-operating fixtures will be limited to 10% of the total fixture count per facility.

The energy and demand savings calculations should also account for lighting controls that are present on existing lighting systems. The EAF and PAF factors in the Lighting Controls measure section should be used for these calculations to adjust the deemed hours and coincidence factors on the pre side of the equations. Savings for controls installed on new fixtures are accounted for in the Lighting Controls measure.

Installed fixture wattage for fixtures defined by DLC as having “field-adjustable light output capability under the product features tab should be reported at the “default,” or maximum lumen output, setting. These fixtures may also utilize the Institutional Tuning control type. Field adjustments should be tracked in project inventories and verified with lumen measurements conducted during field inspections.

Frontier Associates Lighting Survey Form, Fixture Codes tab: http://texasefficiency.com/index.php/regulatory-filings/lighting.

IECC 2015 Table C405.4.2(1) and ANSI/ASHRAE/IESNA Standard 90.1-2013 Table 9.5.1.

IECC 2015 Table C405.5.1(2) and ANSI/ASHRAE/IESNA Standard 90.1-2013 Table 9.4.2-2. Differences between the two standards are noted.

In June 2016, the Texas Comptroller issued a state certification letter adopting ASHRAE 90.1-2013 as the energy code for state buildings while the Commercial building code remains IECC 2015. State-funded buildings are required to submit SECO compliance certificates as part of the NC/Renovation process. More details can be found at the Comptroller website: https://comptroller.texas.gov/programs/seco/code/state-funded.php. This space type is missing from the IECC 2015 LPD table, but the TRM authorizes the use of these LPDs for non-state-funded buildings.

Ibid.

ASHRAE 90.1-2013 reflects a higher baseline. The TRM specifies the higher, more conservative, baseline to allow the same LPD to apply to all buildings, regardless of whether they are state-funded.

Based on product review of LED replacement high-bay and corn lamp equivalent wattages.

DOE-EIA Commercial Building Energy Consumption Survey.

Principal Building Activities are based on sub-categories from 2003 CBECS questionnaire.

Assuming a partial summer session in June with no summer session in July.

“2015 U.S. Lighting Market Characterization”, U.S. Department of Energy. November 2017. Value derived by multiplying average daily operating hours from Table 2-30 by 365.25 hours/year.

Ibid.

This space type refers to fixtures controlled either by photocells or by timers operating on a dusk-to-dawn schedule. Calculated based on average dark hours for Amarillo (northernmost) and Corpus Christi (southernmost) climate zones from sunrise to sunset excluding ½ of civil twilight period. https://www.timeanddate.com/sun/. Note: pending update to US Naval Observatory annual data once website maintenance has completed. http://aa.usno.navy.mil/data/docs/RS_OneYear.php.

This space type refers to fixtures controlled by timers operating on a less than dusk-to-dawn schedule.

Assuming a partial summer session in June with no summer session in July.

This space type refers to fixtures controlled either by photocells or by timers operating on a dusk-to-dawn schedule.

This space type refers to fixtures controlled by timers operating on a less than dusk-to-dawn schedule.

Annual Statewide Portfolio Report for Program Year 2013 – Volume I. Prepared for the Public Utility Commission of Texas. October 6, 2014.

More information on how these values were created can be found in PUCT Docket #39146.

PUCT Docket 39146. Table 7 (page 17) and Table 12 (page 24).

These factors are only applicable for projects in climate zones 1 and 5. They are derived by taking a ratio of total HVAC energy use for spaces with evaporative and refrigerated cooling then applying that ratio against the IEF factors specified for refrigerated air.

2012 Commercial Building Energy Consumption Survey (CBECS). https://www.eia.gov/consumption/commercial/. 2018 version not available until mid-2020.

2014 Manufacturing Energy Consumption Survey (MECS). https://www.eia.gov/consumption/manufacturing/.

2015 U.S. Lighting Market Characterization, Department of Energy. November 2017. https://www.energy.gov/sites/prod/files/2017/12/f46/lmc2015_nov17.pdf.

2012 CBECS and 2014 MECS.

Weighting assumptions: 15% commercial, 85% residential applications based on review of 2015 U.S. Lighting Market Characterization, Table 4.1. Residential LEDs make up 80-84% of total general purpose and reflector lamp inventory, respectively. https://www.energy.gov/sites/prod/files/2017/12/f46/lmc2015_nov17.pdf.

Ibid.

ENERGY STAR® Lamp Center Beam Intensity Benchmark Tool. Revised September 2016. https://www.energystar.gov/products/spec/lamps_specification_version_2_0_pd.

ENERGY STAR® Light Bulbs Product Finder: https://www.energystar.gov/productfinder/product/certified-light-bulbs/results.

Ibid.

ENERGY STAR® Lamp Center Beam Intensity Benchmark Tool. Revised September 2016. https://www.energystar.gov/products/spec/lamps_specification_version_2_0_pd.

ENERGY STAR® Light Bulbs Qualified Product Listing. Accessed 7/23/2019. https://www.energystar.gov/productfinder/product/certified-light-bulbs/results.

PUCT Docket 36779.

PUCT Docket 38023.

Based on review of new construction EULs claimed by Oncor and CenterPoint during the PY 2019 and 2020 weighted by energy savings.

Ibid.

State-funded buildings are required to submit SECO compliance forms as part of the NC/renovation process. Buildings that submit SECO compliance forms are considered state-funded and must meet the provisions of ASHRAE 90.1-2013 rather than IECC 2015. Previous tables in this section present the alternative compliance values where they are encountered in the codes.

https://comptroller.texas.gov/programs/seco/code/state-funded.php. All state-funded agencies and institutions of higher education must comply with all errata sheets, as published by the ASHRAE Standard committee, so applicable values may differ from those shown in the tables as Errata are issued.

Williams, Alison, Atkinson, Barbara, Barbesi, Karina, and Rubinstein, Francis, “A Meta-Analysis of Energy Savings from Lighting Controls in Commercial Buildings”. Lawrence Berkeley National Laboratory. September 2011. Table 6, p. 14. Weighted average by number of “reviewed” and “non-reviewed” papers.

No control savings are allowed for outdoor controls because they are already required by code. ASHRAE 90.1-1989, Section 6.4.2.8 specifies that exterior lighting not intended for 24-hour continuous use shall be automatically switched by timer, photocell, or a combination of timer and photocell. This is consistent with current specifications in ASHRAE 90.1-2010, Section 9.4.1.3, which specifies that lighting for all exterior applications shall have automatic controls capable of turning off exterior lighting when sufficient daylight is available or when the lighting is not required during nighttime hours.

For multiple control types, specify the installed control types by combining the control codes for the individual control types. Savings factor based on: “Energy Savings from Networked Lighting Control (NLC) Systems”, Prepared by Energy Solutions for DesignLights Consortium. September 21, 2017. https://www.designlights.org/lighting-controls/reports-tools-resources/nlc-energy-savings-report/.

Based on review of new construction EULs claimed by Oncor and CenterPoint during the PY 2019 and 2020 weighted by energy savings.

GDS Associates. Measure Life Report—Residential and Commercial/Industrial Lighting and HVAC Measures. Prepared for the New England State Program Working Group (SPWG). June 2007. This report only specifies an EUL for Occupancy Sensors and Photocells, so it is assumed that the same EUL was applied to time clocks. http://library.cee1.org/content/measure-life-report-residential-and-Commercialindustrial-lighting-and-hvac-measures.

For a control type that combines multiple features (e.g., occupancy + daylighting), specify the installed control types by combining the control codes for the individual control types.

https://comptroller.texas.gov/programs/seco/code/state-funded.php. All state-funded agencies and institutions of higher education must comply with all errata sheets, as published by the ASHRAE Standard committee, so applicable values may differ from those shown in the tables as Errata are issued.

Current federal standards for traffic and pedestrian signals can be found at the DOE website at: https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=12.

Memorandums related to this decision can be found on the ENERGY STAR website at: https://www.energystar.gov/index.cfm?c=archives.traffic_signal_spec.

Maximum wattage is the wattage at which power consumed by the module after being operated for 60 minutes while mounted in a temperature testing chamber so that the lensed portion of the module is outside the chamber, all portions of the module behind the lens are within the chamber at a temperature of 74 °C, and the air temperature in front of the lens is maintained at a minimum of 49 °C.

Nominal wattage is defined as power consumed by the module when it is operated within a chamber at a temperature of 25 °C after the signal has been operated for 60 minutes.

Northwest Power and Conservation Council: Regional Technical Forum. Commercial LED Traffic Signals measure workbook. Version 2.2 updated 6/29/2016. http://rtf.nwcouncil.org/measures/measure.asp?id=114&decisionid=37.

Traffic signals operate consistently during each hour of the year. Therefore, CFs are calculated by dividing the assumed AOH value by 8,760 hours/year.

Northwest Power and Conservation Council: Regional Technical Forum. Commercial LED Traffic Signals measure workbook. Version 2.2 updated 6/29/2016. http://rtf.nwcouncil.org/measures/measure.asp?id=114&decisionid=37.

Based on ENERGY STAR® HVAC Maintenance Checklist. www.energystar.gov/index.cfm?c=heat_cool.pr_maintenance.

Code specified EER and HSPF value from ASHRAE 90.1-2010 (efficiency value effective January 23, 2006 for units < 65,000 Btu/hr and prior to January 1, 2010 for units ≥ 65,000 Btu/hr). HSPF = from COP x 3.412.

Code specified HSPF from federal standard effective January 23, 2006, through January 1, 2015.

Code specified 13 SEER from federal standard effective January 23, 2006, through January 1, 2015, converted to EER using EER = -0.02 x SEER2 + 1.12 x SEER. National Renewable Energy Laboratory (NREL). “Building America House Simulation Protocols.” U.S. Department of Energy. Revised October 2010. http://www.nrel.gov/docs/fy11osti/49246.pdf.

Energy Center of Wisconsin, May 2008; “Central Air-Conditioning in Wisconsin, A Compilation of Recent Field Research.”

GDS Associates, Inc. (2007). Measure Life Report: Residential and Commercial/Industrial Lighting and HVAC Measures. Prepared for The New England State Program Working Group; Page 1-3, Table 1.

2014 California Database for Energy Efficiency Resources. http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx.

Ibid.

Air-Conditioning, Heating, and Refrigeration Institute (AHRI) Directory: https://www.ahridirectory.org/.

Department of Energy Compliance Certification Management System (DOE CCMS): https://www.regulations.doe.gov/certification-data/.

The actual age should be determined from the nameplate, building prints, equipment inventory list, etc. and whenever possible the actual source used should be identified in the project documentation.

As noted in Docket 40885, page 14-15: Failure probability weights are established by assuming that systems for which age information will be unavailable are likely to be older, setting a minimum age threshold, and using the survival functions for the relevant system type to estimate the likelihood that an operational system is of a given age beyond that threshold. Baseline efficiency for each year of system age is established relative to program year. Baseline efficiency levels can be estimated for the next ten program years, considering increments in efficiency standards that took place in the historical period.

The standards do not include an EER requirement for this size range, so the code specified SEER value was converted to EER using EER = -0.02 x SEER2 + 1.12 x SEER. National Renewable Energy Laboratory (NREL). “Building America House Simulation Protocols.” U.S. Department of Energy. Revised October 2010. http://www.nrel.gov/docs/fy11osti/49246.pdf

Ibid.

Baseline EER values shown from ASHRAE/IECC assume Natural Gas heating for the predominant heating section type expected for Commercial facilities in Texas. For units installed from 2002 to present, 0.2 EER may be added for “Electric Resistance (or None)” heating types. For units installed before 2002 and greater than or equal to 11.3 tons, 0.2 EER may be added for no heating.

IEER values were not added to the Standard until 2010, so IEERs for prior years are approximated as EER + 0.2 for systems between 5.4 tons and less than 20 tons and as EER + 0.1 for systems greater than 20 tons based on the relationship of EER to IEER from the current federal standard.

Baseline IEER values shown from ASHRAE/IECC assume Natural Gas heating for the predominant heating section type expected for Commercial facilities in Texas. For units installed from 2002 to present, 0.2 IEER may be added for “Electric Resistance (or None)” heating types. For units installed before 2002 and greater than or equal to 11.3 tons, 0.2 IEER may be added for no heating.

The standards do not include an EER requirement for this size range, so the code specified SEER value was converted to EER using EER = -0.02 x SEER2 + 1.12 x SEER. National Renewable Energy Laboratory (NREL). “Building America House Simulation Protocols.” U.S. Department of Energy. Revised October 2010. http://www.nrel.gov/docs/fy11osti/49246.pdf.

Ibid.

Baseline EER values shown from ASHRAE/IECC assume Electric Resistance as the predominant heating section type expected for Commercial facilities in Texas. For units installed from 2002 to present, 0.2 EER may be subtracted for all other heating section types. For units installed before 2002 and greater than or equal to 11.3 tons, 0.2 EER may be subtracted for no heating.

IEER values were not added to the Standard until 2010, so IEERs for prior years are approximated as EER + 0.2 for systems between 5.4 tons and less than 20 tons and as EER + 0.1 for systems greater than 20 tons based on the relationship of EER to IEER from the current federal standard.

Baseline IEER values shown from ASHRAE/IECC assume Electric Resistance as the predominant heating section type expected for Commercial facilities in Texas. For units installed from 2002 to present, 0.2 IEER may be subtracted for all other heating section types. For units installed before 2002 and greater than or equal to 11.3 tons, 0.2 IEER may be subtracted for no heating.

IECC 2015 Table C403.2.3(1) and C403.2.3(2).

These baseline efficiency standards noted as “DOE Standards” are cited in the Code of Federal Regulations, 10 CFR 431.97. http://www.gpo.gov/fdsys/pkg/CFR-2012-title10-vol3/pdf/CFR-2012-title10-vol3-sec431-97.pdf.

There is no code specified EER for this size category. The code specified SEER value was converted to EER using EER = -0.02 x SEER2 + 1.12 x SEER for systems < 5.4 tons. National Renewable Energy Laboratory (NREL). “Building America House Simulation Protocols.” U.S. Department of Energy. Revised October 2010. http://www.nrel.gov/docs/fy11osti/49246.pdf.

IECC 2015 Table C403.2.3(1) and C403.2.3(2).

ASHRAE 90.1-2010 Table 6.8.1B. These systems larger than 5.4 tons, the minimum efficiency levels provided in this table are based on systems with heating type “No Heating or Electric Resistance Heating”, excluding systems with “All Other Types of Heating”.

There is no code specified EER for this size category. The code specified SEER value converted to EER using EER = -0.02 x SEER2 + 1.12 x SEER for systems < 5.4 tons. National Renewable Energy Laboratory (NREL). “Building America House Simulation Protocols.” U.S. Department of Energy. Revised October 2010. http://www.nrel.gov/docs/fy11osti/49246.pdf.

Heat pump retrofits must also exceed the baseline efficiency levels for heating efficiencies.

ENERGY STAR® Heating & Cooling, https://www.energystar.gov/products/heating_cooling.

CEE Program Resources, http://www.cee1.org/content/cee-program-resources.

From PUCT Docket #41070.

The Commercial Building Energy Consumption Survey (CBECS) implemented by the US Energy Information Administration includes a principal building activity categorization scheme that separates the Commercial sector into 29 categories and 51 subcategories based on principal building activity (PBA). For its purposes, the CBECS defines Commercial buildings as those buildings greater than 1,000 square feet that devote more than half of their floorspace to activity that is neither residential, manufacturing, industrial, nor agricultural. The high-level building types adopted for the TRM are adapted from this CBECS categorization, with some building types left out and one additional building type—Large Multifamily—included. https://www.eia.gov/consumption/commercial/.

Principal Building Activities are based on sub-categories from 2003 CBECS questionnaire.

Building prototype information from DOE Commercial Reference Buildings, “Not specified” means that a building prototype is not defined for that building type. http://energy.gov/eere/buildings/Commercial-reference-buildings, last accessed 10/20/2015.

For heat pump projects without explicit heating factors, implementers may use the listed heating factors from the “Other” building type for heating energy/demand savings.

For heat pump projects without explicit heating factors, implementers may use the listed heating factors from the “Other” building type for heating energy/demand savings.

For heat pump projects without explicit heating factors, implementers may use the listed heating factors from the “Other” building type for heating energy/demand savings.

For heat pump projects without explicit heating factors, implementers may use the listed heating factors from the “Other” building type for heating energy/demand savings.

For heat pump projects without explicit heating factors, implementers may use the listed heating factors from the “Other” building type for heating energy/demand savings.

The EUL of 15 years has been cited in several places - PUCT Docket No. 36779, DOE 77 FR 28928, 10 CFR Part 431, and in the DEER 2014 update. http://www.deeresources.com/.

PUCT Docket No. 40083, Attachment A describes the process in which the RUL of replaced systems has been calculated.

Current New Construction baseline matches the baseline for existing systems manufactured in 2018. Existing systems manufactured after 1/1/2018 are not eligible to use the early retirement baseline.

RULs are capped at the 75th percentile of equipment age, 18 years, as determined based on DOE survival curves. Systems older than 18 years should use the ROB baseline. See the January 2015 memo, “Considerations for early replacement of residential equipment,” for further detail.

Savings can also be claimed by a retrofit involving a change in equipment type (e.g., air cooled packaged DX system to a water-cooled centrifugal chiller, or a split system air cooled heat pump to an air-cooled non-centrifugal chiller). If this type of retrofit is performed, reference the tables from the following HVAC measure templates: HVAC-Chillers, Split System/Single Packaged Heat Pumps, and Air Conditioners

Air-Conditioning, Heating, and Refrigeration Institute (AHRI) Directory: https://www.ahridirectory.org/.

Department of Energy Compliance Certification Management System (DOE CCMS): https://www.regulations.doe.gov/certification-data/.

The actual age should be determined from the nameplate, building prints, equipment inventory list, etc. and whenever possible the actual source used should be identified in the project documentation.

IECC 2015 not enforced in Texas until program year 2018.

Code-specified efficiencies in effect prior to 2002 were given in COP and have been converted to EER using EER = COP x 3.412. Values in the “< 2001” row have been converted and are expressed in italics.

Ibid.

Ibid.

Ibid.

Ibid.

Ibid.

According to ASHRAE 90.1-2007 Addenda M, Path A is intended for applications where significant operating time is expected at full-load conditions, while Path B is an alternative set of efficiency levels for water-cooled chillers intended for applications where significant time is spent at part-load operation (such as with a VSD chiller).

IECC 2015 Table C403.2.3(7).

From PUCT Docket #41070.

This extra adjustment is noted in PUCT Docket No. 41070.

The Commercial Building Energy Consumption Survey (CBECS) implemented by the US Energy Information Administration includes a principal building activity categorization scheme that separates the Commercial sector into 29 categories and 51 subcategories based on principal building activity (PBA). For its purposes, the CBECS defines Commercial buildings as those buildings greater than 1,000 square feet that devote more than half of their floorspace to activity that is neither residential, manufacturing, industrial, nor agricultural. The high-level building types adopted for the TRM are adapted from this CBECS categorization, with some building types left out and one additional building type—Large Multifamily—included. https://www.eia.gov/consumption/commercial/.

Coefficient values are derived from the petitions filed in Docket 40885 and Docket 30331. Coefficients were updated with Docket 40885, but not all building types (herein “principal building activities,” or PBAs) that were originally available in Docket 30331 were updated in Docket 40885. Coefficient values for those PBAs that were not updated in Docket 40885 remain valid.

Ibid.

Ibid.

Ibid.

Ibid.

PUCT Docket No. 36779. The original source was DEER 2008, but DEER 2014 provides the same value of 20 years for “High Efficiency Chillers”. DEER does not differentiate between centrifugal and non-centrifugal chillers.

PUCT Docket No. 40885, review of multiple studies looking at the lifetime of centrifugal chillers as detailed in petition workpapers.

PUCT Docket No. 40885, Attachment A describes the process in which the RUL of replaced systems has been calculated.

Current New Construction baseline matches the baseline for existing systems manufactured in 2018. Existing systems manufactured after 1/1/2018 are not eligible to use the early retirement baseline.

RULs are capped at the 75th percentile of non-centrifugal equipment age, 24 years, as determined based on DOE survival curves. Non-centrifugal systems older than 24 years should use the ROB baseline. See the January 2015 memo, “Considerations for early replacement of residential equipment,” for further detail.

Ibid.

Air-Conditioning, Heating, and Refrigeration Institute (AHRI) Directory: https://www.ahridirectory.org/.

Department of Energy Compliance Certification Management System (DOE CCMS): https://www.regulations.doe.gov/certification-data/.

The actual age should be determined from the nameplate, building prints, equipment inventory list, etc. and whenever possible the actual source used should be identified in the project documentation.

As noted in Docket 40885, page 14-15: Failure probability weights are established by assuming that systems for which age information will be unavailable are likely to be older, setting a minimum age threshold, and using the survival functions for the relevant system type to estimate the likelihood that an operational system is of a given age beyond that threshold. Baseline efficiency for each year of system age is established relative to program year. Baseline efficiency levels can be estimated for the next ten program years, considering increments in efficiency standards that took place in the historical period.

ER only applies to Standard Size units because the minimum efficiency requirements for Non-Standard systems have never changed, making the ER baseline efficiency the same as for ROB.

IECC 2015 Table C403.2.3(3).

Cap refers to the rated cooling capacity in Btuh. If the capacity is less than 7,000 Btuh, use 7,000 Btuh in the calculation. If the capacity is greater than 15,000 Btuh, use 15,000 Btuh in the calculation.

Direct final rule for new Room Air Conditioner Standards was published on April 21st, 2011 (76 FR 22454), effective August 19th, 2011, and are required starting June 1st, 2014. These are found in 10 CFR Part 430.

Modified from PUCT Docket #41070 for TRMv3 to limit replacement of only smaller-sized units and extend Early Retirement to cover PTAC/PTHP.

Rated efficiency is commonly reported at both 230V and 208V. Savings calculations should reference efficiency at 230V, as AHRI rating conditions specify that voltage.

Ibid.

http://www.deeresources.com/

Technical Support Document: Room Air Conditioners, June 2020, p. ES-14. https://beta.regulations.gov/document/EERE-2014-BT-STD-0059-0013.

PUCT Docket No. 40083, Attachment A describes the process in which the RUL of replaced systems has been calculated.

Current federal standard effective date is 2/2013. Existing systems manufactured after this date are not eligible to use the early retirement baseline.

RULs are capped at the 75th percentile of equipment age, 18 years, as determined based on DOE survival curves. Systems older than 18 years should use the ROB baseline. See the January 2015 memo, “Considerations for early replacement of residential equipment,” for further detail.

National Renewable Energy Laboratory’s (NREL) National Solar Radiation Data Base: 1991- 2005 Update for Typical Meteorological Year 3 (TMY3).  Available at https://sam.nrel.gov/weather-data.html.

For AHU, a 60% minimum setpoint strategy is assumed, so any results below 60% are set to 60%. Similarly, any results greater than 100% are set to 100%.

ASHRAE 2017 Fundamentals, Ch 14 Appendix: design conditions for selected locations, 0.4% Cooling DB.

National Renewable Energy Laboratory’s (NREL) National Solar Radiation Data Base: 1991- 2005 Update for Typical Meteorological Year 3 (TMY3).  Available at https://sam.nrel.gov/weather-data.html.

PNNL, ANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual, page 3.249, pump minimum speed default.

ASHRAE 2017 Fundamentals, Ch 14 Appendix: design conditions for selected locations, 0.4% Cooling DB.

National Renewable Energy Laboratory’s (NREL) National Solar Radiation Data Base: 1991- 2005 Update for Typical Meteorological Year 3 (TMY3).  Available at https://sam.nrel.gov/weather-data.html.

PNNL, ANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual, page 3.249, pump minimum speed default.

ASHRAE 2017 Fundamentals, Ch 14 Appendix: design conditions for selected locations, 99.6% Heating DB.

https://focusonenergy.com/sites/default/files/Focus%20on%20Energy_TRM_January2015.pdf, page 225. Please note, the CFM2 coefficients in Equation 38 and Equation 39 have the wrong sign in the reference document.

PNNL, ANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual, Table 87 Default Part-load CIRC-PUMP-FPLR Coefficients – Constant Speed, no VSD.

https://focusonenergy.com/sites/default/files/Focus%20on%20Energy_TRM_January2015.pdf, page 225.

PNNL, ANSI/ASHRAE/IES Standard 90.1-2016 Performance Rating Method Reference Manual, Table 87 Default Part-load CIRC-PUMP-FPLR Coefficients – Default (VSD, No Reset).

Fan curves by control type are provided in the BPA ASD Calculator, http://www.bpa.gov/EE/Sectors/‌Industrial/‌‌Documents/ASDCalculators.xls.

The building hours of operation were noted in PUCT Docket 40668 to have been referenced from Commercial Building Energy Consumption Survey (CBECS) 2003. The specific analysis/report could not be confirmed.

Motor operation hours are building occupied hours plus 20 percent of unoccupied hours.

The “other” building type may be used when none of the listed building types apply. The values used for other are the most conservative of the listed building types.

Extracted from weather data from building models that were used to create summer peak period value used for this measure.

The Commercial Building Energy Consumption Survey (CBECS) implemented by the US Energy Information Administration includes a principal building activity categorization scheme that separates the Commercial sector into 29 categories and 51 subcategories based on principal building activity (PBA). For its purposes, the CBECS defines Commercial buildings as those buildings greater than 1,000 square feet that devote more than half of their floor space to activity that is neither residential, manufacturing, industrial, nor agricultural. The high-level building types adopted for the TRM are adapted from this CBECS categorization, with some building types left out and one additional building type—Large Multifamily—included. https://www.eia.gov/consumption/commercial/.

ET13SCE1020: Evaporative Condenser Air Pre-Coolers, Southern California Edison. December 2015. https://wcec.ucdavis.edu/wp-content/uploads/2016/06/et13sce1020_evaporative_pre-cooler_final.pdf.

Air-Conditioning, Heating, and Refrigeration Institute (AHRI) Directory: https://www.ahridirectory.org/.

Department of Energy Compliance Certification Management System (DOE CCMS): https://www.regulations.doe.gov/certification-data/.

IECC 2015 Table C403.2.3(1) and C403.2.3(2).

The Commercial Building Energy Consumption Survey (CBECS) implemented by the US Energy Information Administration includes a principal building activity categorization scheme that separates the commercial sector into 29 categories and 51 subcategories based on principal building activity (PBA). For its purposes, the CBECS defines commercial buildings as those buildings greater than 1,000 square feet that devote more than half of their floor space to activity that is neither residential, manufacturing, industrial, nor agricultural. The high-level building types adopted for the TRM are adapted from this CBECS categorization, with some building types left out and one additional building type - Large Multifamily – included.

Principal Building Activities are based on sub-categories from 2003 CBECS questionnaire.

The EUL of 15 years has been cited in several places - PUCT Docket No. 36779, DOE 77 FR 28928, 10 CFR Part 431, and in the DEER 2014 update.

Motor hp from manufacturer product specification sheets available from https://macroairfans.com/architects-engineers/ and https://www.bigassfans.com/aedownloads/. Airflow range from Kammel et al, “Design of High Volume Low Speed Fan Supplemental Cooling System in Dairy Free Stall Barns,” available at https://www.researchgate.net/publication/271433461_Design_of_high_volume_low_speed_fan_supplemental_cooling_system_in_dairy_freestall_barns, and from MacroAir Fans “Horse Barn Ventilation Systems” white paper, available at https://macroairfans.com/wp-content/uploads/2012/03/Horse-Barn-Ventilation-White-Paper.pdf.

Database of circulating fans tested by the Bioenvironmental and Structural Systems Laboratory of the Agricultural and Biological Engineering Dept., University of Illinois at Urbana-Champagne including 231 fan models by 17 manufacturers. Average efficacy ratio (CFM/watt) of single-phase, 230V circulating fans 48” diameter and larger. Available at http://www.bess.illinois.edu/currentc.asp.

Docket No. 40885 provides demand and energy savings by building type and cooling equipment for the four different climate zones.  This original petition was dated 10/29/2012.  An amended petition, dated 11/13/2012 was approved, which provides the original energy and demand coefficients (Table 2 18: CF and EFLH Values for Amarillo (Climate Zone 1) through Table 2-16, but also amended Tables (B3a through B3d and B4a through B4d).

For example, fans are turned on in dairy applications when the Temperature Humidity Index (THI) exceeds 68. The THI exceeds 68 in all the peak hours in the TMY files for all the Texas TRM Climate Zones as presented in Tables 4-5 through 4-9 of Volume 1 of this TRM.

DOE Motor Systems Tip Sheet #3 available at https://www.energy.gov/sites/prod/files/2014/04/f15/extend_motor_operlife_motor_systemts3.pdf. Accessed August 2020.

The existing associated computer room air conditioning (CRAC) unit condenser and evaporator are expected to remain in place for this measure.  If those units are also replaced, reference the CRAC measure TRM entry.

Site data are sourced from 3 data centers in Oncor territory that replaced 243 CRAH fan motors either with ECMs or retrofitted with VFDs.

Oncor site data. Average kW/hp values are weighted by measure count.

Peak coincidence factors are calculated according to the method in Section 4 of the Texas TRM Vol 1 using average hourly kW trends from Oncor site data. Summer and winter CF ranged from 0.10 to 0.12 across all climate zones, and the average value of 0.11 is used as the default input assumption for calculating demand savings.

U.S. DOE, Technical Support Document, “Energy Efficiency Program for Commercial Equipment: Energy Conservation Standards for Electric Motors”, Median of “Table 8.2.23 Average Application Lifetime”.  Download TSD at: https://www.mercatus.org/system/files/1904-AC28-TSD-Electric-Motors.pdf.  Accessed July 2020.

ENERGY STAR® Roof Products Specification. https://www.energystar.gov/products/building_products/roof_products/key_product_criteria.

As defined in proposed ASTN Standard E 1918-97.

ENERGY STAR® Certified Roofs. http://www.energystar.gov/productfinder/product/certified-roof-products/.

ENERGY STAR® Program Requirements for Roof Products v2.1. https://www.energystar.gov/ia/partners/product_specs/program_reqs/roofs_prog_req.pdf.

CRRC Rated Products Directory: https://coolroofs.org/directory.

ENERGY STAR® Roof Products Sunset Decision Memo. https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Roof%20Products%20Sunset%20Decision%20Memo.pdf.

Lawrence Berkeley National Lab Cool Roofing Material Database. https://heatisland.lbl.gov/resources/cool-roofing-materials-database. Accessed 08/2018.

ENERGY STAR® Roof Products Specification. https://www.energystar.gov/products/building_products/roof_products/key_product_criteria.

Estimates R-values are based on applicable code requirements in the year of construction.

Database for Energy Efficiency Resources (DEER), http://www.deeresources.com/.

2001 ASHRAE Handbook: Fundamentals, p. 30.39.

Values are taken from the 1997 ASHRAE Fundamentals, Chapter 29 Table 17, based on the amount of solar radiation transmitted through single-pane clear glass for a cloudless day at 32ºN Latitude for the 21st day of each month by hour of day and solar orientation. The SHG values listed above have been aggregated into daily totals for weekdays during the months of April through October.

Coincidence factors specific to Climate Zone 1 could not be calculated since utility load data are not currently available for this region. In their absence, Climate Zone 2 values may be used.

1997 ASHRAE Fundamentals, Table 29. Converted to SHGC by multiplying SC by 1.15.

Not defined in 1997 ASHRAE Fundamentals. SHGC established as conservative end of range determined by general product review.

Based on review applicable codes, including IECC 2000, 2009, and 2015.

Database for Energy Efficiency Resources (DEER), http://www.deeresources.com/.

ASHRAE Cooling and Heating Load Calculation Manual, p. 5.8. 1980.https://www.hud.gov/sites/documents/DOC_10603.PDF.

Cho, H., K. Gowri, and B. Liu, “Energy Saving Impact of ASHRAE 90.1 Vestibule Requirements: Modeling of Air Infiltration through Door Openings.” November 2010.https://www.pnnl.gov/main/publications/external/technical_reports/PNNL-20026.pdf.

TMY3 climate data.

Assuming 4-degree setback.

Ibid.

CLEAResult, “Commercial Door Air Infiltration Memo”. March 18, 2015. Average reduction in Arkansas based on test results from the CLEAResult Brush Weather Stripping Testing Method and Results (59% infiltration reduction).

This factor is applied to account for the difference between the laboratory test from the “Commercial Door Air Infiltration Memo” and the real-world ability to seal the openings around a door.  In the absence of research regarding the actual difference, this factor was set to 0.85.

2013 ASHRAE Handbook of Fundamentals; Equation 33, p. 16.11.

Database for Energy Efficient Resources, http://www.deeresources.com/.

ENERGY STAR® Program Requirements for Commercial Ovens https://www.energystar.gov/sites/default/files/Commercial%20Ovens%20Final%20Version%202.2%20Specification.pdf. Accessed07/2020.

CEE Commercial Kitchens Initiative’s overview of the Food Service Industry: https://library.cee1.org/system/files/library/4203/CEE_CommKit_InitiativeDescription_January2015.pdf. Accessed07/2020.

ENERGY STAR®. Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment. Calculator: http://www.energystar.gov/buildings/sites/default/uploads/‌‌files/Commercial‌‌_kitchen_‌‌equipment_calculator.xlsx. Accessed 07/2020

P = Pan Capacity

Pan Capacity is defined as the number of steam table pans the combination oven is able to accommodate as per the ASTM F-1495-05 standard specification.

California End Use Survey (CEUS), Building workbooks with load shapes by end use. Accessed 07/12.2012.

ENERGY STAR®. Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment Calculator: http://www.energystar.gov/buildings/sites/default/uploads/files/Commercial_kitchen_‌‌equipment_calculator.xlsx. Accessed 01/27/2015.

ENERGY STAR® Program Requirements for Commercial Ovens. https://www.energystar.gov/sites/default/files/Commercial%20Ovens%20Final%20Version%202.2%20Specification.pdf. Accessed 07/2020.

CEE Commercial Kitchens Initiative’s overview of the Food Service Industry: http://library.cee1.org/sites/default/files/library/4203/CEE_CommKit_InitiativeDescription_June2014.pdf. Accessed 07/2020.

ENERGY STAR®. Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment. Calculator: http://www.energystar.gov/buildings/sites/default/uploads/files/Commercial_kitchen_equipment_calculator.xlsx. Accessed 07/2020

California End Use Survey (CEUS), Building workbooks with load shapes by end use. Accessed 07/12/2012.

Default values in ENERGY STAR® calculator for Convection Ovens.

CEE Commercial Kitchens Initiative’s overview of the Food Service Industry: http://library.cee1.org/sites/default/files/library/4203/CEE_CommKit_InitiativeDescription_June2014.pdf. Accessed 04/30/2015.

ENERGY STAR® Program Requirements Product Specification for Commercial Dishwashers, Version 2.0. https://www.energystar.gov/products/commercial_food_service_equipment/commercial_dishwashers.

ENERGY STAR®. "Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment." Accessed 07/2020.

Low temperature machines apply a chemical sanitizing solution to the surface of the dishes to achieve sanitation.

High temperature machines apply only hot water to the surface of the dishes to achieve sanitation.

Table 125 values are provided in the ENERGY STAR® Program Requirements Product Specification for Commercial Dishwashers, Version 2.0. https://www.energystar.gov/products/commercial_food_service_equipment/commercial_dishwashers. Accessed 07/2020.

Water Consumption for pot, pan and utensil is specified in gallons per square foot rather than gallons per rack.

ENERGY STAR®. "Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment." Accessed 07/2020.

California End Use Survey (CEUS), Building workbooks with load shapes by end use. Accessed 07/12/12.

ENERGY STAR®. "Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment." Accessed 07/2020

A list of ENERGY STAR® qualified products can be found on the ENERGY STAR® website: https://www.energystar.gov/products/commercial_food_service_equipment/commercial_hot_food_holding_cabinets. Accessed 07/2020.

CEE Commercial Kitchens Initiative’s overview of the Food Service Industry: http://library.cee1.org/sites/‌‌default/‌files/library/4203/CEE_CommKit_InitiativeDescription_June2014.pdf. Accessed 07/2020.

V = Interior Volume = Interior Height x Interior Width x Interior Depth

Additionally, Table 129 is pulled from the ENERGY STAR® Program Requirements for Commercial Hot Food Holding Cabinets document, Table 1 “Maximum Idle Energy Rate Requirements for ENERGY STAR Qualification”
https://www.energystar.gov/sites/default/files/specs/private/Commercial_HFHC_Program_Requirements_2.0.pdf

Averages determined per Product Interior Volume Range classification ENERGY STAR®

Calculated as per the Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment. https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator.xlsx. Accessed 07/2020.

California End Use Survey (CEUS), Building workbooks with load shapes by end use. Accessed 07/12/12.

ENERGY STAR® measure life based on Food Service Technology Center (FSTC) research on available models, 2009. ENERGY STAR®. "Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment." https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator.xlsx. Accessed 07/2020.

ENERGY STAR® Program Requirements Product Specifications for Electric Fryers. Eligibility Criteria Version 3.0.. https://www.energystar.gov/sites/default/files/Commercial%20Fryers%20Program%20Requirements.pdf Accessed 08/2020.

CEE Commercial Kitchens Initiative’s overview of the Food Service Industry: http://library.cee1.org/sites/‌default/files/library/4203/CEE_CommKit_InitiativeDescription_June2014.pdf. Accessed 04/30/2015.

Deemed input values come from ENERGY STAR® Commercial Kitchen Equipment Calculator. https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator.xlsx. Accessed 08/2020.

California End Use Survey (CEUS), Building workbooks with load shapes by end use. Accessed 07/12/12.

Federal standards, 10 CFR 431.266. https://www.ecfr.gov/cgi-bin/text-idx?SID=2ab37ee5fbd56d810322f3adce2124c6&mc=true&node=sp10.3.431.o&rgn=div6#se10.3.431_1266

“Summary of ENERGY STAR® Specification Development Process and Rationale for PreRinse Spray Valves”. March 2006. https://www.energystar.gov/ia/partners/prod_development/downloads/PRSV_Decision_Memo_Final.pdf?1e37-d3b8

FEMP Performance Requirements for Federal Purchases of Pre-rinse Spray Valves, Based on ASTM F2324-03: Standard Test Method for Pre-rinse Spray Valves.

“CEE Commercial Kitchens Initiative Program Guidance on pre-rinse valves”, page 3. Midpoint of typical hours of operation in footnoted building types. https://library.cee1.org/system/files/library/4252/PRSV%20Program%20Guidance.pdf

Assuming that institutions (e.g., prisons, university dining halls, hospitals, nursing homes) are serving three meals a day, prorate schools by 1.5hrs to 3hrs (assuming schools serve breakfast to half of the students and lunch to all), yielding 105 minutes per day.

According to ASTM F2324-03 Cleanability Test, the optimal operating conditions are at 120°F. This test consists of cleaning a plate of dried tomato sauce in less than 21 seconds with 120 ± 4°F water at a specified distance from the plate. This test is performed at 60 ± 2 psi of flowing water pressure.

FEMP Performance Requirements for Federal Purchases of Pre-rinse Spray Valves, Based on ASTM F2324-03: Standard Test Method for Pre-rinse Spray Valves. Average calculated input water temperature for five Texas climate zone cities.

For facilities that operate year-round: assume operating days of 360 days/year; For schools open weekdays except summer: 360 x (5/7) x (9/12) = 193; For dormitories with few occupants in the summer: 360 x (9/12) = 270.

ASHRAE Handbook 2011. HVAC Applications. Chapter 50 - Service Water Heating American Society of Heating Refrigeration and Air-Conditioning Engineers, Inc. (ASHRAE) 2011. ASHRAE, Inc., Atlanta, GA. The Hourly Flow Profiles given in Figure 24 on page 50.19, were reviewed and A-85 118 analyzed. The Hourly Peak Demand as a percent of the daily flow was estimated by knowing the total daily flow, the hourly flow, and the peak demand period window.

https://www.gearteamju.com/GC/Home/Engineering/Hvac%20I/sheets/Ashrae-2011%20Hvac%20Applications%20Si%20-%20GearTeam.pdf

ENERGY STAR® Qualified Commercial Steam Cookers. List Posted on May 15, 2012. http://www.energystar.gov/ia/products/prod_lists/Steamers_prod_list.pdf. Accessed 09/09/2013.

CEE Commercial Kitchens Initiative’s overview of the Food Service Industry: http://library.cee1.org/sites/default/files/library/4203/CEE_CommKit_InitiativeDescription_June2014.pdf. Accessed 04/30/2015.

ENERGY STAR®. "Commercial Steam Cookers Key Product Criteria.". https://www.energystar.gov/products/commercial_food_service_equipment/commercial_steam_cookers/key_product_criteria. Accessed 11/13/19.

Cooking Energy Efficiency is based on “heavy load (potato) cooking capacity,” i.e. 12 by 20 by 2½ inch (300 by 500 by 65 mm) perforated hotel pans each filled with 8.0 ± 0.2 lb (3.6 ± 0.1 kg) of fresh, whole, US No. 1, size B, red potatoes

ENERGY STAR®. "Savings Calculator for ENERGY STAR® Qualified Commercial Kitchen Equipment." Accessed 09/26/11. Equipment specifications from 2009 Food Service Technology Center (FSTC) research on available models. Equipment cost from 2010 EPA research on available models using AutoQuotes. https://www.energystar.gov/sites/default/files/asset/document/commercial_kitchen_equipment_calculator.xlsx. Accessed 08/2020.

California End Use Survey (CEUS), Building workbooks with load shapes by end use. Accessed 07/12/12.

Fisher, D., Swierczyna, R., and Karas, A. (February 2013) Future of DCV for Commercial Kitchens. ASHRAE Journal, 48-53.

Food Service Technology Center Outdoor Air Load Calculator. No longer available online.

Percentage of buildings with electric resistance and heat pump heat are taken from the Energy Information Administration 2012 Commercial Buildings Energy Survey (CBECS), tables b.28 Primary space-heating energy sources and b.38 Heating equipment, using data for buildings with cooking. https://www.eia.gov/consumption/commercial/data/2012. Accessed August 2020.

The CFM per HP ratio was calculated using data from Southern California Edison, ET 07.10 Report on Demand Control Ventilation for Commercial Kitchen Hoods, June 2009.

All values are the average of Casual and Quick Service Restaurant data from Future of DCV for Commercial Kitchens.

All values are the average of Hotel Restaurant data from Future of DCV for Commercial Kitchens.

Savings and MAU are calculated as the average of University Dining data from Future of DCV for Commercial Kitchens; Hours per day and Days per year are calculated using operating hours from Table 144.

PWPLS factors are calculated according to the methods described in TRM Volume 1, Section 4.3. The load shape source is the Pacific Norhtwest National Laboratory Technical Support Document: 50% Energy Savings for Quick-Service Restaurants, Table B.4, Schedule for Kitchen exhaust flow.

CEE Commercial Kitchens Initiative’s overview of the Food Service Industry: https://library.cee1.org/system/files/library/4203/CEE_CommKit_InitiativeDescription_January2015.pdf. Accessed 07/2020.

Code of Federal Regulations, Title 10 Part 431 for air-cooled batch-type and continuous-type automatic commercial ice makers with capacities between 50 and 4,000 pounds per 24-hour period manufactured on or after January 28, 2018. https://www.law.cornell.edu/cfr/text/10/431.136

ENERGY STAR® Commercial Ice Maker Key Product Criteria Version 3.0, https://www.energystar.gov/products/commercial_food_service_equipment/commercial_ice_makers/key_product_criteria, Accessed August 2019.

A list of ENERGY STAR® qualified products can be found on the ENERGY STAR® website: https://www.energystar.gov/productfinder/product/certified-commercial-ice-machines/results

Accessed 08/2020

The assumed duty cycle value of 80% is taken from a PGE Emerging Technologies study, ET Project #ET12PGE3151 Food Service Technology—Efficient Ice Machines and Load Shifting, average duty cycle of preexisting machines in tables ES1 and ES2.

Probability weighted peak load factors are calculated according to the method in Section 4 of the Texas TRM Vol 1 using data from the EPRI Load Shape Library 6.0. ERCOT regional End Use Load Shapes for Commercial Refrigeration. Peak Season, Peak Weekday values used for summer calculations. Off Peak Season, Peak Weekday values used for winter calculations. http://loadshape.epri.com/enduse. Accessed August 2019.

Department of Energy, Energy Conservation Program: Energy Conservation Standards for Automatic Commercial Ice Makers, 80 FR 4698, https://www.federalregister.gov/d/2015-00326/p-652.

“Vacuum-Sealing and Packaging Machines for Food Service Field Test, ET13SCE1190 Report,” SCE & FTSC. December 2014. https://www.etcc-ca.com/reports/commerical-hand-wrap-machines-food-service-applications-field-test.

See Volume 1, Section 4.

“Useful Life Indices for Equipment Depreciation”, University of California Office of the President. https://eulid.ucop.edu/.

Pennsylvania TRM, “3.5.6 Controls: Anti-Sweat Heater Controls”. page 381, Table 3-101. June 2016. http://www.puc.pa.gov/pcdocs/1350348.docx. Accessed 08/2020.

Additional reference from Pennsylvania TRM: State of Wisconsin, Public Service Commission of Wisconsin, Focus on Energy Evaluation, Business Programs Deemed Savings Manual. Table 4-75., March 22, 2010. https://focusonenergy.com/sites/default/files/bpdeemedsavingsmanuav10_evaluationreport.pdf.

Pennsylvania TRM, “3.5.6 Controls: Anti-Sweat Heater Controls”. page 383, June 2016. http://www.puc.pa.gov/pcdocs/1350348.docx. Accessed 08/2020.

Additional reference from Pennsylvania TRM: State of Wisconsin, Public Service Commission of Wisconsin, Focus on Energy Evaluation, Business Programs Deemed Savings Manual. Table 4-75. March 22, 2010. https://focusonenergy.com/sites/default/files/bpdeemedsavingsmanuav10_evaluationreport.pdf.

Three door heater configurations are presented: standard, low-heat, and no-heat. The standard configuration was chosen on the assumption that low-heat and no-heat door cases will be screened from participation.

Ibid..

A Study of Energy Efficient Solutions for Anti-Sweat Heaters. Southern California Edison RTTC. December 1999.

Work Paper PGEREF108: Anti-Sweat Heat (ASH) Controls. Pacific Gas and Electric Company. May 29,2009. Assumes 15% oversizing.

ASHRAE Climatic Region Data, 0.5% (ºF).

Database for Energy Efficient Resources, EUL Table Update, February 5, 2014. Accessed 08/2020. http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx.

The Pennsylvania TRM, June 2016, utilizes the Efficiency Vermont source reproduced below this footnoted statement for an assumption of 8,273 hours for walk-in freezers. This is, furthermore, equivalent to stating the freezer’s duty cycle is approximately 94.4% (8,273 / 8,760 ≈ 0.944), an assumed value which appears in Table 155 for the DCEvapFreezer variable. The Maine TRM, July 2019, details the derivation of 8,273 and thus approximately 94.4%: “A[n] evaporator fan in a cooler runs all the time, but a freezer runs only 8,273 hours per year due to defrost cycles (4 20-min defrost cycles per day)”

- Pennsylvania TRM, “3.5.3 High-Efficiency Fan Motors for Walk-In Refrigerated Cases”. page 369, Table 3-93. June 2016. http://www.puc.pa.gov/pcdocs/1350348.docx.

- Efficiency Vermont, Technical Reference Manual 2009-54, 12/08. Hours of operation accounts for defrosting periods where motor is not operating. http://www.greenmountainpower.com/upload/photos/371TRM_User_Manual_No_2013-82-5-protected.pdf

- Efficiency Maine, Commercial/Industrial and Multifamily Technical Reference Manual 2020.1, July 1, 2019. Page 83, footnote 401.

The Massachusetts Technical Reference Manual, 2012 Program Year – Plan Version, “Refrigeration – Evaporator Fan Controls”, October 2011. Page 216, footnote 414 cites the following as the source for this variable:

“The value is an estimate by National Resource Management (NRM) based on extensive analysis of hourly use data. These values are also supported by Select Energy (2004). Cooler Control Measure Impact Spreadsheet User's Manual. Prepared for NSTAR.”

The Pennsylvania TRM, June 2016, cites the following as the source for determining the load factor of the evaporator fan motor:

“ActOnEnergy; Business Program-Program Year 2, June 2009 through May 2010. Technical Reference Manual, No. 2009-01.” Published 12/15/2009.

Pennsylvania TRM, “3.5.2 High-Efficiency Fan Motors for Reach-In Refrigerated Cases”. page 365, Table 3-89. June 2016. http://www.puc.pa.gov/pcdocs/1350348.docx.

Efficiency Maine, Commercial/Industrial and Multifamily Technical Reference Manual 2020.1, July 1, 2019. Page 83, footnote 401

See Footnotes 1 and 4

See Footnote 1 for the explanation of the assumption of 8,273 for walk-in freezers.

The first three rows in this table are sourced from the Pennsylvania TRM, June 2016.

Pennsylvania TRM, “3.5.2 High-Efficiency Fan Motors for Reach-In Refrigerated Cases”. page 366, Table 3-90. June 2016. http://www.puc.pa.gov/pcdocs/1350348.docx

The last two rows are estimated using logarithmic linear regression of smaller motor efficiencies.

2017 ASHRAE Handbook: Fundamentals, 0.4% summer design dry-bulb temperatures. http://ashrae-meteo.info/v2.0/.

Database for Energy Efficient Resources, EUL Table Update, February 5, 2014. Accessed 08/2020. http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx.

Southern California Edison, Anti-Sweat Heat (ASH) Controls Work Paper WPSCNRRN009 (rev.o.2007).

Ibid.

Energy and Resource Solutions (2005). Measure Life Study. Prepared for The Massachusetts Joint Utilities. https://www.ers-inc.com/wp-content/uploads/2018/04/Measure-Life-Study_MA-Joint-Utilities_ERS.pdf.

The Maine Technical Reference Manual was utilized to determine all of these assumed values.

Efficiency Maine, Commercial/Industrial and Multifamily Technical Reference Manual 2020.1, July 1, 2019.

- kWevap: Page 78, footnote 366 states this value is determined “based on a weighted average of 80% shaded-pole motors at 132 watts and 20% PSC motors at 88 watts. This weighted average is based on discussions with refrigeration contractors and is considered conservative (market penetration estimated at approximately 10%).”

- kWcirc: Page 78, footnote 367 states this value is the “wattage of fan used by Freeaire and Cooltrol”

- DCcomp: Page 78, footnote 368 states the reasoning for this value as follows: “A 50% duty cycle is assumed based on examination of duty cycle assumptions from Richard Traverse (35%-65%), Control (35%-65%), Natural Cool (70%), Pacific Gas and Electric (58%). Also, manufacturers typically size equipment with a built-in 67% duty factor and contractors typically add another 25% safety factor, which results in a 50% overall duty factor.”

- DCevap: 94.4% is equivalent to 8,273 / 8,760 annual operating hours. The assumption of 8,273 is the annual total of the assumption that “a[n] evaporator fan in a cooler runs all the time, but a freezer only runs 8273 hours per year due to defrost cycles (4 20-min defrost cycles per day)”, an explanation given on page 82, footnote 401.

- BF: Page 183, Table 45, footnote A summarizes the Bonus Factor (-1 + 1/COP) as “assum[ing] 2.0 COP for low temp, 3.5 COP for medium temp, and 5.4 COP for high temp, based on the average of standard reciprocating and discus compressor efficiencies with Saturated Suction Temperatures of -20°F, 20°F, and 45°F, respectively, and a condensing temperature of 90°F.”

Database for Energy Efficient Resources, EUL Table Update, February 5, 2014. Accessed 08/2020. http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx.

Faramarzi, R. “Practical Guide: Efficient Display Case Refrigeration”, 1999 ASHRAE Journal, Vol. 41, November 1999.

ASHRAE 2018. Refrigeration Handbook. Retail Food Store Refrigeration and Equipment. Atlanta, Georgia. p. 15.6.

Ibid.

Ibid., p. 15.26

2004-2005 Database for Energy Efficiency Resources (DEER) Update Study. 2005. Run ID D03- 205. The EM&V team, Inc. p. 7-74 and 7-75. DEER.

ASHRAE 2009 Handbook Fundamentals.

Southern California Edison, Anti-Sweat Heat (ASH) Controls Work Paper WPSCNRRN009 (rev.0.2007).

Compressor capacity is determined by multiplying baseline cooling load by a compressor over-sizing factor of 15 percent.

Work Paper PGEREF108: Anti-Sweat Heat (ASH) Controls. Pacific Gas and Electric Company. May 29,2009.

PUCT Docket No. 40669, page A-2 states that Amarillo, Texas was chosen as a conservative climate zone due to little variation between climate zones. This statement has not been expanded upon.

Database for Energy Efficient Resources, EUL Table Update, February 5, 2014. Accessed 08/2020. http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx.

https://www.ecfr.gov/cgi-bin/text-idx?SID=ea9937006535237ca30dfd3e03ebaff2&mc=true&node=se10.3.431_166&rgn=div8

V = Interior volume [ft3] of a refrigerator or freezer (as defined in the Association of Home Appliance Manufacturers Standard HRF1-1979).

ENERGY STAR® Program Requirements for Commercial Refrigerators and Freezers Partner Commitments Version 4.0, U.S. Environmental Protection Agency. Accessed 08/2020. https://www.energystar.gov/sites/default/files/Commercial%20Refrigerators%20and%20Freezers%20V4%20Spec%20Final%20Version_0.pdf.

The summer peak coincidence factor is assumed equal to 1.0, since the annual kWh savings is divided by the total annual hours (8,760), effectively resulting in the average kW reduction during the peak period.

Database for Energy Efficient Resources, EUL Table Update, February 5, 2014. Accessed 08/2020. http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx.

Values based on analysis prepared by ADM for FirstEnergy utilities in Pennsylvania, provided by FirstEnergy on June 4th, 2010. Based on a review of deemed savings assumptions and methodologies from Oregon and California.

Database for Energy Efficient Resources, EUL Table Update, February 5, 2014. Accessed 08/2020. http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx.

Here, “medium temperature” is equivalent to the categorization “coolers”.
(Pennsylvania TRM) State of Wisconsin, Public Service Commission of Wisconsin, Focus on Energy Evaluation, Business Programs Deemed Savings Manual. Table 4-75.March 22, 2010. https://focusonenergy.com/sites/default/files/bpdeemedsavingsmanuav10_evaluationreport.pdf.

This prior source appears to have furthermore been sourced from the Pennsylvania TRM, June 2016, which states that “Three door heater configurations are presented: standard, low-heat, and no-heat. The standard configuration was chosen on the assumption that low-heat and no-heat door cases will be screened from participation.”

Pennsylvania TRM, “3.5.6 Controls: Anti-Sweat Heater Controls”. page 383, June 2016. http://www.puc.pa.gov/pcdocs/1350348.docx. Accessed 08/2020.

Ibid. (Here, “low temperature” is equivalent to the categorization “freezers”.)

A Study of Energy Efficient Solutions for Anti-Sweat Heaters. Southern California Edison RTTC. December 1999.

Work Paper PGEREF108: Anti-Sweat Heat (ASH) Controls. Pacific Gas and Electric Company. May 29, 2009. Assumes 15% oversizing.

2017 ASHRAE Handbook: Fundamentals, 0.4% summer design dry-bulb temperatures. http://ashrae-meteo.info/v2.0/.

Ibid., 0.4% DP

Database for Energy Efficient Resources, EUL Table Update, February 5, 2014. Accessed 08/2020. http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx.

Gasket efficacy is defined as the ratio of the gasket length that was removed by the installers to the gasket length that was replaced. A 90 percent gasket efficacy translates to an average of 10 percent of missing, badly damaged or ineffective gasket by length replaced.

Southern California Edison (SCE). WPSCNRRN0013—Door Gaskets for Glass Doors of Medium and Low Temperature Reach-in Display Cases and Solid Doors of Reach-in Coolers and Freezers. 2007.

Commercial Facilities Contract Group (ComFac), 2006-2008 Direct Impact Evaluation Study ID: PUC0016.01. February 18, 2010.

https://energy.mo.gov/sites/energy/files/comfac_evaluation_v1_final_report_02-18-2010.pdf.

Ibid., Table 5-3

The SCE ex-ante savings as reported in the PG&E report were 10.2 and 21.7 kWh/linear foot for coolers and freezers respectively.

Commercial Facilities Contract Group (ComFac), 2006-2008 Direct Impact Evaluation Study ID: PUC0016.01. February 18, 2010. Table 5-3. https://energy.mo.gov/sites/energy/files/comfac_evaluation_v1_final_report_02-18-2010.pdf.

Modeled savings as reported in the SCE report for climate zone 4 were approximately 6 and 15 kWh/linear foot for coolers and freezers respectively.

https://gds-files.nrelcloud.org/rredc/1991-2005.zip

Database for Energy Efficient Resources, EUL Table Update, February 5, 2014. Accessed 08/2020. http://www.deeresources.com/files/DEER2013codeUpdate/download/DEER2014-EUL-table-update_2014-02-05.xlsx.

Appliance Standards for Refrigerated Beverage Vending Machines. https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=29#current_standards.

Pacific Gas and Electric, Work Paper VMCold, Revision 3, August 2009, Measure Code R97.

Chappell, C., Hanzawi, E., Bos, W., Brost, M., and Peet, R. (2002). "Does It Keep the Drinks Cold and Reduce Peak Demand? An Evaluation of a Vending Machine Control Program," 2002 ACEEE Summer Study on Energy Efficiency in Buildings Proceedings, pp. 10.47-10.56. https://www.eceee.org/static/media/uploads/site-2/library/conference_proceedings/ACEEE_buildings/2002/Panel_10/p10_5/paper.pdf.

Pacific Gas and Electric, Work Paper VMReach, Revision 3, August 2009, Measure Code R143.

Pacific Gas and Electric, Work Paper VMSnack, Revision 3, August 2009, Measure Code R98.

Database for Energy Efficiency Resources (DEER), http://www.deeresources.com/.

The original petition also includes savings for HVAC-only control in master-metered multifamily individual dwelling units. These values are not reported here because the permanent occupation of a residential unit is significantly different from the transitory occupation of hotel/motels and even dormitories. This measure is not currently being implemented and is not likely to be used in the future, but it can be added to a future TRM if warranted.

HVAC occupancy rates appear to be based on a single HVAC study of three hotels, but not dorms or multifamily buildings. For the lighting study, a typical guest room layout was used as the basis for the savings analysis. Hotel guest rooms are quite different from either dorms or multifamily units.

A more detailed description of the modeling assumptions can be found in Docket 40668 Attachment A, pages A-46 through A-58.

Regions used in the original petition were mapped to current TRM representative weather stations and regions as follows: Amarillo (Panhandle) was “Panhandle”, Dallas-Ft Worth (North) was “North”, Houston (South) was “South Central”, El Paso (West) was “Big Bend”, and McAllen (Valley) was “Rio Grande Valley”.

Energy and Resource Solutions (2005). Measure Life Study. Prepared for the Massachusetts Joint Utilities; Table 1-1, Prescriptive Common Measure Life Recommendations, Large C&I retrofit, HVAC Controls, EMS.

Fluid pounding occurs when the downhole pump rate exceeds the production rate of the formation. The pump strikes the top of the fluid column on the down stroke causing extreme shock loading of the components which can result in premature equipment failure.

The API number is a unique, permanent identifier assigned by the American Petroleum Institute. The API number should correspond to a well that was in existence prior to the date of PUCT Docket 42551.

Bullock, J.E. “SPE 16363 Electrical Savings in Oil Production”, (paper presented at the Society of Petroleum Engineers California Regional Meeting held in Ventura, California, April 8-10, 1987).

2006-2008 Evaluation Report for PG&E Fabrication, Process and Manufacturing Contract Group. CALMAC Study ID: CPU0017.01. Itron, Inc. Submitted to California Public Utilities Commission. February 3, 2010.

The EM&V Team will work with SPS/Xcel Energy in developing the sample plan for the field data collection effort.

The equations in the petition for peak demand simplify to the equation shown.

This equation from the petition deviates from that in SPE 16363 but will provide conservative savings estimates. The equation will be updated and made consistent when this measure is updated with field data. The correct equation term is (Runcontstant + Runcoefficient * VolumetricEfficiency%) with the volumetric efficiency expressed as percent value not a fraction (i.e., 25 not 0.25 for 25%).

Bullock, J.E. “SPE 16363 Electrical Savings in Oil Production, (paper presented at the Society of Petroleum Engineers California Regional Meeting held in Ventura, California, April 8-10, 1987).

Comprehensive Process and Impact Evaluation of the (Xcel Energy) Colorado Motor and Drive Efficiency Program, FINAL. Tetra Tech. March 28, 2011. Adjusted based on Field Measurements provided by ADM Associates, based on 2010 custom projects.

Engineering estimate for standard gearbox efficiency.

A TimeClock%On of 80% is typical from observations in other jurisdictions, but that was adjusted to 65% for a conservative estimate. This value will be reevaluated once Texas field data is available.

DOE Final Rule regarding energy conservation standards for electric motors. 79 FR 30933. Full-load Efficiencies for General Purpose Electric Motors [Subtype I] https://www1.eere.energy.gov/buildings/appliance_standards/standards.aspx?productid=6&action=viewlive.

CPUC 2006-2008 Industrial Impact Evaluation "SCIA_06-08_Final_Report_Appendix_D-5": An EUL of 15 years was used for the ex-post savings, consistent with the SPC—Custom Measures and System Controls categories in the CPUC Energy Efficiency Policy Manual (Version 2) and with DEER values for an energy management control system.

Per PUCT Docket 42551, Southwestern Public Service Company (SPS)/Xcel Energy has agreed to collect field data in 2015 on post-run times for a sample of wells to improve the accuracy of POC saving estimates.

These pump products are ineligible for ENERGY STAR® v3.0 certification: https://www.energystar.gov/sites/default/files/ENERGY%20STAR%20Final%20Version%203.0%20Pool%20Pumps%20Specification.pdf

Hunt, A. and Easley, S., , “Measure Guideline: Replacing Single-Speed Pool Pumps with Variable Speed Pumps for Energy Savings.” Building America Retrofit Alliance (BARA), U.S. U.S. DOE. May 2012. http://www.nrel.gov/docs/fy12osti/54242.pdf.

The ENERGY STAR® Pool Pump Savings Calculator, updated May 2020, can be found on the ENERGY STAR® website at: https://www.energystar.gov/productfinder/downloads/Pool_Pump_Calculator_2020.05.05_FINAL.xlsx, Accessed July 2020.

Conventional pump PFR and EF values are taken from pump curves found in the ENERGY STAR® Pool Pump Savings Calculator.

Limited Hours assumes that pump operating hours are 12 hours per day, based on 2016 Commercial pool pump program data reviewed by the Texas Evaluation Contractor.

ENERGY STAR® values are taken from default inputs and pump curves found in the ENERGY STAR® Pool Pump Savings Calculator.

Based on 2016 Commercial pool pump program data reviewed by the Texas Evaluation Contractor.

The results in this table may vary slightly from results produced by the ENERGY STAR® calculator because of rounding of default savings coefficients throughout the measure and pool volume.

Ibid.

Database for Energy Efficient Resources (2014). http://www.deeresources.com/.

ENERGY STAR® Low Carbon IT Calculator available for download at: https://www.energystar.gov/products/low_carbon_it_campaign/put_your_computers_sleep.

Based on 2015 custom project metering from El Paso Electric.

Based on 2015 custom project metering from El Paso Electric.

Equipment wattages taken from the Low Carbon IT Savings Calculator, downloaded 07/27/2020.  https://www.energystar.gov/sites/default/files/asset/document/LowCarbonITSavingsCalc.xlsx

Average of 17.0-24.9 inches monitor sizes taken from the ENERGY STAR® Office Equipment Calculator.

Hours taken from assumptions in the ENERGY STAR® calculator. Hourspre assume baseline computer settings never enter sleep mode, and 60% of computers are turned off each night. Hourspost assume managed computer settings enter sleep mode after 15 minutes of inactivity, and 80% of computers are turned off each night.

Internal Revenue Service, 1.35.6.4 (09-27-2019), Property and Equipment Capitalization, Useful life for Laptop and Desktop Equipment. https://www.irs.gov/irm/part1/irm_01-035-006 . Accessed July 2020.

Federal Standards for Electric Motors, Table 1: Nominal Full-load Efficiencies of General Purpose Electric Motors (Subtype I), Except Fire Pump Electric Motors, https://www.ecfr.gov/cgi-bin/retrieveECFR?n=pt10.3.431#sp10.3.431.b. Accessed July 2020.

Federal Standards for Electric Motors, Table 4: Nominal Full-load Efficiencies of NEMA Design B General Purpose Electric Motors (Subtype I and II), Except Fire Pump Electric Motors, https://www.ecfr.gov/cgi-bin/retrieveECFR?n=pt10.3.431#sp10.3.431.b. Accessed July 2020.

Federal Standards for Electric Motors, Tables 3 (≤ 200 hp), and 4 (> 200hp),

https://www.ecfr.gov/cgi-bin/retrieveECFR?n=pt10.3.431#sp10.3.431.b. Accessed July 2020.

Assumes 3-shift operating schedule

U.S. DOE, Technical Support Document, “Energy Efficiency Program for Commercial Equipment: Energy Conservation Standards for Electric Motors, 10.2.2.1 Motor Capacity”.  Download TSD at: https://www.mercatus.org/system/files/1904-AC28-TSD-Electric-Motors.pdf. Accessed July 2020.

In the case of rewound motors, in-situ efficiency may be reduced by a percentage as found in Table 203

Itron 2004-2005 DEER Update Study, Dec 2005; Table 3-25. Accessed July 2020. http://deeresources.com/files/deer2005/downloads/DEER2005UpdateFinalReport_ItronVersion.pdf

Commercial Prototype Building Models HVAC operating schedules for hours ending 15-18. U.S. Department of Energy. https://www.energycodes.gov/development/commercial/prototype_models. Accessed July 2020.

Factors are equivalent to Table 74 Yearly Motor Operation Hours by Building Type for HVAC Frequency Drives.

United States Industrial Electric Motor Systems Market Opportunities Assessment, Dec 2002; Table 1-19. Accessed 07/2020. https://www1.eere.energy.gov/manufacturing/tech_assistance/pdfs/mtrmkt.pdf

United States Industrial Electric Motor Systems Market Opportunities Assessment, Dec 2002; Table 1-15. Accessed 07/2020. https://www1.eere.energy.gov/manufacturing/tech_assistance/pdfs/mtrmkt.pdf

U.S. DOE, Technical Support Document, “Energy Efficiency Program for Commercial Equipment: Energy Conservation Standards for Electric Motors, 8.2.2.1 Annual Energy Consumption”. Download TSD at: https://www.mercatus.org/system/files/1904-AC28-TSD-Electric-Motors.pdf. Accessed July 2020.

Federal Standards for Electric Motors, Tables 1 and 5,

https://www.ecfr.gov/cgi-bin/retrieveECFR?n=pt10.3.431#sp10.3.431.b. Accessed July 2020.

Current federal standard effective date is 12/19/2010. Existing systems manufactured after this date are not eligible to use the early retirement baseline.

RULs are capped at the 75th percentile of equipment age, 17 years, as determined based on DOE survival curves (see Figure 5). Systems older than 17 years should use the ROB baseline. See the January 2015 memo, “Considerations for early replacement of residential equipment,” for further detail.

Department of Energy, Federal Register, 76 Final Rule 57516, Technical Support Document: 8.2.3.1 Estimated Survival Function. September 15, 2011. Accessed July 2020. http://www1.eere.energy.gov/buildings/appliance_standards/pdfs/refrig_finalrule_tsd.pdf.

Ibid.

Federal Standards for Electric Motors, Table 3,

https://www.ecfr.gov/cgi-bin/retrieveECFR?n=pt10.3.431#sp10.3.431.b. Accessed July 2020.

Federal Standards for Electric Motors, Table 4,

https://www.ecfr.gov/cgi-bin/retrieveECFR?n=pt10.3.431#sp10.3.431.b. Accessed July 2020.

U.S. DOE, Technical Support Document, “Energy Efficiency Program for Commercial Equipment: Energy Conservation Standards for Electric Motors”, Median of “Table 8.2.23 Average Application Lifetime”.  Download TSD at: https://www.mercatus.org/system/files/1904-AC28-TSD-Electric-Motors.pdf. Accessed July 2020.

A 93% pump runtime reduction is assumed based on the average runtime reduction of field studies conducted at multiple sites: “Evaluation of New DHW System Controls in Hospitality and Commercial Buildings,” Minnesota Department of Commerce, average reduction of 87%; and “Energy-Efficiency Controls for Multifamily Domestic Hot Water Systems,” New York State Energy Research and Development Authority, average reduction of 99%.

Probability weighted peak load factors are calculated according to the method in Section 4 of the Texas TRM Vol 1 using data from the EPRI Load Shape Library 6.0. ERCOT regional End Use Load Shapes for Water and Process Heating. Peak Season, Peak Weekday values used for summer calculations. Off Peak Season, Peak Weekday values used for winter calculations. http://loadshape.epri.com/enduse. Accessed July 2020.

For the purposes of this measure, the lodging building type applies to all buildings where lodging takes place, including multifamily, hotels, nursing homes, dormitories, prisons, and similar.

Reference kWh are the annual energy savings per dwelling unit from the Southern California Edison Company Work Paper SCE13WP002, Demand Control for Centralized Water Heater Recirculation Pump for California Climate Zone 13.

HDD Adjustment factors for DHW controls are derived by dividing the HDD for each Texas climate zone by the HDD from the reference climate zone (California Climate Zone 13).

DEER 2014.

DASMA Standard Specification for High Speed Doors and Grilles, definition 2.6 for High Speed Door. https://www.dasma.com/PDF/Publications/standards/DASMA403.pdf. Accessed August 2020.

Operating hours taken from TRM Volume 3, Table 8, hours for refrigerated warehouse.

From ASHRAE 2018 Refrigeration Handbook, Chapter 24-4, equation 16.

From ASHRAE 2018 Refrigeration Handbook, Chapter 24-4, simplification of equation 17 notes; assume baseline door open-close time is 15 seconds, and high speed door open-close time is 10 seconds, for a difference in percent of time the door is open of (15-10)/15 = 0.33.

ASHRAE 2018 Refrigeration Handbook, Chapter 24-4, equation 17 notes.

ASHRAE 2018 Refrigeration Handbook, Chapter 24-4, simplification of equation 17 notes. ASHRAE provides a range of doorway effectiveness, stating 0.95 for newly installed doors though that may quickly decrease to 0.8 or 0.85 depending on door use frequency and maintenance. Air curtain effectiveness ranges from very poor to more than 0.7. The input assumptions for this measure are conservatively estimated for baseline door effectiveness of 0.7 and high speed door effectiveness of 0.9.

Air cooled chiller efficiency from IECC 2009.

From ASHRAE 2018 Refrigeration Handbook, Chapter 24-4, figure 9. Values in table are summarized to reflect average annual and summer and winter peak infiltration air Temperatures. Where infiltration air Temperatures are not shown on ASHRAE figure 9, qsA is estimated by extrapolation. Values for infiltration air temperature of 75°F are used to calculate energy and demand factors for doorways between cold room and conditioned space.

Sensible heat ratio determined from psychrometric chart, using values for the air properties of dry bulb Temperature and relative humidity. Relative humidity of the cold room is estimated at 90% based on ASHRAE 2018 Refrigeration Handbook, Chapter 24-4, Table 9. Energy factor values for unconditioned space are the average annual values between the expected operating hours of 8am – 6pm using TMY3 data. Demand factor values for unconditioned space are taken using the highest probability Temperatures from TRM Volume 1 and their associated relative humidity from TMY3 data. Energy and demand factor values for conditioned space assume conditioned air temperature of 75°F and 45% RH.

A temperature sensitive restrictor valve is any device that uses water temperature to regulate water flow in showers.

Shower Stream 2019 pilot study based on 747 metered shower events with an average duration of 104.51 seconds. This represents a subset of the total data set, as this value was not recorded for the entire data set. This assumption will be updated in future years to reflect additional pilot study data.

Shower Stream 2019 pilot study based on 2,406 metered shower events. Weighted average calculated by dividing total shower events by total number of devices. This assumption will be updated in future years to reflect additional pilot study data..

2001-2019 U.S. hotel occupancy rates from Statista. https://www.statista.com/statistics/200161/us-annual-accomodation-and-lodging-occupancy-rate/. Used average of last 5 years (2015-2019).

Assuming industry standard for standard one-bathroom rooms.

Average percent hot water from (Lutz 2004) Feasibility Study and Roadmap to Improve Residential Hot Water Distribution Systems and (Sherman 2015) Calculating Savings For: Auto-Diverting Tub Spout System with ShowerStart TSV.

120°F represents the assumed water heater setpoint. New York Department of Public Service recommends using water heater setpoint as a default value, see “New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs” October 2010, page 99.

Data collection discussed in Appendix D of the EM&V team’s Annual Statewide Portfolio Report for Program Year 2014-Volume 1, Project Number 40891 (August 2015), also supports a default value of 120°F.

Default values based on median recovery efficiency of residential water heaters by fuel type in the AHRI database. https://www.ahridirectory.org/.

Based on typical meteorological year (TMY) dataset for TMY3: https://nsrdb.nrel.gov/about/tmy.html.

2014 California Database for Energy Efficiency Resources. http://www.deeresources.com/.

A temperature sensitive restrictor valve is any device that uses water temperature to regulate water flow in showers.

Assumption from (Sherman 2015) Calculating Savings For: Auto-Diverting Tub Spout System with ShowerStart TSV.

Percent of warm-up events from (Sherman 2014) Disaggregating Residential Shower Warm-Up Waste (Appendix B, Question 8).

Shower Stream 2019 pilot study based on 747 metered shower events with an average duration of 104.51 seconds. This represents a subset of the total data set, as this value was not recorded for the entire data set. This assumption will be updated in future years to reflect additional pilot study data.

Average diverter leak rate from (Taitem 2011) Taitem Tech Tip – Leaking Shower Diverters.

Cadmus and Opinion Dynamics Evaluation Team, “Memorandum: Showerhead and Faucet Aerator Meter Study”. Prepared for Michigan Evaluation Working Group.

Shower Stream 2019 pilot study based on 2,406 metered shower events. Weighted average calculated by dividing total shower events by total number of devices. This assumption will be updated in future years to reflect additional pilot study data.

2001-2019 U.S. hotel occupancy rates from Statista. https://www.statista.com/statistics/200161/us-annual-accomodation-and-lodging-occupancy-rate/. Used average of last 5 years (2015-2019).

Assuming industry standard for standard one-bathroom rooms.

Average percent hot water for warm up events from (Lutz 2004) Feasibility Study and Roadmap to Improve Residential Hot Water Distribution Systems and (Sherman 2015) Calculating Savings For: Auto-Diverting Tub Spout System with ShowerStart TSV.

120°F represents the assumed water heater setpoint. New York Department of Public Service recommends using water heater setpoint as a default value, see “New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs” October 2010, page 99.

Data collection discussed in Appendix D of the EM&V team’s Annual Statewide Portfolio Report for Program Year 2014-Volume 1, Project Number 40891 (August 2015), also supports a default value of 120°F.

Default values based on median recovery efficiency of residential water heaters by fuel type in the AHRI database. https://www.ahridirectory.org/.

Based on typical meteorological year (TMY) dataset for TMY3: https://nsrdb.nrel.gov/about/tmy.html.

2014 California Database for Energy Efficiency Resources. http://www.deeresources.com/.

National Renewable Energy Laboratory (NREL), February 2018, “Charging Electric Vehicles in Smart Cities: An EVI-Pro Analysis of Columbus Ohio,” page 26, Table 8: Charging Statistics by Location Type and Level, ChargePoint Data. Average across all location types, dwell time minus charging duration.

Average Idle Mode Input Power from ENERGY STAR certified EVSE product list as of July 13, 2020.

NREL “Charging Electric Vehicles in Smart Cities: An EVI-Pro Analysis of Columbus Ohio,” page 26, Table 8; 24 hours per day minus average dwell time.

Average No Vehicle Mode Input Power from ENERGY STAR certified EVSE product list.

NREL “Charging Electric Vehicles in Smart Cities: An EVI-Pro Analysis of Columbus Ohio,”  page 25; 0.56 charging sessions per day per plug in Austin, Texas. 365 x 0.56 = 204.

ENERGY STAR Electric Vehicle Chargers Buying Guidance: “ENERGY STAR certified EV charger… on average use 40% less energy than a standard EV charger when the charger is in standby mode (i.e., not actively charging a vehicle).” https://www.energystar.gov/products/other/evse. Accessed July 2020.

Probability weighted peak load factors are calculated according to the method in Section 4 of the Texas TRM Vol 1 using data from  NREL “Charging Electric Vehicles in Smart Cities: An EVI-Pro Analysis of Columbus Ohio,” page 27, Figure 21: Daily distribution of ChargePoint charging events by EVSE type and day of the week.

U.S. Department of Energy Vehicle Technologies Office, November 2015, “Costs Associated with Non-Residential Electric Vehicle Supply Equipment” p. 21. https://afdc.energy.gov/files/u/publication/evse_cost_report_2015.pdf, Accessed July 2020.

Retired system refers to the existing equipment that was in use before the retrofit has occurred.

Baseline used for a replace-on-burnout project of the same type and capacity as the system being installed in the Early Retirement project (as specified in the applicable measure).

Replacement system refers to the installed equipment that is in place after the retrofit has occurred.

The exact values to be used each year for the escalation rate, discount rate, and avoided costs are established by the PUC in Substantive Rule §25.181 and updated annually, as applicable. Please note that the discount rates are based on a utility’s weighted average cost of capital and, as such, will vary by utility and may change each year.