## Specific Instructions
General Instructions for Entering Information - 2008
NOTES:
1. Please use "na" whenever appropriate to reduce ambiguity, except in the "Costs," "Percent Complete," and "Percent Variance" columns.
Column Title: | 2. Any new or revised entry must be entered using a red font. In the month following the red font entry, change the previous month's red entries back to black and make any new entries for the new month in red. This aids PUCT staff in quickly identifying any changes from the previous month’s report.
Utility's Project Number | Enter the Utility's Project Number. No duplicate numbers are allowed in this column.
Project Name | Enter the name of the project. If possible, use the same name as was reported to ERCOT in any reports.
Location (City/County) | Enter the names of the counties where the project is located. Also enter the names of cities, if appropriate. Please delineate all county and city names with commas only. (e.g., Liberty, Chambers, Anahuac, etc.)
Description | Describe the project in enough detail to allow the Commission to ensure that the work does not require a CCN, if the utility does not intend to apply for a CCN. Include any significant or relevant detail not being reported in other columns.
Estimated (or Actual) Start Date | Enter the estimated project starting date. When construction begins, please replace the estimated date with the actual date of the start of construction.
Finish Date (Construction Complete) | Enter the date (dd/mm/yy) when the construction related to the project has been completed.
Date Energized (If Applicable) | Enter the date (dd/mm/yy) the project was energized or restored to service (if applicable).
Initial Estimated Project Cost | CCN Projects Only: Enter the estimated cost from the CCN application. When reporting both T-Line and Substation Costs, enter them separately in the same cell. (e.g., "$3,946,000 T-Line; $1,768,000 Substation") This number should not be changed in future months unless the Application is amended. Please DO NOT use links to other sheets within the workbook. Non-CCN Projects Only: No entry is needed; Enter the estimated cost in the Final Estimated Cost column.
Final Estimated Project Cost | CCN Projects: Enter the latest available estimated cost for the month that construction starts. This number should not be changed after construction begins. For Non-CCN Projects: Enter the initial estimated cost. Estimate revisions are not necessary, and a cost variance explanation is not required unless requested by PUC Staff .
Final Actual Project Cost | Enter the actual, final project cost after the project has been energized and all costs have been recorded. Omit the project from all following reports.
% Variance | The cells contain a formula for calculating the percent variance of the final actual cost with respect to the final estimated cost. This is essentially a calculation of the percent of the cost over-run or under-run.
Percent Complete | State the approximate construction progress of the report as a percent. Please use only an integer and do not write"%." Do not report the percent of money spent.
Existing Voltage | Enter the nominal system existing voltage, if any. In the event of a voltage upgrade, this will be the "before" voltage. If the project is for a new line, enter "na." For projects involving multiple voltages, please delineate the voltages by a comma, e.g., "69,138" and explain further in comments or project description, if needed for clarification. Please do not write "volts."
Upgraded or New Voltage | Enter the nominal system voltage after upgrading or if new line construction is involved. Please use the same practices described in the"Existing Voltage" column. Please do not write "volts."
Circuit Length (Miles) | Enter the total circuit length. Example: For a new double-circuit line using 10 miles of new ROW, the circuit length would be 20 miles. Please enter only a number, if possible. Please do not write "miles."
Conductor Type & Size & Bundling | Describe the conductor characteristics, including whether double or single circuit or mixed. Length explanations should be made in the Project Description column.
Structure Type(s) | Describe structure types and materials used.
Existing ROW Width (Feet) | Enter width of existing ROW. The entry type is unrestricted. If the project is only for new line and no old ROW exists, enter "na." Entries such as "60,80,100" or "60 - 100" or "centerline" are permissible. Make detailed explanations, if needed, elsewhere. Please do not write "feet."
Existing ROW Length (Miles) | Enter length of existing ROW. The entry type is unrestricted. If the project is only for new line and no old ROW exists, enter "na." Make detailed explanations, if needed, elsewhere. Please do not write "miles."
New ROW Width (Feet) | Enter width of new ROW. The entry type is unrestricted. Entries such as "60,80,100" or "60 - 100" or "centerline" or "railroad" or "street" are permissible. Make detailed explanations, if needed, elsewhere. Please do not write "feet."
New ROW Length (Miles) | Enter new (additional) ROW length, in miles. Please do not write "miles."
Rule Section or PUC Control Number | Enter the PUC Rule 25.101 section(s) which are applicable. For multiple section applicability, please delineate by commas, e.g., "25.101(c)(5)(A),25.101(c)(5)(B)" for a project incorporating a line extension (A) and a voltage upgrade on the existing line which is being extended(B). If the project is approved under a CCN, please enter ONLY the 5-digit control number. Please do not write "docket," "CCN" or other indicators. Should the project encompass work done under both CCN and exempted sections, follow the same practices and delineate with commas.
Comments | Enter information not included elsewhere, including reimbursed costs, references to any required Affidavits of Notice or Landowner Consent statements, etc.
Note on A18: aboling: If applicable.

## Sugg.Practices(TabNotOnWebsite)
SUGGESTED SPREADSHEET PRACTICES
VERY IMPORTANT: Any new or revised entry MUST be entered using a red font. In the month following the red font entry, change the previous month's red entries back to black and make any new entries for the new month in red. This aids PUCT staff in quickly identifying any changes from the previous month’s report.
Please enter your Utility Name and Month in the top center header. Also, please enter the appropriate data in the bottom left footer. Your personal contact information WILL NOT appear in the report posted at the PUC website. Please do not change the right-hand header and footer.
Adjust Row and Column Heights and Widths to a pleasing dimension as you wish. Vertical centering is recommended to improve readability when using the "Wrap Text" Feature.
Please do not use multiple Rows for any project. Each project should occupy only one line. If necessary, however, multiple project numbers may be entered in the same cell in the "Project Number" column. Use the "Wrap Text" feature throughout the spreadsheet and the "Row Height Autofit" feature for all lines except for the header.
Never enter identical project numbers in the "Project Number" column. If your internal practices split a project into multiple parts, use distinguishing suffixes, such as 103668XYA and 103668XYB.
If a project number has not been assigned for a project, please create one (a "dummy") to use in your construction reports, rather than leaving the cell empty. Continue using that project number, revising later if you like, but please use red font in the "Project Number" cell to indicate any change in the number.
Please do not insert extra rows between projects. PUCT staff must delete any extra lines to properly compile report data.
Please do not enter “NA” or any other text in the "Estimated," "Final" or "% Variation" numerical columns. Text in those columns must be manually removed before PUC staff can compile the report.
A percent variation calculation formula is contained within the "% VAR." column. Please leave this formula as it is. However, if you copy & paste data and overwrite those cells, don't worry about it.
In the "Rule Section...." column, enter the PUC assigned docket number (if project requires a CCN) or the PUC exemption qualifying section or sections (if the project is exempt from CCN requirements). Do not enter "EXEMPT."
Monthly Construction Progress Reports may be found at the PUCT website. Individual utility MCPR worksheets for each utility are contained within each month's compiled report at: http://www.puc.state.tx.us/electric/reports/cpr/index.cfm.
Please contact Allen Boling at (512)936-7402 or allen.boling@puc.state.tx.us for assistance or clarification, including questions (or advice) about MS Excel spreadsheets.
For Subst. Rule §25.83(c)(3) notice compliance purposes, the PUC contact will be Allen Boling, at (512) 936-7402 or (888) 782-8477. Hearing and speech-impaired individuals with text telephones (TTY) may contact Mr. Boling at (512) 936-7136 or Relay Texas at (800) 735-2989.
Suggested Language (after providing utility contact information with the utility as the primary contact): "In the event you have unresolved questions or complaints after discussing these activities with (utility name), you may contact Allen Boling at the PUCT, at P.O. Box 13326, Austin, Texas 78711-3326, or call Mr. Boling at (512)936-7402 or (888)782-8477 or by e-mail at allen.boling@puc.state.tx.us. Hearing and speech-impaired individuals with text telephones (TTY) may contact Mr. Boling at the PUCT and (512)936-7136 or Relay Texas at (800)735-2989."

## ETI MCPRF 08-09
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
TL5400 | Proposed Merlin Substation to L-17 138kV Transmission Line | Orange County, Texas | Construct new 138kV single pole double circuit transmission line from the new proposed Merlin Substation to the existing line 17 | 2009-09-01 | 2010-10-22 | 2010-10-22 | 3142673 | 4649648 |  |  | 100% | na | 138 | 2.6 | Bundled 666 ACSR | Single Pole Steel & Concrete | na | na | 100 | 2.6 | 31241 | Working on final costs.
TLX001 | L-824 Upgrades | Montgomery County, TX | Replace double circuit h-frame with double circuit single pole. H-frame only has one circuit (L-824). Install new conductor in vacant circuit position and renumber to L-824. Transfer existing conductor to new single pole and renumber to L-87 to allow for cut-in of new Lewis Creek Substation. All work is in existing R/W. | 2010-12-01 |  |  | 4150000 | 4135000 |  |  | 100% | 138 | 230 | 3 | 1272 ACSR | Single Pole Dbl Ckt Concrete | 250 | 3 | na | na | 25.101(c)(5)(B)(i)(ii)(C)(i)(ii) | Working on final Costs.
TLX002 | L-587 Cut-in to New Caney Creek Substation | Montgomery County, TX | Cut-in 138kV L-587 into new SHECO Caney Creek Substation | 2010-04-01 | 2010-05-20 | 2010-05-20 | 1100000 |  |  |  | 100% | 138 |  | 0.1 | 1272 ACSR | Steel | na | na | na | na | 25.101(c)(5)(A)(i)(ii) | SHECO has relocated their Caney Creek Substation to be served from 138kV as part of the L-824 conversion to 230kV.
TLX003 | L-824 bypass of old Caney Creek Substation | Montgomery County, TX | Install one pole in old Caney Creek Substation and bypass old substation | 2010-12-01 | 2011-02-03 | 2011-02-03 | 120000 |  |  |  | 100% | 138 | 230 | na | 2-649 ACAR | Steel | na | na | na | na | 25.101(c)(5)(B)(i)(ii) | Working on final Costs.
TLX004 | Tie existing Lewis Creek 138kV Switchyard to new Lewis Creek Substation | Montgomery County, TX | Install three spans from existing Lewis Creek 138kV switchyard to the New Lewis Creek 230/138kV Substation | 2010-12-01 |  |  | 830000 | 970000 |  |  | 100% | 138 | na | 0.2 | 1272 ACSR | Steel | 100 | 0.2 | na | na | 25.101(c)(5)(A)(i)(ii) | Working on final Costs.
TL1298 | Bentwater L-112 Cut-in | Montgomery County, TX | Cut-in 138kV L-112 to new Bentwater Substation | 2010-04-05 | 2010-04-22 | 2010-04-23 | 461371 |  |  |  | 100% | 138 | na | 0.03 | 1272 ACSR | Concrete | na | na | na | na | 25.101(c)(5)(A)(i)(ii) | Working on final costs.
TLM003 | L-804 Raise Line | Orange County, TX | L-804 Raise line for highway overpass project | 2010-07-05 | 2010-07-09 |  | 300098 |  |  |  | 100% | 69 | na | 0.01 | 795 ACSR | Concrete | 100 | 0.01 | na | na | 25.101(c)(5)(F)(i)(ii) | This is a project that got put on the fast track by TxDot to spend some stimulus money from the federal government. All property owners have been notified.
TLM004 | L-525 Raise Line | Orange County, TX | L-525 Raise line for highway overpass project | 2010-09-20 | 2010-09-24 |  | 173000 |  |  |  | 100% | 69 | na | 0.01 | 395 ACAR | Concrete | 80 | 0.01 | na | na | 25.101(c)(5)(F)(i)(ii) | This is a project that got put on the fast track by TxDot to spend some stimulus money from the federal government. All property owners have been notified.
TLM002 | Cut L-57 into Customer Owned Daisy substation | Liberty County , TX | Tap existing 69 Kv Line 57 and construct single pole double circuit line into new Customer Owned Daisy Substation | 2010-11-30 |  |  | 1375815 | 1375815 |  |  | 100% | 69 | na | 0.45 | 666 ACSR | Steel | 60 | na | 60 | 0.45 | 25.101(c)(5)(A)(i)(ii) | Working on final costs.
TLM005 | Cut L-114 into customer owned Gladys substation | Jefferson County, Texas | Tap existing 69kV L-114 and construct single pole double circuit line into customer owned Gladys Substation | 2011-01-01 |  |  | 1053000 |  |  |  | 95% | 69 | na | 0.23 | 666 ACSR | Steel and Concrete | 60 | na | 60 | 0.23 | 25.101(c)(5)(A)(i)(ii) | Outage scheduled in two weeks for Line cut-in.
TL9821 | L-886 Rebuild from Tamina Substation to Cedar Hill | Montgomery County, TX | Rebuild 138Kv H-Frame L-886 from Tamina Substation to Cedar Hill | 2011-01-01 |  |  | 4700541 |  |  |  | 45% | 138 | na | 4.45 | 1272 ACSS | Steel | 150 | 4.45 | na | na | 25.101(c)(5)(B)(i)(ii) | This project will be worked in two phases due to outage constraints.
TLZ002 | 230kV line 195 Reconductor for new line rating | Orange & Newton Counties | Reconductor 230 kV Line 195 From McLewis Substation to Hartburg Substation | 2011-02-28 |  |  | 7801731 |  |  |  |  | 230 | 230 | 12 | 1461 ACCC & 1272 ACSS | na | 150 | 12 | na | na | 25.101(c)(5)(B)(i)(ii) | This Is a reconductor uprate project with the exception of the in-out section to Inland Orange Substation. This four spans will be rebuilt from wood h-frame structures to single steel poles and use the 1272 ACSS conductor.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## CCN 31241 COST ANALYSIS
CCN Docket No :31241 | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance
Transmission
Right-of-way (Easement and Fees) | 469315 | 413719.0481
Materials and Supplies | 737599 | 1694933.1072
Labor and Transportation (Utility) | 43234 | 72702.5301
Labor and Transportation (Contract) | 1307571 | 2172829.527
Stores | Inc in Materials above
Engineering and Administration (Utility) | 329169 | 189856.3077
Engineering and Administration (Contract) | 255785 | 105657.48
Transmission Total Cost | 3142673 | 4649698
Substation
Right-of-way (Easement and Fees) | 189664 | 247595.2534
Materials and Supplies | 1031813 | 913698.6251
Labor and Transportation (Utility) | 113178 | 95297.9926
Labor and Transportation (Contract) | 961788 | 1222403.2739
Stores | Inc. in Materials Above
Engineering and Administration (Utility) | 373175 | 181140.497
Engineering and Administration (Contract) | 25569 | 11967.358
Substation Total Cost | 2695187 | 2672103