## MonthlyReportForm
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
TL174 | Copper - Lane 115kV Rebuild & Reconductor | El Paso, El Paso | EPE will replace approximately sixty-four 65' wooden monopole structures with 95' steel monopole structures along a 3.5 mile stretch of Interstate 10 between Lane and Copper Substations. In addition, conductor will be upgraded to 954 MCM ACSR. One new pole will be constructed off of the existing route due to encroaching residential development. | 2017-09-01 |  |  | 3319403 |  |  |  | 0% | 115 | n/a | 5.01 | 556 kcmil ACSR, single conductor, will be replaced with 954 kcmil ACSR | 65'/70' wood single pole structures will be replaced with 95'-110' galvanized steel monopole structures; one corner self-supported structure on new route will be constructed | TxDOT permit | 3.57 | n/a | n/a | 25.101(c)(5)(B) and (E) | Project has been moved to late 2017. Other projects in Texas and New Mexico must be completed first.
TL127 | Felipe to Alamo, Alamo to Neely, and Neely to Farmer Structure Replacement | Fabens and Tornillo, El Paso County; Sierra Blanca, Hudspeth County; Van Horn, Culberson County | EPE will replace existing wood monopole structures with steel monopole structures in approximate 94 miles of 69kV transmission line. EPE will utilize the existing centerline. Span lengths may be adjusted according to terrain features. | 2012-06-30 |  |  | 6502992 | 11.0447,753 |  |  | 66% | 69 | n/a | 94 | 4/0 ACSR single conductor | 60 & 65' wood monopoles being replaced with 75' galvanized steel monopole structures | varies | 94 | n/a | n/a | 25.101(c)(5)(B)
TL101 | TxDOT SL375 Border West Expressway - Paisano @ Racetrack Adjustments | El Paso, El Paso | EPE will adjust 2 sets of H-frame transmission structures carrying 2 transmission circuits each across US 85 (Paisano) necessary to increase the height of conductors to accommodate a TxDOT project and to comply with TxDOT highway clearance requirements. EPE will replace existing structures on both sides of Paisano with taller steel monopole and drilled pier structures ranging from 79' to 105'. 4- tangents and 6-deadends. | 2016-12-19 |  |  | 1938865 |  |  |  | 85% | 69 & 115 | n/a | Rio Grande Sunset 0.97; Rio Grande Mesa 0.95 | 795 kcmil ACSS "Drake" single conductor & 954 ACSR "Rail" single and double bundle conductor | 79'-97' steel monopole; 95'-105 steel self-supported drill pier foundation structures; double circuit | varies | Rio Grande Sunset 5.32/Rio Grande Mesa 2.31 | n/a | n/a | 25.101(c)(5)(F) | Structure installation affecting the TxDOT project completed, allowing TxDOT road project to proceed. Final 4 structures to be installed after electric summer peak season.
TL189 | Reconductor Sol to Vista 115kV transmission line | El Paso, El Paso | Reconductor the line to relieve summer overload on the line . EPE will replace wood H-frame structures with steel monopole structures to accommodate upgrade of wire to 954 ACSR | 2017-03-27 | 2017-05-19 | 2017-06-03 | 1290000 | 1290000 | 1377497 | 6.783% | 100% | 115 | n/a | 2 | 556 ACSR conductor will be replaced with 954 ACSR single conductor | Replace H-frame wood structures with 85'-90' steel monopoles. 16 tangents and 2 dead-end drill pier foundation | 100' | 2 | n/a | n/a | 25.101(c)(5)(B)(i) | Energized June 3, 2017
TL239 | Reconductor Durazno to Ascarate 115kV transmission line | El Paso, El Paso | Reconductor the line to relieve overloading on the line. EPE will replace wood monopole structures with steel monopole structures to accommodate upgrade of wire to 954 ACSR | 2017-10-01 |  |  | 1922157 |  |  |  |  | 115 | n/a | 3.5 | 556 ACSR conductor will be replaced with 954 ACSR single conductor | Replace wood monopole structures with 85'-105' steel monopoles. | varies and street ROW franchise | 3.5 | 10 | 0.19 | 25.101(c)(5)(B)(ii) | Engineering design is underway to upgrade the line to transport 170 MW between substations
TL240 | Reconductor Sunset North to Durazno 115kV transmission line | El Paso, El Paso | Reconductor the line to relieve overloading on the line. EPE will replace wood monopole structures with steel monopole structures to accommodate upgrade of wire to 954 ACSR | 2017-11-01 |  |  | 1175300 |  |  |  |  | 115 | n/a | 4.63 | 556 ACSR conductor will be replaced with 954 ACSR single conductor | Replace wood monopole structures with 85'-105' steel monopoles. | varies and street ROW franchise | 4.63 | n/a | n/a | 25.101(c)(5)(B)(i) | Engineering design is underway to upgrade the line to transport 170 MW between substations
TL246 | Scotsdale to Vista 115kV transmission line modifications | El Paso, El Paso | Re-spacing and replacing 5 structures to accommodate the expansion of Scotsdale Substation. | 2017-06-01 |  |  | 365000 |  |  |  | 20% | 115 | n/a | 0.19 | 556 ACSR single conductor | Replace wood h-frame and monopole structures with steel 75'-80' h-frame and monopole structures | 25' | 0.19 | n/a | n/a | 25.101(c)(5)(B)(i) | Two structures inside Scotsdale substation installed to allow substation work to proceed.
TL247 | TxDOT SL375 Interchange Improvements | El Paso, El Paso | Adjust 2-345kV transmission lines, Caliente to Amrad and Caliente to Picante to accommodate the new eastbound and westbound frontage roads to be constructed by TxDOT. EPE will replace several poles on either side of SL375 with taller steel poles for each line. | 2018-04-01 |  |  | 1430235 |  |  |  |  | 345 | n/a | 0.73 each | 954 ACSR corncrake double bundle conductor | Replace wood h-frame structures with 90'-125' steel h-frame or 3-pole structures. Replace corncrake with cardinal 954 ACSR conductor | 300' | 0.73 each | n/a | n/a | 25.101(c)(5)(F) | Soil boring has been completed to proceed with structure designs.
TL101 | Rebuild and reconductor 2- 69kV transmission lines from Rio Grande to Sunset and the Rio Grande to Sunset North 115kV line, rebuild a portion of the Rio Grande to Mesa 115kV transmission line | El Paso, El Paso | Rebuild and reconductor the lines to relieve overloading and replace aged infrastructure, over 80 years old. The 2-69kV lines, 5500 and 5600 Rio Grande to Sunset, will be on one set of double circuit steel monopole structures. The 115kV transmission lines, 15800-Rio Grande to Sunset North and 16200-Rio Grande to Mesa , will be on a separate set of steel monopole structures. All lines will be within the same corridor to a point where they converge on the west side of I-10 in the east/west direction. At this point the 2-69kV lines and the15800-Rio Grande to Sunset North 115kV line will be constructed in a new corridor. The wire for the 69kV lines and Rio Grande to Sunset North 115kV line will be upgraded to 954 ACSR. 3.44% of the project is in New Mexico | 2017-10-01 |  |  | 16075700 |  |  |  |  | 69 & 115 | n/a | 5500/69kV - 4.69; 5600/69kV -5.04; 15800/115kV -4.87; 16200/115kV-2.17 | 69kV lines -556 ACSR & 115kV line -556 ACSR double bundle | Replace wood structures with 55'-120' steel monopole structures and self-support structures on drill pier foundations. Replace wire with 954 ACSR rail; 115kV will be double bundle | 50'-150' | 5500/69kV - 4.78; 5600/69kV - 5.32; 15800/115kV - 5.08; 16200/115kV-2.17 | 120 | 0.94 | 25.101(c)(5)(b)(ii) | Prior written consent obtained from landowner for the new location. Two 69kV and one 115kV transmission lines will be moved to the new ROW. One landowner within 300' of the new ROW has been notified.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.