SOAH DOCKET NO. 473-17-2686

PUC DOCKET NO. 46831

APPLICATION OF EL PASO	§	BEFORE THE STATE OFFICE

ELECTRIC COMPANY TO	§	OF

CHANGE RATES		§	ADMINISTRATIVE HEARINGS

EL PASO ELECTRIC COMPANY'S RESPONSE TO

TEXAS INDUSTRIAL ENERGY CONSUMERS'

THIRD REQUEST FOR INFORMATION

QUESTION NOS. TIEC 3-1 THROUGH TIEC 3-10

TIEC 3-6:

Does the Company routinely take its local generating units off-line for major planned overhauls?  If so, please explain the types of maintenance activities typically performed during major planned overhauls, and the typical frequency and duration of major planned overhauls for EPE’s different types of local generating units.

RESPONSE:

Yes, the Company routinely takes its local generating units off-line for major planned overhauls.  Please see the direct testimony of EPE witness Andres Ramirez’s at page 26, lines 8 through 11.

EPE has an assorted fleet of different types of gas and steam turbines.  While not all inspections are identical, the major category of inspections and maintenance activities for a steam turbine major overhaul can be, but are not limited to, the following:

- Disassembly of turbine;

- Clean and inspect rotating and stationary components using different techniques such as dye penetrant and magnetic particle inspection and repair or replace as necessary;

- Inspect bearings;

- Inspect pumps;

- Disassembly of major valves, inspect and repair as needed;

- Disassembly of generator;

- Electrically inspect and test generator;

- Make repairs based off of findings from inspections; and

- Reassemble the units.

For a gas turbine major overhaul, repair activities would be items such as:

- Inspect and repair as necessary the compressor section;

- Inspect and repair the combustor section;

- Inspect and repair the turbine section; and

- Inspect and test the generator.

The typical frequency between major turbine inspections is 60,000 hours for steam turbines, 48,000 hours for a heavy frame gas turbines, and 50,000 hours for an aeroderivative gas turbine.

The typical duration for a plant major outage depends on the type of turbine and the scope of repair work needed.  However, a standard that EPE uses for outage durations is as follows for the different turbines in EPE’s fleet:

- Steam turbine major outages average 84 days;

- 7EA (Newman Unit 5) gas turbine major outages average 42 days;

- 501B (Newman Unit 4) gas turbine major outages average 56 days; and

- Aeroderivative (LMS-100) major outages average 3-7 days with the use of rotable components.

Preparer:	M. Martin Lopez	Title: 	Director-Generation Operations

Sponsor:	Andres R. Ramirez	Title: 	Vice President-Power Generation