SOAH DOCKET NO. 473-17-2686

PUC DOCKET NO. 46831

APPLICATION OF EL PASO	§	BEFORE THE STATE OFFICE

ELECTRIC COMPANY TO	§	OF

CHANGE RATES		§	ADMINISTRATIVE HEARINGS

EL PASO ELECTRIC COMPANY'S RESPONSE TO

TEXAS INDUSTRIAL ENERGY CONSUMERS'

THIRD REQUEST FOR INFORMATION

QUESTION NOS. TIEC 3-1 THROUGH TIEC 3-10

TIEC 3-7:

Are major planned overhauls routinely performed on the Palo Verde generating units? If so, please explain the types of maintenance activities typically performed during major planned overhauls, and the typical frequency and duration of major planned overhauls for Palo Verde.

RESPONSE:

“Major planned overhaul” (a term commonly understood to apply to fossil-fired generation plants) activities are undertaken during planned refueling outages.  Palo Verde Nuclear Generating Station conducts refueling outages on an 18 month per unit cycle frequency and a typical duration of 30 days.  Please see Schedule H-6.1 for the historical and planned outage schedule.  For a list of frequently performed “major overhaul” maintenance activities, please see below:

- Low/High Pressure turbine inspections and replacement/repair of degraded components as necessary (Every 9 years);

- Main Generator/Turbine testing (Every Outage); - Low Pressure turbine blade inspection (Every 4.5 years); - All LP rotors have been replaced after approximately 20+ years of run time

Preparer:	Nadia Powell	Title: 	Director – Remote Asset Management

Sponsor:	John Cadogan	Title: 	Senior Vice President-Site Operations-PVNGS