SOAH DOCKET NO. 473-17-2686

PUC DOCKET NO. 46831

APPLICATION OF EL PASO	§	BEFORE THE STATE OFFICE

ELECTRIC COMPANY TO	§	OF

CHANGE RATES		§	ADMINISTRATIVE HEARINGS

EL PASO ELECTRIC COMPANY'S RESPONSE TO

SOLAR ENERGY INDUSTRIES ASSOCIATION’S

FOURTH SET OF REQUESTS FOR INFORMATION

QUESTION NOS. SEIA 4-1 THROUGH SEIA 4-4

SEIA 4-3:

For Residential DG customers in EPE’s service territory:

- What percentage of Residential DG customers added solar to an existing house vs. constructed a new house with DG installed at or near the time of utility hookup?  If an exact figure is not known, please estimate the approximate percentages.

b.	For a Residential DG customer that added DG to an existing house, what additional distribution hardware beyond metering did EPE add to its distribution grid to accommodate the DG?  If none, please confirm.

c.	For a Residential DG customer that added DG to an existing house, what distribution hardware did EPE remove from its distribution grid to accommodate the lower levels of sales to the Residential DG customer?  If none, please confirm.

d.	If all Residential DG customers removed their DG systems from EPE distribution grid, what would be the impact on the distribution system?  What hardware would EPE need to add or remove to accommodate this change?

RESPONSE:

- EPE does not have information regarding the number of renewable energy systems added to existing homes or new construction homes. This information is not requested from the customer who is installing a renewable energy system.

- With the current levels of DG penetration, EPE has not had to add additional distribution equipment (beyond metering) to accommodate DG.  However, the feeder load masking effect of DG (i.e., full potential feeder load is not seen until cloud cover reduces the output of DG systems) is beginning to be of concern in the protection and planning process. EPE also suspects, and is investigating, whether the presence of DG has increased the duty cycle (number of on/off operations for line capacitors, or voltage regulator tap change operations) of automated line equipment.

- EPE confirms that it has not removed distribution hardware from its distribution system to accommodate DG.  Because of the masking effect of DG (see response to b. above) EPE has not, and cannot, remove equipment as a result of DG.

- No distribution equipment would be added or removed. However, removing DG from the distribution system would result in more predictable feeder load and voltage profiles and would, potentially (see response to b. above), reduce the duty of voltage control equipment like voltage regulators and capacitor banks.

Preparers:	Jessica Sosa	Title: 	Analyst Finance-Associate

Ty Pollard	 	Superintendent-Distribution System

Sponsors:	James Schichtl	Title: 	Vice President-Regulatory Affairs

Clay Doyle		Vice President-Transmission & Distribution and System Planning