PUC Interoffice Memorandum

To:	Kevin Bartz, Attorney

Legal Division

Thru:	Heidi Graham, Manager

Water Utility Regulation Division

From:	Debbie Reyes, Program Specialist

Water Utility Regulation Division

Date:	April 17, 2018

Re:	Docket No. 47463:  Application of Summit Ridge, LLC to Obtain a Water Certificate of Convenience and Necessity in Medina County

On August 1, 2017, Summit Ridge LLC (Applicant) filed an application to obtain a water Certificate of Convenience and Necessity (CCN) in Medina County.  The application is being reviewed pursuant to Texas Water Code Ann. (TWC) §§ 13.242 to 13.250 and 16 Texas Administrative Code (TAC) §§ 24.101 to 24.107.

Background

The Applicant is seeking to amend a water CCN for the service area containing approximately 850 acres and zero current customers.

Notice

The comment period ended January 29, 2018, and the Commission did not receive any protests or landowner opt out requests.

Criteria Considered

TWC § 13.246(c) requires the Commission to consider nine criteria when granting or amending a CCN.  Therefore, the following criteria were considered:

TWC § 13.246(c)(1) requires the commission to consider the adequacy of service currently provided to the requested area.

The Applicant has a Texas Commission on Environmental Quality (TCEQ) approved public water system, (PWS) No. 1630048. The source of the water supply for the system is a 230 gallons per minute (gpm) well. Given the TCEQ minimum requirement of 0.6 gpm per connection, the well supply is adequate to serve 383 connections, which is therefore adequate to serve the 195 ultimate connections in this application. The rest of the system will consist of three groundwater storage tanks of 20,000 gallons each, two 500 gpm booster pumps for fire flow, two alternating 150 gpm booster pumps for domestic flow, two 4,000-gallon hydro-pneumatic pressure tanks, and a chlorination system. The water system currently has no outstanding violations, according to the TCEQ database.

TWC § 13.246(c)(2) requires the commission to consider the need for service in the requested area.

The Applicant will be the developer of the 870-acre subdivision.  The requested area will be a residential development with 195 single-family homes. Therefore, the requested area will need water utility service.

TWC § 13.246(c)(3) requires the commission to consider the effect of granting certificate or an amendment on the recipient and on any other retail public utility servicing the proximate area.

There will be no effect on any retail public utility servicing the proximate area, as there are no other water providers in the area.

TWC § 13.246(c)(4) requires the commission to consider the ability of the Applicant to provide adequate service.

The Applicant meets the requirements of 16 TAC § 24.105(a)(14)(A) and (B). A TCEQ approval letter dated March 18, 2009, was provided with the application. As mentioned above, the ultimate number of connections for the development is 195 single-family homes. Given TCEQ criteria for water well supply of 0.6 gpm per connection, 200 gallons per connection for total storage, and pump capacity of 2.0 gpm, the water facility has adequate capacity to serve the requested area.

TWC § 13.246(c)(5) requires the commission to consider the feasibility of obtaining service from an adjacent retail public utility.

Currently, there are no other water providers in the area.

TWC § 13.246(c)(6) requires the commission to consider the financial ability of the Applicant to pay for facilities necessary to provide continuous and adequate service.

TWC § 13.246(c)(6) requires the Commission to consider the financial ability of the Applicant to pay for facilities necessary to provide continuous and adequate service and the financial stability of the Applicant.  16 Texas Admin. Code § 24.11 (TAC) establishes criteria to demonstrate that an owner or operator of a retail public utility has the financial resources to operate and manage the utility and to provide continuous and adequate service to the proposed utility service area.  16 TAC § 24.11(e) lists the financial tests.  Staff notes that the following discussion shows that the Applicant meets two of the five leverage tests, of which the Applicant is only required to meet one in order to demonstrate financial capability.  Staff also noted that the Applicant meets the operations test when cash balances were taken into consideration.

- 16 TAC § 24.11(e)(2) refers to the leverage test.  Below is a summary of two leverage tests that were met by the Applicant and the leverage test as it applies to entities who submitted projected financial statements for five years.

  - 16 TAC § 24.11(e)(2)(A) states that the owner or operator must have a debt to equity ratio of one or less than one, using long term debt and equity or net assets.  For 2016-2017, the Applicant does not have a debt to equity ratio since the utility does not have debt ($0 LT debt, $1,065,540.23 equity). The Applicant has met this requirement using the Applicant’s projected financials.

  - 16 TAC § 24.11(e)(2)(C) states the owner or operator must have sufficient unrestricted cash available as a cushion for two years of debt service.  The Applicant has met this requirement using the Applicant’s latest year’s bank statement and projected financials.

  - For 2016-2017, the Applicant has cash balances of $949,657.09 and no debt service.

- 16 TAC § 24.11(e)(3) refers to the operations test.  This states that the owner or operator must demonstrate sufficient cash is available to cover any projected operations and maintenance shortages in the first five years of operations.

The Applicant provided projected financial statements for the next five years 2016-2017 through 2020-2021 as required in 16 TAC § 24.11(e)(4)(B).  Based on the projected financials, year one is projected to be short by $1,251.53 for 2016-2017 that would require coverage through additional cash reserves.  The Applicant has sufficient bank balances of $949,657 to cover the shortage.  The remaining four years are projected to be positive.

TWC §§ 13.246(7) and (9) require the commission to consider the environmental integrity and the effect on the land to be included in the certificate.

The environmental integrity of the land will be altered, because the landowner plans to develop the land in phases. Upon buildout, the development will have 195 single-family homes. The development will have an adequate supply of water and adequate wastewater treatment facilities, which will be provided by onsite septic systems.

TWC § 13.246(8) requires the commission to consider the probable improvement in service or lowering of cost to consumers.

This is not applicable, since there are no homes receiving service in the requested area.

Based on the above information, Staff recommends the Commission approve the application, issue an order and provide the attached map, certificate, and tariff to Summit Ridge LLC. Staff further recommends that the Applicant file certified copies of the CCN map along with a written description of the CCN service area in the county clerk’s office pursuant to TWC §§ 13.257 (r)-(s).