Task Force 2 Issues

Summary of Hurricane Harvey Follow-Up

(See Attachment (Utility Responses) for detailed utility specific responses)

# Hurricane-Related Flood Protection for Electric Utility Facilities

## Describe the extent to which your facilities (e.g. a substation) were flooded as a result of Hurricane Harvey and compare that flooding to prior flooding in at least the 15 years before Hurricane Harvey.

In general, Harvey caused major wind and some storm surge damage from Matagorda Bay and south while making landfall and then caused major flooding over the following days from Victoria and north generally within 90 miles of the coastline along major rivers and tributaries.  Some utilities have experienced previous flooding events, but not to the magnitude of Harvey, with the exception of CenterPoint during Allison in 2001.  Below is a summary of the rainfall totals and notable damages due to flooding during Harvey, with a note of previous substation flooding if applicable.

| HURRICANE HARVEY - NOTABLE FLOOD DAMAGE TO FACILITIES |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Utility | Flooded Substations |  |  |  |  | Transmission Line | Distribution Line | Other Facilities |
|  | Major | Minor | Storm Surge | Previous |  |  |  |  |
| ETI | 6 | 11 |  | 2 |  |  | Yes |  |
| TNMP | 0 | 1 |  |  |  |  | Yes | 1 |
| AEP TX | 0 | 0 | Yes |  |  |  |  |  |
| CNP | 8 | 0 | 0 | Yes |  | 3 River Crossing Structures | Yes, and 83 URD Vaults |  |
| LCRA TSC | 0 | 0 | 0 | Yes |  | No | No | No |
| Sharyland | 0 | 0 | 0 | 0 |  | No | No | No |
| Major - Significant water in control house affecting electronics and/or water affecting electrical equipment within the substation fence. URD - underground. |  |  |  |  |  |  |  |  |

## Describe the steps that you have taken or plan to take in response to flooding resulting from Hurricane Harvey, in order to reduce the risk of flood damage to your facilities in the future.

The 14 substations noted above as having major flooding due to Harvey are in various stages of being rebuilt.  The goal is to rebuild the substation equipment above the Harvey flood levels; however, this is impractical in some cases.  The water sensitive equipment in the major flooded substations are in the process of being raised above the Harvey flood event water levels when practical.  For example, during the restoration of the flooded control houses which required complete replacement of the control house, the foundations were raised at the time of replacement.  This also required replacing all the control wiring from the control house to the controls in the yard.  The yard equipment is also in the process of being raised, but in some instances this was limited due to the clearance to the substation bus.  In these instances, the equipment could not be raised above the Harvey flood level without rebuilding the substation bus framing, which is considered to be impractical.  For the substations noted as having minor flooding, flood mitigation plans are being developed and will be implemented as appropriate to mitigate damaging the water sensitive equipment.  Items being considered include:  Installation of levees, raising equipment, deployment of tiger dams and the use of sandbags at the time of the next event.  The three river (San Jacinto River) crossing transmission structures were damaged due to floating debris and bank erosion.  The new permanent crossings will be constructed using steel poles with deep drilled shafts, and set farther back from the river bank to minimize the impact of floating debris.  CNP has also initiated a study to further understand the options available for protection of transmission structures, in or near flowing water, from floating debris, bank erosion, etc.  Learnings will be evaluated for application throughout the CNP system.

While the Utilities are conducting studies in regard to flood mitigation caused by Hurricane Harvey and on a case by case basis of a 500 year flood event on certain other facilities, the utilities have not conducted a Harvey level, wide area, flood impact analysis on the existing grid beyond the impacted area’s actual experience during Harvey.  In order to perform a wide area flood impact analysis, numerous assumptions would need to be made, substantial data acquired and outside expertise consulted to adequately model the types of impacts that could occur.  For example, the pre- and post-landfall states of the wide area to be studied, including ground saturation, water levels of rivers, creeks, tributaries, lakes and reservoirs, rainfall rates and coverage, duration of the storm, release rates from affected dams, along with other hydrologic and geologic data and forecasting methodologies would have to be incorporated into the analysis.  The utilities believe such a broad, wide area study is currently beyond the capabilities of the utilities’ experts, requiring the use of outside resources, expertise and significant effort to develop consensus on the assumptions to be studied.

## Explain the elevation standard used for facility construction before and after Hurricane Harvey and explain any changes.

The Utilities are not aware of an industry standard for substation elevations.  As such the utilities have developed their individual standards depending on factors such as existing floodplains, coastal storm surge, past experiences, and likelihood of flood events.

The attached spreadsheet summarizes the utilities’ elevation standards.

## What data is used to determine current floodplains / base flood elevations (“BFE”)?  Is there a standard “high-water” elevation, for example: 100 year BFE, 12” above 100 year BFE,  500 year BFE, 12” above Category 5 Storm Surge, 2’ above the 1% FEMA level, 13’ above sea level.

The Utilities are not aware of an industry standard.  The Utilities use various sources, but all consult the FEMA flood plain maps and currently use a minimum of at or one to two feet above the 100 year flood plain.

# Hardening Measures

## Explain whether any hardening measures you took before Hurricane Harvey improved the resilience of your facilities to Hurricane Harvey.  If they did, describe the hardening measures and what caused you to implement them.

The Utilities in Texas have been implementing storm hardening strategies for decades.  Each storm provides the opportunities for improvements on how we prepare and respond to future storms.  These storm hardening strategies have certainly improved the resiliency of the utility grid.  Please refer to the Attachment for details of each utility response.

## Describe the steps that you have taken or plan to take in response to wind damage from Hurricane Harvey, in order to reduce the risk of wind damage to your facilities in the future.

Harvey was not a significant wind event for ETI, TNMP, CNP, LCRA TSC or Sharyland; as such they will continue with implementing their current storm hardening strategies as it relates to wind mitigation.

Harvey was a significant wind event for AEP; as such AEP has taken steps to increase resilience and to promote effective and efficient restoration.  For example, new or replacement facilities will be planned and constructed in alignment with the Company’s current design standards which incorporate lessons learned from extreme weather events such as Hurricane Harvey.  For additional information, please refer to the Utility Responses attachment.

# Explain whether you purchase facilities and materials (e.g. poles) in preparation for hurricane season.

The Utilities in Texas maintain supplies in anticipation of storms.  As a particular hurricane approaches, materials may be moved in anticipation of where the damage is expected.  Most of the distribution line material supply is handled by individual utilities, some of which can rely on other companies within the same corporation.  The Utilities are also in contact with vendors where there are contracts in place for emergency response and expedited availability.  For larger equipment, each utility has its own inventory of spares which can be shared as part of the mutual assistance groups.  The Utilities have damage prediction models, based on past experience, that can predict the damages based on the forecasted track.  If necessary, the utility can place additional equipment orders ahead of the storm.