## Instructions
§25.52. -- Reliability and Continuity of Service.
http://www.puc.state.tx.us/rules/subrules/electric/25.52/25.52.doc
Application. This section applies to all electric utilities as defined by the Public Utility Regulatory Act (PURA) §31.002(6) and all transmission and distribution utilities as defined by PURA §31.002(19). The term "utility" as used in this section shall mean an electric utility and a transmission and distribution utility.
Public Utility Regulatory Act §31.002
http://www.puc.state.tx.us/rules/statutes/index.cfm
DEFINITIONS.
The term "Electric utility" does not include a municipally owned utility or an electric cooperative.
Information typed in highlighted cells will appear on following sheets.
Type Name of Utility in the Cell Below
Utility: |  | TEXAS-NEW MEXICO POWER COMPANY
Type Total Number of Distribution Feeders in the Cell Below
Feeders: |  | 292
Due: |  | February 14, 2018
File: |  | Five Printed Copies and
One Electronic Copy of This Excel File
Project: |  | 47924
Address: |  | Attn: Filing Clerk
Public Utility Commission of Texas
P.O. Box 13326
Austin, Texas 78711-3326
If you have any questions, please contact:
Larry Reed
Infrastructure & Reliability Division
Commission Staff
Voice: | 512 936 7357
Fax: | 512 936 7328
E-mail: | mailto:larry.reed@puc.state.tx.us

## Cover
Service Quality Report
To The
Public Utility Commission of Texas
In Accordance With
16 Texas Admin. Code §25.81
2017 Reporting Year
TEXAS-NEW MEXICO POWER COMPANY
Project 47924

## System-SAIFI
TEXAS-NEW MEXICO POWER COMPANY
System SAIFI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2017 | 0.7254 | 0.0579 | 0.0191 | 0.036 | 0.0453 | 0.0446 | 0.0723 | 0.1082 | 0.1384 | 0.0574 | 0.0686 | 0.0272 | 0.0504
Scheduled
2017 | 0.0409 | 0.0137 | 0.0017 | 0.0018 | 0.0021 | 0.002 | 0.0078 | 0.0018 | 0.0005 | 0.0001 | 0.0086 | 0.0006 | 0.0002
Outside Causes
2017 | 0.0195 | 0.0029 | 0 | 0.0108 | 0 | 0.0044 | 0.0007 | 0 | 0.0007 | 0 | 0 |  | 0
Major Events
2017 | 0.0899 | 0.0245 |  | 0.0063 |  |  |  |  | 0.0591

## System-SAIDI
TEXAS-NEW MEXICO POWER COMPANY
System SAIDI | Annual | Jan | Feb | March | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Forced
2017 | 75.783 | 5.275 | 2.153 | 5.002 | 5.493 | 3.915 | 7.559 | 11.915 | 10.501 | 5.732 | 8.877 | 2.163 | 7.198
Scheduled
2017 | 2.008 | 0.878 | 0.026 | 0.201 | 0.218 | 0.048 | 0.082 | 0.216 | 0.038 | 0.039 | 0.173 | 0.06 | 0.029
Outside Causes
2017 | 2.265 | 0.219 | 0 | 0.846 | 0.001 | 0.561 | 0.454 | 0.001 | 0.137 | 0.002 | 0.001 |  | 0.043
Major Events
2017 | 22.303 | 5.745 |  | 0.585 |  |  |  |  | 15.973

## Feeder-SAIFI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System |  |  |  |  | Total Number of Feeders
With 10 or more Customers |  |  |  |  | 292
Add or Delete Rows as Necessary
2017 SAIFI Ranking | 2016 SAIFI Ranking | Substation Identification | Feeder Identification | Number of Customers | 2017 SAIFI Value
1 | 13 | Winkler County #6 Substation | 25K11 | 42 | 5.0476
2 | 21 | Reeves County #4 Substation | 13P37 | 253 | 4.1541
3 | 40 | Olney Substation | 1695 | 582 | 3.9841
4 | 290 | Lakepointe Substation | 2544 | 784 | 3.9362
5 | 89 | Sycamore Substation | 24105 | 150 | 3.8163
6 | 174 | Farmersville West Substation | 23568 | 15 | 3.3333
7 | 82 | Stafford Substation | 13P50 | 315 | 3.2285
8 | 159 | Tejas Substation | 1217 | 142 | 3.0492
9 | 180 | Coryell County Substation | 22365 | 1008 | 3.0492
10 | 4 | W.D. Faulkner Substation | 12P259 | 119 | 2.9663
11 | 88 | Alvin Substation | 1259 | 735 | 2.5564
12 | 157 | Alvin Substation | 1117 | 1589 | 2.5223
13 | 76 | Whitney Substation | 22455 | 670 | 2.4464
14 | 95 | Nocona Substation | 13374 | 685 | 2.3902
15 | 34 | La Marque Substation | 1204 | 1552 | 2.3692
16 | 123 | IH-20 Substation | 12P566 | 67 | 2.3432
17 | 16 | California Substation | 12K86 | 30 | 2.3333
18 | 79 | Angleton Substation | 1240 | 1551 | 2.2688
19 | 148 | South Substation | 1103 | 1639 | 2.2477
20 | 255 | Glen Rose Substation | 22295 | 800 | 2.2383
21 | 91 | Airport Substation | 12F271 | 110 | 2.2363
22 | 136 | Tejas Substation | 1215 | 1511 | 2.2342
23 | 221 | League City Main Substation | 1284 | 2912 | 2.2032
24 | 252 | Olney Substation | 1690 | 426 | 2.1777
25 | 6 | Keystone Substation | 12K434 | 46 | 2.1739
26 | 170 | Northside Substation | 1294 | 1084 | 2.1559
27 | 26 | Nocona Substation | 12486 | 156 | 2.0714
28 | 256 | Whitewright Substation | 12573 | 188 | 2.0684
29 | 195 | Stafford Substation | 12P83 | 544 | 2.0643
30 | 230 | Lakepointe Substation | 2540 | 561 | 2.032
31 | 11 | Reeves County #4 Substation | 12P28 | 113 | 2.0176
32 | 293 | Frontier Substation | 4236 | 225 | 2.0088
33 | 171 | Pyote Substation | 25P217 | 100 | 1.98
34 | 288 | Westminster Substation | 15800 | 121 | 1.9763
35 | 126 | Angleton Substation | 1244 | 1240 | 1.954
36 | 212 | Lakepointe Substation | 2512 | 2601 | 1.9407
37 | 93 | Worsham Field Substation | 13P98 | 73 | 1.8904
38 | 10 | California Substation | 12K87 | 58 | 1.8103
39 | 164 | Alvin Substation | 1257 | 1986 | 1.8066
40 | 75 | Alvin Substation | 1115 | 2152 | 1.7695
41 | 94 | Thurber Substation | 1490 | 777 | 1.7595
42 | 8 | Dickinson Substation | 1279 | 1965 | 1.7343
43 | 244 | Alvin Substation | 1116 | 1940 | 1.6407
44 | 144 | La Marque Substation | 1202 | 1077 | 1.6276
45 | 117 | Olney Substation | 1685 | 456 | 1.5951
46 | 41 | Worsham Field Substation | 13P97 | 65 | 1.5846
47 | 262 | Kermit #1 Substation | 4K03 | 253 | 1.577
48 | 260 | Longneck Substation | 23130 | 1338 | 1.5537
49 | 280 | Gatesville #2 Substation | 426 | 462 | 1.546
50 | 54 | Alvin Substation | 1230 | 2029 | 1.5362
51 | 120 | Pecos Main Substation | 12P03 | 519 | 1.526
52 | 49 | Dickinson Substation | 1272 | 2536 | 1.5094
53 |  | Cochise Substation | 12P638 | 63 | 1.5079
54 | 39 | Flat Top Substation | 26P01 | 171 | 1.4853
55 | 131 | Whitney Substation | 22450 | 524 | 1.4671
56 | 87 | Northside Substation | 1295 | 2345 | 1.3701
57 | 112 | Freeway Park Substation | 1101 | 1591 | 1.3632
58 | 127 | Dickinson Substation | 1267 | 1850 | 1.3556
59 | 90 | Dickinson Substation | 1274 | 2419 | 1.3555
60 | 98 | Whitney #2 Substation | 22465 | 388 | 1.3342
61 | 167 | Saint Jo Substation | 15757 | 394 | 1.3257
62 | 227 | Airport Substation | 12F44 | 880 | 1.3238
63 | 175 | Friendswood Substation | 1253 | 862 | 1.319
64 | 183 | Pecos Main Substation | 12P02 | 1104 | 1.317
65 | 9 | Krugerville Substation | 2604 | 2310 | 1.3095
66 | 55 | Angleton Substation | 1153 | 2491 | 1.3018
67 | 289 | Kermit #1 Substation | 4K05 | 176 | 1.3011
68 | 111 | Friendswood Substation | 1108 | 1759 | 1.2961
69 | 154 | Lone Star Substation | 25P171 | 62 | 1.2741
70 | 145 | Blossom Substation | 2207 | 123 | 1.2666
71 | 31 | Wickett Substation | 12K446 | 38 | 1.2631
72 | 5 | Sweeny Substation | 1264 | 1322 | 1.2443
73 | 161 | Heights Substation | 1134 | 926 | 1.1997
74 | 32 | Northside Substation | 1293 | 642 | 1.1838
75 | 258 | Jones Street Substation | 1412 | 493 | 1.1825
76 | 242 | Kermit #1 Substation | 4K04 | 475 | 1.1789
77 | 18 | Freeway Park Substation | 1297 | 882 | 1.1575
78 | 77 | Hamilton City Substation | 23825 | 328 | 1.128
79 | 83 | Petrolia Substation | 12260 | 840 | 1.1223
80 | 106 | La Marque Substation | 1205 | 1059 | 1.1085
81 | 35 | Magnolia Substation | 1145 | 398 | 1.1055
82 | 17 | Alvin Substation | 1231 | 2029 | 1.1015
83 | 206 | Freeway Park Substation | 1102 | 1163 | 1.0945
84 | 194 | League City Main Substation | 1280 | 1486 | 1.0942
85 | 37 | Flat Top Substation | 26P02 | 74 | 1.081
86 | 187 | Coryell County Substation | 22160 | 75 | 1.0675
87 | 7 | Cochise Substation | 25P47 | 48 | 1.0625
88 | 108 | Red River Substation | 2262 | 72 | 1.0555
89 | 155 | Hamilton County Substation | 2345 | 217 | 1.0533
90 | 268 | Whitewright Substation | 12575 | 737 | 1.0439
91 | 22 | West Columbia Local Substation | 1233 | 1086 | 1.0313
92 | 178 | Kermit #1 Substation | 4K02 | 228 | 1.0307
93 | 100 | Tejas Substation | 1212 | 284 | 1.0281
94 | 166 | South Shore Substation | 1190 | 2251 | 1.0239
95 | 243 | Walnut Springs Substation | 2200 | 390 | 1.0227
96 | 2 | Texas Instruments Substation | 1033 | 2273 | 1.0219
97 | 253 | Airport Substation | 12F725 | 789 | 1.0139
98 | 208 | Pecos Main Substation | 12P366 | 313 | 0.9968
99 | 246 | Meridian Substation | 690 | 243 | 0.9878
100 | 124 | West Columbia Local Substation | 1234 | 1075 | 0.9786
101 | 228 | South Shore Substation | 1195 | 1194 | 0.9757
102 | 81 | Pyote Substation | 25P312 | 188 | 0.9734
103 | 134 | Clifton #1 22KV Substation | 22480 | 122 | 0.9485
104 | 115 | Glen Rose Substation | 22285 | 396 | 0.8946
105 | 278 | Clifton #1 22KV Substation | 22495 | 334 | 0.8902
106 | 158 | IH-20 Substation | 12P563 | 212 | 0.849
107 | 33 | League City Main Substation | 1011 | 191 | 0.7905
108 | 125 | Brazoria Substation | 1291 | 694 | 0.7694
109 | 181 | West Columbia Local Substation | 1235 | 787 | 0.7471
110 | 24 | Red River Substation | 2252 | 1132 | 0.7135
111 | 38 | Walnut Springs Substation | 2210 | 459 | 0.7126
112 | 92 | Cochise Substation | 12P637 | 41 | 0.7073
113 | 130 | La Marque Substation | 1203 | 465 | 0.6989
114 | 105 | South Shore Substation | 1192 | 1736 | 0.6768
115 | 101 | Nocona Substation | 13370 | 692 | 0.6728
116 | 53 | Keystone Substation | 12K437 | 697 | 0.6025
117 | 28 | Kermit #2 Substation | 12K48 | 595 | 0.5983
118 | 96 | Red River Substation | 2229 | 344 | 0.5972
119 | 133 | Tolar Substation | 25860 | 570 | 0.5933
120 | 257 | Glen Rose Substation | 22305 | 300 | 0.5907
121 | 25 | Brazoria Substation | 1271 | 1754 | 0.5798
122 | 137 | Sweeny Substation | 1128 | 1439 | 0.5774
123 | 198 | Old Ocean Substation | 1261 | 184 | 0.5706
124 | 69 | Gatesville #2 Substation | 23065 | 523 | 0.5705
125 | 204 | Whitewright Substation | 12698 | 919 | 0.5647
126 | 292 | Sanderson Substation | 4S28 | 276 | 0.5579
127 | 109 | Lone Oak Substation | 13388 | 474 | 0.5576
128 | 142 | Lone Star Substation | 25P174 | 36 | 0.5555
129 | 107 | Angleton Substation | 1155 | 1129 | 0.5358
130 | 27 | Lakepointe Substation | 2508 | 411 | 0.5182
131 | 99 | Jones Street Substation | 1433 | 1035 | 0.5033
132 | 97 | Blossom Substation | 2203 | 1383 | 0.4924
133 | 225 | Lake Whitney Substation | 1230 | 506 | 0.445
134 | 110 | Friendswood Substation | 1109 | 1534 | 0.4445
135 | 146 | Emory Substation (ONCOR) | 1201 | 937 | 0.4399
136 | 45 | Alvin Substation | 1232 | 1245 | 0.4369
137 | 209 | Walnut Springs Substation | 2215 | 119 | 0.4365
138 | 147 | South Substation | 1108 | 1937 | 0.4357
139 | 66 | Sweeny Substation | 1129 | 690 | 0.4318
140 | 169 | Magnolia Substation | 1149 | 1590 | 0.4163
141 | 177 | Northside Substation | 1292 | 780 | 0.4128
142 | 190 | Gatesville #2 Substation | 22725 | 467 | 0.4081
143 | 150 | Friendswood Substation | 1251 | 1803 | 0.3993
144 | 132 | La Marque Substation | 1201 | 908 | 0.3986
145 | 139 | Deport Substation (ONCOR) | 22164 | 581 | 0.3793
146 | 140 | Brazoria Substation | 1270 | 1028 | 0.3735
147 | 3 | Flat Top Substation | 26P03 | 78 | 0.3717
148 | 70 | Kermit #2 Substation | 4K06 | 216 | 0.3518
149 | 163 | Angleton Substation | 1241 | 1575 | 0.3333
150 | 85 | Magnolia Substation | 1144 | 1390 | 0.3273
151 | 229 | West Substation | 1221 | 1931 | 0.3184
152 | 42 | Hill County Substation | 23340 | 607 | 0.3162
153 | 156 | Dickinson Substation | 1277 | 1705 | 0.3102
154 | 149 | League City Main Substation | 1283 | 2056 | 0.3054
155 | 121 | League City Main Substation | 1012 | 946 | 0.3012
156 | 80 | Glen Rose Substation | 22300 | 1160 | 0.3
157 | 118 | Leonard Substation | 12678 | 524 | 0.2998
158 | 1 | Friendswood Substation | 1107 | 1783 | 0.2978
159 | 168 | Dickinson Substation | 1266 | 633 | 0.2954
160 | 84 | Graham Substation | 12605 | 132 | 0.289
161 | 47 | Thurber Substation | 1447 | 617 | 0.2887
162 | 141 | Freeway Park Substation | 1103 | 1457 | 0.2786
163 | 114 | Heights Substation | 1132 | 2286 | 0.2751
164 | 254 | Jones Street Substation | 1413 | 81 | 0.2716
165 | 128 | League City Main Substation | 1285 | 1238 | 0.2625
166 | 294 | Stafford Substation | 12P99 | 305 | 0.259
167 | 184 | Seminole Substation | 1402 | 1381 | 0.2577
168 | 86 | Graham Substation | 1245 | 145 | 0.2571
169 | 56 | Northside Substation | 1228 | 1154 | 0.2564
170 | 138 | South Bend Substation | 1300 | 165 | 0.2532
171 | 29 | Magnolia Substation | 1148 | 2251 | 0.2398
172 | 113 | West Substation | 1235 | 1598 | 0.239
173 | 160 | Westminster Substation | 15804 | 401 | 0.2371
174 | 63 | Clifton #1 22KV Substation | 22485 | 106 | 0.2358
175 | 153 | Angleton Substation | 1243 | 1341 | 0.2244
176 | 58 | Jones Street Substation | 1411 | 1828 | 0.2193
177 | 281 | Leonard Substation | 12682 | 247 | 0.2177
178 | 116 | Freeway Park Substation | 1299 | 859 | 0.2165
179 | 15 | Angleton Substation | 1154 | 1869 | 0.2118
180 | 205 | Leonard Substation | 14631 | 449 | 0.2082
181 | 272 | Longneck Substation | 23126 | 1315 | 0.2031
182 | 152 | Handley Substation | 22825 | 483 | 0.2024
183 | 102 | League City Main Substation | 1282 | 2042 | 0.1993
184 | 151 | Krugerville Substation | 2608 | 2074 | 0.1959
185 | 52 | Angleton Substation | 1245 | 903 | 0.1771
186 | 103 | Bryson Substation | 1230 | 439 | 0.1753
187 | 270 | Farmersville West Substation | 23560 | 493 | 0.1733
188 | 43 | Angleton Substation | 1242 | 533 | 0.1669
189 | 129 | Heights Substation | 1222 | 626 | 0.1645
190 | 210 | Blue Ridge Substation | 22700 | 488 | 0.1591
191 | 36 | Friendswood Substation | 1252 | 1710 | 0.1561
192 | 186 | South Shore Substation | 1196 | 1438 | 0.1543
193 | 23 | Pecos Main Substation | 12P362 | 1050 | 0.1542
194 | 51 | Meridian Substation | 23210 | 848 | 0.1509
195 | 238 | South Shore Substation | 1191 | 1854 | 0.1504
196 | 173 | Freeway Park Substation | 1298 | 2144 | 0.145
197 | 46 | Cochise Substation | 25P48 | 235 | 0.1446
198 | 248 | Stafford Substation | 12P82 | 320 | 0.1406
199 | 162 | League City Main Substation | 1010 | 1030 | 0.13
200 | 261 | Texas Instruments Substation | 1013 | 1830 | 0.1284
201 |  | Walnut Springs Substation | 25925 | 51 | 0.1276
202 | 234 | Lake Whitney Substation | 12355 | 868 | 0.1271
203 | 207 | La Marque Substation | 1110 | 376 | 0.125
204 | 236 | Saint Jo Substation | 15761 | 215 | 0.1244
205 | 19 | Wickett Substation | 12K449 | 203 | 0.1231
206 | 185 | Hamilton County Substation | 2340 | 144 | 0.1188
207 | 44 | Hill County Substation | 22125 | 462 | 0.1166
208 | 273 | Leonard Substation | 14635 | 511 | 0.1139
209 | 135 | Heights Substation | 1224 | 1578 | 0.1089
210 | 122 | Lone Oak Substation | 13384 | 372 | 0.1031
211 | 269 | Whitewright Substation | 12574 | 307 | 0.1009
212 | 199 | Texas Instruments Substation | 1032 | 3632 | 0.0982
213 | 59 | Meridian Substation | 23205 | 349 | 0.0919
214 | 179 | Jones Street Substation | 1431 | 902 | 0.0909
215 | 74 | Brazoria Substation | 1290 | 1050 | 0.0885
216 | 143 | Hamilton City Substation | 22780 | 661 | 0.0877
217 | 65 | Valley Mills Substation | 22570 | 453 | 0.0871
218 | 68 | West Substation | 1223 | 2391 | 0.0861
219 | 165 | Alvin Substation | 1254 | 1839 | 0.0842
220 | 271 | Climax Substation | 22110 | 1079 | 0.0821
221 | 214 | Pecos Main Substation | 12P01 | 220 | 0.0818
222 | 12 | Kermit #2 Substation | 12K98 | 307 | 0.0749
223 | 241 | Magnolia Substation | 1150 | 732 | 0.0737
224 | 203 | Old Ocean Substation | 1262 | 505 | 0.0712
225 | 188 | Hamilton County Substation | 24015 | 616 | 0.069
226 | 71 | Kermit #2 Substation | 4K07 | 331 | 0.0664
227 | 201 | 16th Street Substation | 12F72 | 452 | 0.0641
228 | 193 | Hico City Substation | 395 | 534 | 0.0636
229 | 176 | Clifton #2 Substation | 24370 | 227 | 0.0625
230 | 48 | Hamilton City Substation | 22785 | 369 | 0.0601
231 | 50 | Sweeny Substation | 1263 | 558 | 0.0591
232 | 20 | South Substation | 1107 | 1330 | 0.0571
233 | 62 | South Substation | 1109 | 809 | 0.0568
234 | 235 | West Substation | 1202 | 997 | 0.0551
235 | 57 | Magnolia Substation | 1146 | 2655 | 0.0531
236 | 216 | West Substation | 1222 | 1432 | 0.0516
237 | 218 | South Substation | 1104 | 3510 | 0.0504
238 | 219 | Belding Substation | 12F161 | 40 | 0.05
239 | 226 | Bryson Substation | 1233 | 186 | 0.0439
240 | 223 | Nocona Substation | 12490 | 307 | 0.0423
241 | 239 | Glen Rose Substation | 23875 | 870 | 0.0416
242 | 78 | Valley Mills Substation | 22575 | 673 | 0.0398
243 | 72 | Seminole Substation | 1404 | 1865 | 0.0386
244 | 264 | Butler Road Substation | 1436 | 3828 | 0.0378
245 | 232 | Downtown 12.5KV Substation | 12F114 | 619 | 0.0371
246 | 191 | South Shore Substation | 1194 | 1952 | 0.0368
247 | 30 | Nocona Substation | 13610 | 676 | 0.0349
248 | 14 | Tejas Substation | 1214 | 587 | 0.034
249 | 222 | Downtown 12.5KV Substation | 12F520 | 368 | 0.0326
250 | 196 | Lakepointe Substation | 2536 | 1501 | 0.0319
251 | 119 | West Columbia Local Substation | 1237 | 782 | 0.0319
252 | 200 | Old Ocean Substation | 1260 | 66 | 0.0303
253 | 247 | Valley Mills Substation | 22565 | 423 | 0.0275
254 | 61 | South Substation | 1102 | 1476 | 0.0271
255 | 67 | Seminole Substation | 1403 | 1077 | 0.025
256 | 220 | Coryell County Substation | 22155 | 852 | 0.0244
257 | 267 | Sanderson Substation | 4S26 | 236 | 0.0211
258 | 217 | Sanderson Substation | 4S27 | 104 | 0.0192
259 | 274 | Clifton #2 Substation | 4165 | 312 | 0.019
260 | 172 | Hico City Substation | 390 | 271 | 0.0187
261 | 197 | Thurber Substation | 22890 | 417 | 0.0166
262 | 202 | Handley Substation | 22820 | 68 | 0.0147
263 | 245 | Whitewright Substation | 13563 | 351 | 0.0142
264 | 276 | Clifton #1 4KV Substation | 407 | 141 | 0.014
265 | 265 | Gatesville #2 Substation | 429 | 435 | 0.0139
266 | 211 | 16th Street Substation | 12F71 | 1120 | 0.0133
267 | 284 | Clifton #2 Substation | 23165 | 85 | 0.0114
268 | 182 | Hamilton City Substation | 23820 | 203 | 0.0099
269 | 237 | Downtown 12.5KV Substation | 12F130 | 1041 | 0.0096
270 | 192 | West Substation | 1234 | 1496 | 0.0086
271 | 60 | Texas Instruments Substation | 1012 | 1425 | 0.0063
272 | 240 | Stafford Substation | 12P50 | 319 | 0.0062
273 | 279 | Butler Road Substation | 1437 | 166 | 0.006
274 | 266 | Trenton Substation | 4120 | 209 | 0.0047
275 | 251 | West Substation | 1201 | 708 | 0.0042
276 | 104 | West Substation | 1233 | 596 | 0.0016
277 | 277 | Clifton #1 4KV Substation | 405 | 229
278 | 283 | Puckett Substation | 25F18 | 33
279 | 249 | Puckett Substation | 25F14 | 54
280 | 282 | Gomez Substation | 25F61 | 18
281 | 215 | Gomez Substation | 25F05 | 25
282 | 231 | Belding Substation | 12F164 | 19
283 | 291 | Talco West Substation | 22237 | 31
284 | 213 | West Substation | 1203 | 910
285 | 64 | Clifton #2 Substation | 4160 | 499
286 | 250 | League City Main Substation | 1281 | 760
287 | 287 | Lakepointe Substation | 2524 | 974
288 | 189 | Lakepointe Substation | 2516 | 897
289 | 285 | Whitney #2 Substation | 22460 | 527
290 | 73 | Sycamore Substation | 24100 | 27
291 | 263 | Meridian Substation | 680 | 307
292 | 286 | 16th Street Substation | 13F14 | 343

## Feeder-SAIDI
Distribution Feeder Indices for Forced Interruptions
List all Distribution Feeders on Texas System |  |  |  |  | Total Number of Feeders
With 10 or more Customers |  |  |  |  | 292
Add or Delete Rows as Necessary
2017 SAIDI Ranking | 2016 SAIDI Ranking | Substation Identification | Feeder Identification | Number of Customers | 2017 SAIDI Value
1 | 3 | Winkler County #6 Substation | 25K11 | 42 | 937.3095
2 | 259 | Whitewright Substation | 12573 | 188 | 640.2
3 | 59 | Pyote Substation | 25P217 | 100 | 613.6
4 | 1 | California Substation | 12K86 | 30 | 579.3333
5 | 149 | IH-20 Substation | 12P566 | 67 | 570.5074
6 | 187 | Farmersville West Substation | 23568 | 15 | 569.5333
7 | 42 | Dickinson Substation | 1279 | 1965 | 527.7694
8 | 290 | Frontier Substation | 4236 | 225 | 517.8362
9 | 4 | W.D. Faulkner Substation | 12P259 | 119 | 456.3109
10 | 102 | Sycamore Substation | 24105 | 150 | 406.102
11 | 287 | Westminster Substation | 15800 | 121 | 385.8818
12 | 71 | Angleton Substation | 1240 | 1551 | 373.0638
13 | 2 | Keystone Substation | 12K434 | 46 | 351.3043
14 | 89 | Airport Substation | 12F271 | 110 | 346.6272
15 | 177 | IH-20 Substation | 12P563 | 212 | 346.033
16 | 66 | Worsham Field Substation | 13P98 | 73 | 338.5616
17 | 52 | Olney Substation | 1695 | 582 | 327.4797
18 | 12 | Reeves County #4 Substation | 12P28 | 113 | 311.4513
19 |  | Cochise Substation | 12P638 | 63 | 305.8571
20 | 53 | Nocona Substation | 13374 | 685 | 296.3601
21 | 175 | Northside Substation | 1294 | 1084 | 294.7758
22 | 292 | Lakepointe Substation | 2544 | 784 | 282.4502
23 | 15 | Reeves County #4 Substation | 13P37 | 253 | 272.3241
24 | 155 | Angleton Substation | 1244 | 1240 | 265.2733
25 | 106 | South Substation | 1103 | 1639 | 262.1866
26 | 236 | Airport Substation | 12F44 | 880 | 245.1988
27 | 57 | La Marque Substation | 1204 | 1552 | 240.0451
28 | 9 | Wickett Substation | 12K446 | 38 | 236.7894
29 | 14 | Cochise Substation | 25P47 | 48 | 235.7708
30 | 100 | Pecos Main Substation | 12P03 | 519 | 234.5722
31 | 219 | Old Ocean Substation | 1261 | 184 | 234.5271
32 | 174 | La Marque Substation | 1202 | 1077 | 228.4558
33 | 64 | League City Main Substation | 1011 | 191 | 221.0418
34 | 47 | Nocona Substation | 12486 | 156 | 217.422
35 | 8 | Magnolia Substation | 1145 | 398 | 215.9497
36 | 257 | Airport Substation | 12F725 | 789 | 212.0874
37 | 203 | Pecos Main Substation | 12P02 | 1104 | 211.4193
38 | 214 | Whitewright Substation | 12698 | 919 | 211.3771
39 | 61 | Whitney Substation | 22455 | 670 | 208.619
40 | 132 | Alvin Substation | 1117 | 1589 | 203.9811
41 | 137 | Alvin Substation | 1257 | 1986 | 203.7356
42 | 228 | Lakepointe Substation | 2540 | 561 | 195.6417
43 | 248 | Glen Rose Substation | 22295 | 800 | 195.3011
44 | 258 | Olney Substation | 1690 | 426 | 192.8388
45 | 11 | Sweeny Substation | 1264 | 1322 | 192.8101
46 | 121 | Thurber Substation | 1490 | 777 | 190.6624
47 | 20 | Flat Top Substation | 26P02 | 74 | 184.1756
48 | 142 | Olney Substation | 1685 | 456 | 183.4048
49 | 58 | Alvin Substation | 1259 | 735 | 180.5619
50 | 205 | Friendswood Substation | 1253 | 862 | 168.2784
51 | 18 | Flat Top Substation | 26P01 | 171 | 166.5672
52 | 122 | West Columbia Local Substation | 1234 | 1075 | 164.9944
53 | 7 | Texas Instruments Substation | 1033 | 2273 | 164.4232
54 | 38 | Pyote Substation | 25P312 | 188 | 163.0478
55 | 280 | Gatesville #2 Substation | 426 | 462 | 159.3596
56 | 109 | Freeway Park Substation | 1101 | 1591 | 158.7146
57 | 117 | Saint Jo Substation | 15757 | 394 | 156.6565
58 | 184 | Coryell County Substation | 22365 | 1008 | 155.2568
59 | 119 | Glen Rose Substation | 22285 | 396 | 155.1519
60 | 67 | Alvin Substation | 1115 | 2152 | 154.0803
61 | 120 | Friendswood Substation | 1108 | 1759 | 153.7629
62 | 211 | Lakepointe Substation | 2512 | 2601 | 151.0865
63 | 208 | League City Main Substation | 1284 | 2912 | 140.3619
64 | 159 | Tejas Substation | 1217 | 142 | 137.9577
65 | 10 | California Substation | 12K87 | 58 | 135.6896
66 | 90 | La Marque Substation | 1203 | 465 | 133.7247
67 | 113 | Dickinson Substation | 1267 | 1850 | 133.0643
68 | 75 | Petrolia Substation | 12260 | 840 | 131.6021
69 | 136 | Tejas Substation | 1215 | 1511 | 125.6419
70 | 87 | Dickinson Substation | 1272 | 2536 | 124.4917
71 | 68 | Dickinson Substation | 1274 | 2419 | 122.9756
72 | 233 | Walnut Springs Substation | 2200 | 390 | 119.4444
73 | 225 | Stafford Substation | 12P83 | 544 | 119.2242
74 | 97 | Westminster Substation | 15804 | 401 | 117.2176
75 | 34 | Worsham Field Substation | 13P97 | 65 | 115.6615
76 | 44 | Stafford Substation | 13P50 | 315 | 114.8666
77 | 157 | West Substation | 1221 | 1931 | 110.0947
78 | 111 | Hamilton County Substation | 2345 | 217 | 106.3644
79 | 124 | Whitney Substation | 22450 | 524 | 106.1698
80 | 249 | Jones Street Substation | 1412 | 493 | 106.0385
81 | 36 | West Columbia Local Substation | 1233 | 1086 | 105.4659
82 | 152 | Lone Star Substation | 25P174 | 36 | 103.8611
83 | 49 | Red River Substation | 2229 | 344 | 102.1416
84 | 54 | Northside Substation | 1295 | 2345 | 100.9867
85 | 24 | Cochise Substation | 12P637 | 41 | 97.5853
86 | 158 | Lone Star Substation | 25P171 | 62 | 96.6935
87 | 84 | Lone Oak Substation | 13388 | 474 | 96.0555
88 | 56 | Alvin Substation | 1230 | 2029 | 88.7432
89 | 60 | Northside Substation | 1293 | 642 | 88.3629
90 | 79 | Whitney #2 Substation | 22465 | 388 | 88.3131
91 | 160 | Dickinson Substation | 1266 | 633 | 88.2259
92 | 22 | Krugerville Substation | 2604 | 2310 | 87.9025
93 | 150 | Nocona Substation | 13370 | 692 | 87.1114
94 | 96 | Sweeny Substation | 1128 | 1439 | 86.4933
95 | 65 | South Shore Substation | 1192 | 1736 | 84.7246
96 | 72 | South Substation | 1108 | 1937 | 84.272
97 | 41 | Red River Substation | 2252 | 1132 | 83.5061
98 | 115 | Hamilton City Substation | 23825 | 328 | 82.442
99 | 222 | Pecos Main Substation | 12P366 | 313 | 81.738
100 | 107 | Jones Street Substation | 1433 | 1035 | 80.2309
101 | 148 | Emory Substation (ONCOR) | 1201 | 937 | 79.4817
102 | 80 | Tejas Substation | 1212 | 284 | 75.8661
103 | 93 | Blossom Substation | 2203 | 1383 | 75.1101
104 | 238 | Alvin Substation | 1116 | 1940 | 74.6448
105 | 265 | Longneck Substation | 23130 | 1338 | 74.1341
106 | 128 | La Marque Substation | 1201 | 908 | 72.6277
107 | 116 | Keystone Substation | 12K437 | 697 | 72.4404
108 | 108 | Friendswood Substation | 1109 | 1534 | 72.3383
109 | 166 | Tolar Substation | 25860 | 570 | 71.9647
110 | 45 | Gatesville #2 Substation | 23065 | 523 | 71.1895
111 | 153 | South Shore Substation | 1190 | 2251 | 70.4837
112 | 28 | Alvin Substation | 1231 | 2029 | 69.9226
113 | 169 | Northside Substation | 1292 | 780 | 69.0397
114 | 83 | Hill County Substation | 23340 | 607 | 68.4238
115 | 261 | Kermit #1 Substation | 4K03 | 253 | 67.7984
116 | 112 | Blossom Substation | 2207 | 123 | 67.7583
117 | 209 | West Columbia Local Substation | 1235 | 787 | 65.4396
118 | 85 | Angleton Substation | 1153 | 2491 | 64.7796
119 | 283 | Sanderson Substation | 4S28 | 276 | 64.7717
120 | 95 | Red River Substation | 2262 | 72 | 63.7638
121 | 196 | South Shore Substation | 1195 | 1194 | 63.4212
122 | 144 | Kermit #2 Substation | 4K06 | 216 | 62.8055
123 | 163 | Brazoria Substation | 1291 | 694 | 61.2334
124 | 156 | League City Main Substation | 1285 | 1238 | 60.7899
125 | 186 | Magnolia Substation | 1149 | 1590 | 57.0484
126 | 151 | Heights Substation | 1134 | 926 | 53.501
127 | 244 | Kermit #1 Substation | 4K04 | 475 | 53.1094
128 | 76 | Graham Substation | 12605 | 132 | 52.9062
129 | 43 | Jones Street Substation | 1411 | 1828 | 52.2073
130 | 27 | Brazoria Substation | 1271 | 1754 | 52.0171
131 | 277 | Kermit #1 Substation | 4K05 | 176 | 50.5113
132 | 6 | Flat Top Substation | 26P03 | 78 | 50.2179
133 | 77 | Alvin Substation | 1232 | 1245 | 49.9477
134 | 180 | League City Main Substation | 1280 | 1486 | 49.5006
135 | 260 | Glen Rose Substation | 22305 | 300 | 48.8943
136 | 17 | Lakepointe Substation | 2508 | 411 | 48.27
137 | 138 | League City Main Substation | 1283 | 2056 | 47.211
138 | 82 | Heights Substation | 1132 | 2286 | 46.6776
139 | 51 | Sweeny Substation | 1129 | 690 | 45.6681
140 | 32 | Walnut Springs Substation | 2210 | 459 | 43.8663
141 | 141 | Freeway Park Substation | 1103 | 1457 | 42.4021
142 | 139 | Deport Substation (ONCOR) | 22164 | 581 | 41.9562
143 | 162 | Leonard Substation | 12678 | 524 | 41.6015
144 | 191 | Walnut Springs Substation | 2215 | 119 | 39.9603
145 | 217 | Meridian Substation | 690 | 243 | 39.4898
146 | 101 | Friendswood Substation | 1251 | 1803 | 38.7021
147 | 161 | Brazoria Substation | 1270 | 1028 | 38.6848
148 | 5 | Friendswood Substation | 1107 | 1783 | 37.5765
149 | 154 | Angleton Substation | 1155 | 1129 | 37.3746
150 | 291 | Stafford Substation | 12P99 | 305 | 37.0393
151 | 133 | West Substation | 1235 | 1598 | 36.5782
152 | 104 | La Marque Substation | 1205 | 1059 | 35.1114
153 | 37 | Freeway Park Substation | 1297 | 882 | 34.6655
154 | 185 | Coryell County Substation | 22160 | 75 | 33.9324
155 | 73 | Cochise Substation | 25P48 | 235 | 33.8
156 | 273 | Leonard Substation | 12682 | 247 | 33.262
157 | 123 | Dickinson Substation | 1277 | 1705 | 32.5571
158 | 125 | Handley Substation | 22825 | 483 | 32.283
159 | 213 | Kermit #1 Substation | 4K02 | 228 | 32.0043
160 | 50 | Thurber Substation | 1447 | 617 | 31.7732
161 | 147 | South Bend Substation | 1300 | 165 | 31.5714
162 | 118 | Freeway Park Substation | 1299 | 859 | 31.1292
163 | 230 | Lake Whitney Substation | 1230 | 506 | 30.5509
164 | 140 | Clifton #1 22KV Substation | 22480 | 122 | 29.9338
165 | 70 | Kermit #2 Substation | 12K48 | 595 | 29.1865
166 | 206 | Gatesville #2 Substation | 22725 | 467 | 28.3888
167 | 23 | Angleton Substation | 1154 | 1869 | 27.8191
168 | 181 | Angleton Substation | 1241 | 1575 | 27.1733
169 | 35 | Magnolia Substation | 1148 | 2251 | 27.1168
170 | 105 | Magnolia Substation | 1144 | 1390 | 26.0935
171 | 250 | Jones Street Substation | 1413 | 81 | 25
172 | 99 | Pecos Main Substation | 12P362 | 1050 | 24.5304
173 | 127 | Heights Substation | 1222 | 626 | 24.4089
174 | 91 | Clifton #1 22KV Substation | 22485 | 106 | 24.1509
175 | 39 | Glen Rose Substation | 22300 | 1160 | 23.8576
176 | 131 | League City Main Substation | 1012 | 946 | 23.3361
177 | 198 | Seminole Substation | 1402 | 1381 | 23.2809
178 | 256 | Whitewright Substation | 12575 | 737 | 22.5618
179 | 272 | Farmersville West Substation | 23560 | 493 | 22.5371
180 | 207 | Freeway Park Substation | 1102 | 1163 | 22.4393
181 | 13 | Wickett Substation | 12K449 | 203 | 22.2512
182 | 98 | Graham Substation | 1245 | 145 | 22.2285
183 | 267 | Whitewright Substation | 12574 | 307 | 21.57
184 | 86 | Bryson Substation | 1230 | 439 | 20.4123
185 | 103 | Northside Substation | 1228 | 1154 | 19.9748
186 | 164 | Krugerville Substation | 2608 | 2074 | 19.9706
187 | 231 | South Shore Substation | 1191 | 1854 | 19.268
188 | 271 | Longneck Substation | 23126 | 1315 | 19.2182
189 | 130 | League City Main Substation | 1282 | 2042 | 18.8437
190 | 188 | Blue Ridge Substation | 22700 | 488 | 18.4263
191 | 167 | La Marque Substation | 1110 | 376 | 18.3351
192 | 55 | West Substation | 1223 | 2391 | 17.9272
193 | 285 | Clifton #1 22KV Substation | 22495 | 334 | 17.27
194 | 254 | Stafford Substation | 12P82 | 320 | 16.9656
195 | 189 | Hamilton County Substation | 2340 | 144 | 16.8811
196 | 69 | Meridian Substation | 23210 | 848 | 16.7391
197 | 176 | Angleton Substation | 1243 | 1341 | 15.6689
198 | 135 | Freeway Park Substation | 1298 | 2144 | 15.2887
199 | 31 | Friendswood Substation | 1252 | 1710 | 14.9005
200 | 182 | Leonard Substation | 14631 | 449 | 14.629
201 | 263 | Texas Instruments Substation | 1013 | 1830 | 13.2349
202 | 62 | Angleton Substation | 1242 | 533 | 12.8499
203 | 247 | Saint Jo Substation | 15761 | 215 | 12.5437
204 | 202 | South Shore Substation | 1196 | 1438 | 12.2878
205 | 134 | Heights Substation | 1224 | 1578 | 12.133
206 |  | Walnut Springs Substation | 25925 | 51 | 11.4893
207 | 229 | Pecos Main Substation | 12P01 | 220 | 11.3727
208 | 268 | Climax Substation | 22110 | 1079 | 11.2465
209 | 192 | Texas Instruments Substation | 1032 | 3632 | 11.2053
210 | 223 | West Substation | 1202 | 997 | 11.0732
211 | 204 | South Substation | 1104 | 3510 | 10.8427
212 | 168 | Hamilton County Substation | 24015 | 616 | 10.6741
213 | 170 | Alvin Substation | 1254 | 1839 | 10.0342
214 | 94 | Hill County Substation | 22125 | 462 | 10.0166
215 | 143 | Meridian Substation | 23205 | 349 | 9.658
216 | 221 | Lake Whitney Substation | 12355 | 868 | 9.6071
217 | 220 | Old Ocean Substation | 1262 | 505 | 9.5089
218 | 21 | South Substation | 1107 | 1330 | 9.2624
219 | 195 | West Substation | 1222 | 1432 | 7.8519
220 | 293 | Leonard Substation | 14635 | 511 | 7.6365
221 | 165 | Hamilton City Substation | 22780 | 661 | 7.4977
222 | 146 | Kermit #2 Substation | 4K07 | 331 | 7.4652
223 | 110 | Brazoria Substation | 1290 | 1050 | 7.3447
224 | 92 | Hamilton City Substation | 22785 | 369 | 7.2513
225 | 126 | Jones Street Substation | 1431 | 902 | 7.2339
226 | 145 | Valley Mills Substation | 22570 | 453 | 6.4575
227 | 33 | Lone Oak Substation | 13384 | 372 | 6.3439
228 | 114 | South Substation | 1109 | 809 | 5.7762
229 | 240 | Belding Substation | 12F161 | 40 | 5.775
230 | 46 | Kermit #2 Substation | 12K98 | 307 | 5.5439
231 | 88 | Angleton Substation | 1245 | 903 | 5.5337
232 | 234 | Magnolia Substation | 1150 | 732 | 5.5245
233 | 78 | Magnolia Substation | 1146 | 2655 | 5.4538
234 | 172 | Hico City Substation | 395 | 534 | 5.043
235 | 190 | League City Main Substation | 1010 | 1030 | 4.8
236 | 269 | Sanderson Substation | 4S26 | 236 | 4.5635
237 | 278 | Clifton #2 Substation | 4165 | 312 | 4.3968
238 | 224 | Glen Rose Substation | 23875 | 870 | 4.0764
239 | 40 | Seminole Substation | 1404 | 1865 | 4.0294
240 | 216 | Coryell County Substation | 22155 | 852 | 3.7476
241 | 193 | Lakepointe Substation | 2536 | 1501 | 3.6155
242 | 235 | 16th Street Substation | 12F72 | 452 | 3.3561
243 | 30 | South Substation | 1102 | 1476 | 3.2804
244 | 26 | Tejas Substation | 1214 | 587 | 3.2385
245 | 201 | South Shore Substation | 1194 | 1952 | 3.2377
246 | 215 | Bryson Substation | 1233 | 186 | 3.1538
247 | 226 | Downtown 12.5KV Substation | 12F520 | 368 | 3.1222
248 | 227 | Nocona Substation | 12490 | 307 | 3.1009
249 | 19 | Valley Mills Substation | 22575 | 673 | 3.0014
250 | 16 | Sweeny Substation | 1263 | 558 | 2.9247
251 | 275 | Clifton #1 4KV Substation | 407 | 141 | 2.8943
252 | 255 | Butler Road Substation | 1436 | 3828 | 2.8845
253 | 239 | Valley Mills Substation | 22565 | 423 | 2.7591
254 | 171 | Hico City Substation | 390 | 271 | 2.7518
255 | 242 | Whitewright Substation | 13563 | 351 | 2.6524
256 | 173 | Old Ocean Substation | 1260 | 66 | 2.5757
257 | 245 | Downtown 12.5KV Substation | 12F114 | 619 | 2.2617
258 | 29 | Nocona Substation | 13610 | 676 | 2.2597
259 | 179 | Clifton #2 Substation | 24370 | 227 | 1.875
260 | 178 | Handley Substation | 22820 | 68 | 1.5441
261 | 183 | West Substation | 1234 | 1496 | 1.5207
262 | 63 | Seminole Substation | 1403 | 1077 | 1.4187
263 | 266 | Gatesville #2 Substation | 429 | 435 | 1.4079
264 | 197 | Downtown 12.5KV Substation | 12F130 | 1041 | 1.3823
265 | 194 | 16th Street Substation | 12F71 | 1120 | 1.3321
266 | 218 | Thurber Substation | 22890 | 417 | 1.1309
267 | 210 | Hamilton City Substation | 23820 | 203 | 1.0895
268 | 129 | West Columbia Local Substation | 1237 | 782 | 0.9398
269 | 232 | Sanderson Substation | 4S27 | 104 | 0.8653
270 | 286 | Clifton #2 Substation | 23165 | 85 | 0.6896
271 | 25 | Texas Instruments Substation | 1012 | 1425 | 0.6245
272 | 81 | West Substation | 1233 | 596 | 0.4697
273 | 264 | Trenton Substation | 4120 | 209 | 0.4407
274 | 252 | Stafford Substation | 12P50 | 319 | 0.3824
275 | 281 | Butler Road Substation | 1437 | 166 | 0.3614
276 | 246 | West Substation | 1201 | 708 | 0.233
277 | 284 | Puckett Substation | 25F18 | 33
278 | 253 | Puckett Substation | 25F14 | 54
279 | 282 | Gomez Substation | 25F61 | 18
280 | 200 | Gomez Substation | 25F05 | 25
281 | 243 | Belding Substation | 12F164 | 19
282 | 288 | 16th Street Substation | 13F14 | 343
283 | 199 | West Substation | 1203 | 910
284 | 289 | Lakepointe Substation | 2524 | 974
285 | 251 | League City Main Substation | 1281 | 760
286 | 212 | Lakepointe Substation | 2516 | 897
287 | 279 | Whitney #2 Substation | 22460 | 527
288 | 74 | Sycamore Substation | 24100 | 27
289 | 270 | Meridian Substation | 680 | 307
290 | 48 | Clifton #2 Substation | 4160 | 499
291 | 274 | Clifton #1 4KV Substation | 405 | 229
292 | 294 | Talco West Substation | 22237 | 31

## Causes
TEXAS-NEW MEXICO POWER COMPANY
INTERRUPTION CAUSES
Provide the percentage of interruptions attributable to each cause.
2017 Reporting Year
Causes of Forced Interruptions |  | Percentage
| WEATHER | 28.2%
| UTILITY-OWNED EQUIPMENT | 25%
| VEGETATION | 23.1%
| ANIMALS AND BIRDS | 13.3%
| UNKNOWN | 5.8%
| PEOPLE | 3.3%
| OTHER | 1.4%
| TOTAL | 100.1%