## MonthlyReportForm
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
TL174 | Copper - Lane 115kV Rebuild & Reconductor | El Paso, El Paso | EPE will replace approximately sixty-four 65' wooden monopole structures with 95' steel monopole structures along a 3.5 mile stretch of Interstate 10 between Lane and Copper Substations. In addition, conductor will be upgraded to 954 MCM ACSR. One new pole will be constructed off of the existing route due to encroaching residential development. | 2017-09-27 |  |  | 3319403 |  |  |  | 50% | 115 | n/a | 5.01 | 556 kcmil ACSR, single conductor, will be replaced with 954 kcmil ACSR | 65'/70' wood single pole structures will be replaced with 95'-110' galvanized steel monopole structures; one corner self-supported structure on new route will be constructed | TxDOT permit | 3.57 | n/a | n/a | 25.101(c)(5)(B) and (E) | Continued with structure replacements and new wire installation. To be continued after summer peak and completion of the rebuild of TL240 Sunset North to Durazno
TL127 | Felipe to Alamo, Alamo to Neely, and Neely to Farmer Structure Replacement | Fabens and Tornillo, El Paso County; Sierra Blanca, Hudspeth County; Van Horn, Culberson County | EPE will replace existing wood monopole structures with steel monopole structures in approximate 94 miles of 69kV transmission line. EPE will utilize the existing centerline. Span lengths may be adjusted according to terrain features. | 2012-06-30 |  |  | 6502992 | 11.0447,753 |  |  | 66% | 69 | n/a | 94 | 4/0 ACSR single conductor | 60 & 65' wood monopoles being replaced with 75' galvanized steel monopole structures | varies | 94 | n/a | n/a | 25.101(c)(5)(B)
TL239 | Reconductor Durazno to Ascarate 115kV transmission line | El Paso, El Paso | Reconductor the line to relieve overloading on the line. EPE will replace wood monopole structures with steel monopole structures to accommodate upgrade of wire to 954 ACSR | 2018-11-01 |  |  | 1922157 |  |  |  |  | 115 | n/a | 3.5 | 556 ACSR conductor will be replaced with 954 ACSR single conductor | Replace wood monopole structures with 85'-105' steel monopoles. | varies and street ROW franchise | 3.5 | 10 | 0.19 | 25.101(c)(5)(B)(ii)
TL240 | Reconductor Sunset North to Durazno 115kV transmission line | El Paso, El Paso | Reconductor the line to relieve overloading on the line. EPE will replace wood monopole structures with steel monopole structures to accommodate upgrade of wire to 954 ACSR | 2018-04-17 |  |  | 1175300 |  |  |  | 20% | 115 | n/a | 4.63 | 556 ACSR conductor will be replaced with 954 ACSR single conductor | Replace wood monopole structures with 85'-105' steel monopoles. | varies and street ROW franchise | 4.63 | 10 | 0.049 | 25.101(c)(5)(B)(ii) | Based on the latest load projections, this line must be in service by this summer's peak, if not, the line may experience overloads of up to 15% under certain single contingencies. Transferring the higher loads onto other transmission lines in the area increases the risk of overloading these lines as well, resulting in potentially disrupting service to customers and a violation of NERC Reliability Standards for EPE's System Operating Limits. All drill pier foundations completed.
TL247 | TxDOT SL375 Interchange Improvements | El Paso, El Paso | Adjust 2-345kV transmission lines, Caliente to Amrad and Caliente to Picante to accommodate the new eastbound and westbound frontage roads to be constructed by TxDOT. EPE will replace several poles on either side of SL375 with taller steel poles for each line. | 2018-10-01 |  |  | 1430235 |  |  |  |  | 345 | n/a | 0.73 each | 954 ACSR corncrake double bundle conductor | Replace wood h-frame structures with 90'-125' steel h-frame or 3-pole structures. Replace corncrake with cardinal 954 ACSR conductor | 300' | 0.73 each | n/a | n/a | 25.101(c)(5)(F) | TxDOT now anticipates awarding the project in the fall, to be worked in parallel with the TL247 TxDOT US 62/180 projects. TxDOT is requesting all utilities to complete their adjustments prior to the contractor starting construction.
TL247 | TxDOT Zaragoza Road Improvement | El Paso, El Paso | Adjust the Diamondhead to Caliente 115kV transmission line to accommodate the expansion of the Zaragoza Road at the Montwood Interchange by TxDOT | 2018-04-12 |  |  | 506493 |  |  |  | 20% | 115kV | n/a | 6.04 | 954 ACSR single bundle | Replace and relocate 1-wood structure and 3-steel self support structures with 1-85' monopole and 3-(100'-105') dead end self support structures | Highway Right of Way | 950 feet | n/a | n/a | 25.101(c)(5)(F)(ii) | Drill pier foundations completed.
TL233 | Nuway Project | El Paso, El Paso | This is a 2-phase project to allow for the construction of a new substation, Nuway, underneath two transmission lines. Phase 1 temporarily reroute the 115kV Montoya to Anthony and permanently reroute the 69kV Rio Grande to Border Steel presently on a double circuit steel monopole. Phase 2 complete the installation of the 115kV transmission line Montoya to Anthony which will cut into the new Nuway Substation. | 2018-03-25 | 2018-03-31 |  | 687000 | 730000 |  |  | 100% | 115kV and 69kV | n/a | 115kV-8.58 and 69kV-13.09 | Both transmissions 795 ACSR single bundle | Temporarily install 2-95' steel structures to reroute the 115kV line to the east side of the substation. Permanently install an 85' steel double circuit monopole on the north and south side of the substation to continue with the 69kV and 115kV lines. Reroute the 69kV line to the west side of the substation on 2-85' single circuit monopoles. Once the substation is near completion, permanently install 2-85' single circuit monopoles for the 115kV line and tapping into Nuway Substation. | 50'-100' | 115kV 8.58 and 69kV 13.09 | n/a | n/a | 25.101(c)(5)(A)(i) | Construction completed March 31, 2018
TL247 | TxDOT US 62/180 (Montana Ave) Expansion | El Paso, El Paso | Adjust three 115kV transmission lines out of Vista Substation to accommodate the road expansion of US 62/180 by TxDOT. Vista to Caliente, Vista to Global Reach and Vista to Scotsdale | 2018-06-01 |  |  | 757233 |  |  |  |  | 115kV | n/a | Vista Caliente - 6.64; Vista Global Reach - 2.96, Vista Scotsdale - 5.18 | Vista Caliente - 795 ACSR, Vista Global Reach - 795 ACSS, Vista Scotsdale - 556 ACSR; all single bundle | Replace and relocated wood structures with steel self support, tangent, and h-frame structures. 2-105' h-frame, 1-105' monopole, 4 sets of 3-pole dead ends (65'-100') | 100' and highway ROW | Vista Caliente - 6.64; Vista Global Reach - 2.96, Vista Scotsdale - 5.18 | n/a | n/a | 25.101(c)(5)(F)(ii) | Pending TxDOT completing environmental document.
TL247 | TxDOT US 62/180 (Montana Ave) Expansion Accommodate Distribution Vista to Caliente | El Paso, El Paso | Install taller transmission structures on the Vista to Caliente 115kV line along Montana Ave to accommodate the distribution adjustments for the TxDOT highway expansion | 2018-05-07 |  |  | 595473 |  |  |  |  | 115kV | n/a | 6.64 | 795 ACSR single bundle | Replace existing monopole structures with monopole tangent steel structures; heights from 85'-115' | Highway right of way | 6.64 | n/a | n/a | 25.101(c)(5)(F)(ii) | Pending TxDOT completing environmental document.
TL247 | TxDOT US 62/180 (Montana Ave) Expansion Accommodate Distribution Vista to Scotsdale | El Paso, El Paso | Install taller transmission structures on the Vista to Scotsdale 115kV line along Montana Ave to accommodate the distribution adjustments for the TxDOT highway expansion | 2018-05-07 |  |  | 300185 |  |  |  |  | 115kV` | n/a | 5.18 | 556 ACSR | Replace existing monopole structures with monopole tangent steel structures; heights vary from 75'-105' | Highway right of way | 5.15 | n/a | n/a | 25.101(c)(5)(F)(ii) | Pending TxDOT completing environmental document.
TL247 | Vista to Caliente 115kV Transmission Line Adjustments | El Paso, El Paso | Due to the TxDOT US 62 (Montana) project, the removal of 2 existing span guy poles north of Montana that support the dead end structure holding the Vista-Caliente (VC) and Vista-Scotsdale (VS) 115 kV transmission lines affect the VC, VS, and Vista-Global Reach(VGR) 115kV line all the way back to Vista Substation. The VC line currently crossing under the VGR line, must be moved to the south side of the substation and repositioned to the east side of the corridor. The VGR will become a double circuit line and repositioned on the east side of the shifted VC line. | 2018-04-23 |  |  | 592758 |  |  |  |  | 115kV | n/a | 1.5 | 795 ACSR single bundle | Install intermediate 95' monopoles | 100' | 6.64 | 30 | 0.06 | 25.101(c)(5)(F)(i)(ii)
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.