## MonthlyReportForm
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
TL174 | Copper - Lane 115kV Rebuild & Reconductor | El Paso, El Paso | EPE will replace approximately sixty-four 65' wooden monopole structures with 95' steel monopole structures along a 3.5 mile stretch of Interstate 10 between Lane and Copper Substations. In addition, conductor will be upgraded to 954 MCM ACSR. One new pole will be constructed off of the existing route due to encroaching residential development. | 2017-09-27 | 2019-01-02 | 2019-01-03 | 3319403 | 5,331, 703 |  |  | 100% | 115 | n/a | 5.01 | 556 kcmil ACSR, single conductor, will be replaced with 954 kcmil ACSR | 65'/70' wood single pole structures will be replaced with 95'-110' galvanized steel monopole structures; one corner self-supported structure on new route will be constructed | TxDOT permit | 3.57 | n/a | n/a | 25.101(c)(5)(B) and (E)
TL127 | Felipe to Alamo, Alamo to Neely, and Neely to Farmer Structure Replacement | Fabens and Tornillo, El Paso County; Sierra Blanca, Hudspeth County; Van Horn, Culberson County | EPE will replace existing wood monopole structures with steel monopole structures in approximate 94 miles of 69kV transmission line. EPE will utilize the existing centerline. Span lengths may be adjusted according to terrain features. | 2012-06-30 | 2018-12-05 |  | 6502992 | 11447753 | 12396628 | 8.289% | 100% | 69 | n/a | 94 | 4/0 ACSR single conductor | 60 & 65' wood monopoles being replaced with 75' galvanized steel monopole structures | varies | 94 | n/a | n/a | 25.101(c)(5)(B)
TL239 | Reconductor Durazno to Ascarate 115kV transmission line | El Paso, El Paso | Reconductor the line to relieve overloading on the line. EPE will replace wood monopole structures with steel monopole structures to accommodate upgrade of wire to 954 ACSR | 2019-03-19 |  |  | 1922157 |  |  |  | 7% | 115 | n/a | 3.5 | 556 ACSR conductor will be replaced with 954 ACSR single conductor | Replace wood monopole structures with 85'-105' steel monopoles. | varies and street ROW franchise | 3.5 | 10 | 0.19 | 25.101(c)(5)(B) | Eleven out of 40 drill pier foundations completed.
TL240 | Reconductor Sunset North to Durazno 115kV transmission line | El Paso, El Paso | Reconductor the line to relieve overloading on the line. EPE will replace wood monopole structures with steel monopole structures to accommodate upgrade of wire to 954 ACSR | 2018-04-17 | 2018-10-04 | 2018-10-04 | 1175300 | 2490046 | 2939398 | 18.05% | 100% | 115 | n/a | 4.63 | 556 ACSR conductor will be replaced with 954 ACSR single conductor | Replace wood monopole structures with 85'-105' steel monopoles. | varies and street ROW franchise | 4.63 | 10 | 0.049 | 25.101(c)(5)(B)
TL247 | TxDOT SL375 Interchange Improvements | El Paso, El Paso | Adjust 2-345kV transmission lines in two separate locations along SL375, Caliente to Amrad and Caliente to Picante, to accommodate the new eastbound and westbound frontage roads to be constructed by TxDOT. EPE will replace several poles on either side of SL375 with taller steel poles for each line. | 2019-06-03 |  |  | 3248413 |  |  |  |  | 345 | n/a | 1.10 each | 954 ACSR corncrake double bundle conductor | Replace wood H-frame structures with 90'-125' steel H-frame or 3-pole structures. | 300 | 1.10 each | n/a | n/a | 25.101(c)(5)(F) | Pending execution of Utility Agreement by TxDOT
TL233 | Nuway Project | El Paso, El Paso | This is a 2-phase project to allow for the construction of a new substation, Nuway, underneath two transmission lines. Phase 1 temporarily reroute the 115kV Montoya to Anthony and permanently reroute the 69kV Rio Grande to Border Steel presently on a double circuit steel monopole. Phase 2 complete the installation of the 115kV transmission line Montoya to Anthony which will cut into the new Nuway Substation. | 2018-03-25 | 2018-03-31 |  | 687000 | 730000 |  |  | 90% | 115 and 69 | n/a | 115kV-8.58 and 69kV-13.09 | Both transmissions 795 ACSR single bundle | Temporarily install 2-95' steel structures to reroute the 115kV line to the east side of the substation. Permanently install an 85' steel double circuit monopole on the north and south side of the substation to continue with the 69kV and 115kV lines. Reroute the 69kV line to the west side of the substation on 2-85' single circuit monopoles. Once the substation is near completion, permanently install 2-85' single circuit monopoles for the 115kV line and tapping into Nuway Substation. | 50-100 | 115kV 8.58 and 69kV 13.09 | n/a | n/a | 25.101(c)(5)(A)
TL247 | TxDOT US 62/180 (Montana Ave) Expansion | El Paso, El Paso | Adjust three 115kV transmission lines out of Vista Substation to accommodate the road expansion of US 62/180 by TxDOT. Vista to Caliente, Vista to Global Reach and Vista to Scotsdale | 2019-03-04 |  |  | 757233 |  |  |  | 90% | 115 | n/a | Vista Caliente - 6.64; Vista Global Reach - 2.96, Vista Scotsdale - 5.18 | Vista Caliente - 795 ACSR, Vista Global Reach - 795 ACSS, Vista Scotsdale - 556 ACSR; all single bundle | Replace and relocate wood structures with steel self support, tangent, and h-frame structures. 2-105' h-frame, 1-105' monopole, 4 sets of 3-pole dead ends (65'-100') | 100 and highway ROW | Vista Caliente - 6.64; Vista Global Reach - 2.96, Vista Scotsdale - 5.18 | n/a | n/a | 25.101(c)(5)(F) | All structures and fiber installed. Pending removal of guy wires across Montana and existing wood poles.
TL247 | TxDOT US 62/180 (Montana Ave) Expansion Accommodate Distribution Vista to Caliente | El Paso, El Paso | Install taller transmission structures on the Vista to Caliente 115kV line along Montana Ave to accommodate the distribution adjustments for the TxDOT highway expansion | 2019-03-04 |  |  | 595473 |  |  |  | 80% | 115 | n/a | 6.64 | 795 ACSR single bundle | Replace existing monopole structures with monopole tangent steel structures; heights from 85'-115' | Highway right of way | 6.64 | n/a | n/a | 25.101(c)(5)(F) | Twelve out of 24 structures remain to be installed. Will be completed in April.
TL247 | TxDOT US 62/180 (Montana Ave) Expansion Accommodate Distribution Vista to Scotsdale | El Paso, El Paso | Install taller transmission structures on the Vista to Scotsdale 115kV line along Montana Ave to accommodate the distribution adjustments for the TxDOT highway expansion | 2019-04-01 |  |  | 300185 |  |  |  | 85% | 115 | n/a | 5.18 | 556 ACSR | Replace existing monopole structures with monopole tangent steel structures; heights vary from 75'-105' | Highway right of way | 5.15 | n/a | n/a | 25.101(c)(5)(F) | Four of the 9 structures have been installed. The FAA has identified 5 structures affecting the airspace or air navigation. Other alternatives are being reviewed to accommodate the distribution facilities.
TL247 | Vista to Caliente 115kV Transmission Line Adjustments | El Paso, El Paso | Due to the TxDOT US 62 (Montana) project, the removal of 2 existing span guy poles north of Montana that support the dead end structure holding the Vista-Caliente (VC) and Vista-Scotsdale (VS) 115 kV transmission lines affect the VC, VS, and Vista-Global Reach(VGR) 115kV line all the way back to Vista Substation. The VC line currently crossing under the VGR line, must be moved to the south side of the substation and repositioned to the east side of the corridor. The VGR will become a double circuit line and repositioned on the east side of the shifted VC line. | 2019-03-04 |  |  | 592758 |  |  |  | 90% | 115 | n/a | 1.5 | 795 ACSR single bundle | Install intermediate 95' monopoles | 100 | 6.64 | 30 | 0.06 | 25.101(c)(5)(F) | All tangent structures and conductor have been installed. A temporary re-route outside the substation was done to meet the TxDOT April relocation schedule. The permanent alignment will be completed during non-peak season.
TL101 | Rio Grande to Sunset 115kV transmission line rebuild across the mountain located on the University of Texas at El Paso property. | El Paso, El Paso | Rebuild two Rio Grande to Sunset 69kV transmission lines, 5500 and 5600, across the mountain located on University of Texas at El Paso property to replace existing wooden poles with double circuit steel monopoles. One line will carry a 69kV line and a distribution line. The second line will carry a 69kV line and an open position for a future line. | 2019-03-04 |  |  | 3500000 |  |  |  | 30% | 69 | n/a | 0.922 each | Existing 336 and 556 ACSR single bundle conductor will be replaced with 954 ACSR single bundle | Install 25 steel monopoles ranging from 75'-105', all on drill pier foundations | 100 | 0.922 each | n/a | n/a | 25.101(c)(5)(B) | Eleven out of 26 drill pier foundations have been constructed.
TL259 | Sunset to Santa Fe 69kV line upgrade | El Paso, El Paso | Re-conductor the 69kV transmission line and replace all the wood structures to increase the capacity of the line. A total of 9 wood structures will be replaced with 75'-85' steel structures. | 2019-01-25 | 2019-02-28 | 2019-03-19 | 887398 |  |  |  | 100% | 69 | n/a | 1.34 | Replace 336 ACSR single bundle conductor with 954 ACSR single bundle conductor | Replace 9-65' wood poles with 3-75'-85' steel deadend structures on drill pier foundations and 6 75'-80' steel tangent structures | Along street right of way | 1.34 | n/a | n/a | 25.101(c)(5)(B) | Line energized March 19, 2019
TL236 | Rio Grande to Sunset North 115kV transmission line tap into Executive Substation | El Paso, El Paso | Replace structures on the 15800 -115kV transmission line to tap into the new Executive Substation. Will create the Sunset North to Executive and Executive to Rio Grande 115kV lines | 2019-05-15 |  |  | 474590 |  |  |  |  | 115 | n/a | 0.1 | 556 ACSR double bundle; wire will not be replaced | Replace H-frame wood structures with 4-100' steel monopole tangents and install 2-85' deadend steel structures on drill pier foundations | 50 | 0.1 | n/a | n/a | 25.101(c)(5)(A)
TL247 | TxDOT SL375 Interchange Improvements | El Paso, El Paso | Adjust 2-115kV transmission lines, Global Reach to Picante and Liberty to Bliss Industrial to accommodate the new eastbound and westbound frontage roads to be constructed by TxDOT. EPE will replace several poles on either side of SL375 with taller steel poles for each line. | 2019-06-03 |  |  | 1350545 |  |  |  |  | 115 | n/a | 0.34 each | 954 ASCR single bundle | Each line install 2-100' tangent steel H-frame structures and 2-70' 3 pole steel deadend structures. | 100 | 0.34 each | n/a | n/a | 25.101(c)(5)(F)
Note on H1: Author: Please enter only a single integer, if possible.
Note on I1: Author: Please enter only a single integer, if possible.
Note on M1: Author: If applicable.
Note on N1: Author: If applicable.