## SWEPCO TEXAS MPR
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
41617969 | Valliant to NW Texarkana: 345-kV Texas Portion | Bowie | Construct new 345-kV double circuit capable transmission line from the Red River Crossing to the SWEPCO NW Texarakana Substation and necessary termination facilities at NW Texarkana | 2014-10-27 | 2016-12-12 | 2016-12-01 | 69641000 | 71815773 |  |  | 99 |  | 345 | 44.22 | 954 ACSR | Steel, Single Pole |  |  | 150 | 44.22 | 40685 | Approved 08/30/13 Project WO number changed for TX portion of project.
42529111 | Knox Lee 138-kV: Relocation | Panola | Relocate a 2.30 mile portion of the Knox Lee-Rock Hill Heights 138-kV transmission line for Luminant Mining | 2017-02-05 | 2017-05-30 | 2017-04-28 |  | 2698544 |  |  | 99 | 138 | 138 | 2.3 | 795 ACSR | Steel, Single Pole | Centerline | 2.3 | 100 | 2.2 | 16 TAC 25.101 (c)(5)(D) | Landowners Noticed Easements Obtained Project is Reimbursible
42625878 | Naples to Buford Survey: 69-kV Line Rebuild | Morris | Rebuild and Reconductor Naples to Buford Survey 69-kV T-Line to 138-kV Standards but will continue to be operated at 69 kV. | 2019-05-01 | 2019-09-27 |  |  | 7643591 |  |  | 5 | 69 | 69 | 6.6 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole | Varies | 6.6 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42678611 | Morton Substation: T-Line Assets | Van Zandt | Build 1500' of double-circuit 138-kV line for cut-in to SWEPCO Morton Station | 2018-05-14 | 2018-10-01 | 2018-09-21 |  | 1301441 |  |  | 99 |  | 138 | 0.3 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole |  |  | 100 | 0.3 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
42678612 | Morton Substation: T-Station Assets | Van Zandt | Install two 138-kV rated MOABS and one 138-kV Rated bus tie switch. | 2018-04-15 | 2018-10-01 | 2018-09-21 |  | 1487960 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42672427 | Hedley-Memphis 69-kV Line Rebuild | Donley / Hall | Rebuild and Reconductor 12.58 Miles of 69-kV T-Line to 138-kV Standards Continue to Operate at 69 kV | 2017-08-05 | 2018-05-14 | 2018-05-15 |  | 13387787 |  |  | 99 | 69 | 69 | 12.58 | T2 477 KCM ACSR | Steel, Single Pole | Various | 12.58 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42672009 | Whitney Station: Replace Breakers and Transformers | Gregg | Replacement of six (6) transmission breakers, two autotransformers, bus and controls | 2017-09-08 | 2019-06-17 |  |  | 10236675 |  |  | 85 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42621746 | Clarendon-Hedley 69-kV Line Rebuild | Donley | Rebuild and Reconductor 14.49 Miles of 69-kV T-Line to 138-kV Standards Continue to Operate at 69 kV | 2017-09-08 | 2018-05-14 |  |  | 14463583 |  |  | 25 | 69 | 69 | 14.49 | T2 477 KCM ACSR | Steel, Single Pole | Various | 14.49 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42622815 | Jenkins T - Hughes Springs Rebuild | Hughes Springs/Cass,Morris | Rebuild and Reconductor 4.76 Miles of 69-kV T-Line from Jenkins "T" to Hughes Springs Substation to 138-kV Standards. Continue to Operate at 69 kV. | 2017-11-13 | 2018-03-30 | 2018-03-23 |  | 8786000 |  |  | 99 | 69 | 69 | 4.76 | 1272 ACSR | Steel, Single Pole | Various | 4.76 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42581190 | Evenside - NW Henderson 69-kV Rebuild | Henderson/Rusk | Rebuild, Reconductor, and Partially Relocate 6.38 Miles of 69-kV T-Line from Evenside - NW Henderson to 138-kV Standards. Continue to Operate at 69 kV. | 2017-12-04 | 2018-06-01 | 2018-05-11 |  | 9003800 |  |  | 99 | 69 | 69 | 6.38 | 1272 ACSR 54/19 (Pheasant) | Steel, Single Pole | Various | 6.38 | 100 | 0.08 | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.101 (c)(5)(E) | Utilizing existing easements Consent acquired where necessary Landowners noticed
42579898 | Evenside Station: Remote End Work | Henderson/Rusk | Evenside Station - Expand station to accommodate DICM; replace CB-1Z30 and disconnect switches; add surge arresters and replace existing bus PT's with CCVT's; replace RTU. | 2017-10-30 | 2018-06-01 | 2018-05-11 |  | 2215100 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42579900 | NW Henderson Station: Remote End Work | Henderson/Rusk | NW Henderson Station - Upgrade 69-kV Evenside terminal for new relaying | 2018-01-09 | 2018-06-01 | 2018-05-11 |  | 589200 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42751512 | Public Relocation: Hawkins-Mineola | Wood | Raise 69-kV transmission line to meet current clearance standards, requires removal of 5 wood h-frame structures & installation of 5 new steel poles. | 2018-03-05 | 2018-06-01 | 2018-05-17 |  | 823653 |  |  | 99 | 69 |  |  |  | Steel, Single Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(D) | Landowners Noticed
42621757 | Memphis-Estelline 69-kV Line Rebuild | Memphis/Hall, Estelline/Hall | Rebuild, Reconductor, and Partially Relocate 16.15 Miles of 69-kV T-Line to 138-kV Standards Continue to Operate at 69 kV | 2017-12-07 | 2019-02-01 | 2018-12-03 |  | 14745480 |  |  | 99 | 69 |  | 16.15 | T2 477 KCM ACSR | Steel, Single Pole | Various | 16.15 | 100 | 0.18 | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.101 (c)(5)(E) | Landowners Noticed Consent, New Easement & Supplements were acquired as necessary
42672428 | Estelline-W. Chidress 69-kV Rebuild | Estelline/Hall, Childress/Childress | Rebuild and Reconductor 17.23 Miles of 69-kV T-Line to 138-kV Standards Continue to Operate at 69 kV | 2017-12-07 | 2019-12-23 | 2019-03-21 |  | 18743790 |  |  | 90 | 69 |  | 17.23 | T2 477 KCM ACSR | Steel, Single Pole | Various | 17.23 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42672429 | Childress Amoco Tap 69-kV Rebuild | Childress | Rebuild and Reconductor 1.56 Miles of 69-kV to 138-kV Standards Continue to operate at 69 kV | 2017-12-07 | 2019-11-07 |  |  | 2019300 |  |  | 25 | 69 |  | 1.56 | T2 477 KCM ACSR | Steel, Single Pole | Various | 1.56 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42872935 | Bann to Redlick 69-kV Line Rebuild | Bowie | Rebuild and Reconductor the Bann to Redlick 69-kV T-Line (existing double circuit with Bann to New Boston 138-kV transmission line) to 138-kV Standards but will continue to be operated at 69 kV. | 2019-09-03 | 2019-12-13 |  |  | 2815625 |  |  | 0 | 69 |  | 1.5 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole | Varies | 1.5 | 100 | 1.5 | 16 TAC 25.101 (c)(5)(B) | Landowner Consent Obtained
42633475 | Bann to North New Boston 138-kV Line Rebuild | Bowie | Rebuild and Reconductor 1.5 miles of the Bann to North New Boston 138-kV T-Line (existing double circuit with Bann to Redlick 69-kV transmission line). | 2019-09-03 | 2019-12-12 |  |  | 2695041 |  |  | 0 | 138 |  | 1.5 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole | Varies | 1.5 | 100 | 1.5 | 16 TAC 25.101 (c)(5)(B) | Landowner Consent Obtained
42644732 | Adora Tap - West Mt. Pleasant | Mt. Pleasant/Titus | Rebuild and Reconductor 0.86 Miles of 69-kV T-Line to 138-kV Standards Continue to Operate at 69 kV | 2018-03-19 | 2019-05-01 |  |  | 1360000 |  |  | 0 | 69 |  | 0.86 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole | Various | 0.86 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42622941a | Pilgrims Pride-Winfield Rehab (Pilgrims Pride- Adora Tap) | Titus | Rebuild and Reconductor 1.61 Miles of 69-kV T-Line to 138-kV Standards Continue to Operate at 69 kV | 2018-01-15 | 2019-03-16 |  |  | 1416964 |  |  | 5 | 69 |  | 1.61 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole | Various | 1.61 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42678576 | Wilkes 345-kV: Replace breakers and auto transformer | Marion | Replace 138-kV Breakers and Bus and one 138/345-kV auto transformer | 2018-04-01 | 2021-05-14 |  |  | 13776933 |  |  | 35 | 345 / 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42684227 | IPC 138-kV Substation | Cass | Expand Station Property, add a 138-kV CB in parallel with the current CB 7340, new control panels for the new CB, air break switches, bus addition for parallel connection (to existing 138-kV CB and equipment) and new 138-kV metering . | 2018-04-30 | 2018-12-05 | 2018-12-07 |  | 1169064 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42624837 | Cass Tap Station | Cass | Build new 138-kV Box Bay Station with 2-3000A breakers, 1-3000A Tap Switch and 138-kV Combo Metering Units on newly acquired property. | 2018-06-11 | 2019-03-22 | 2019-03-19 |  | 4579869 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42624849 | Munz City Station | Cass | Expand station property, Install two 138 kV, 3000A Breakers, 1-3000A Tap Switch, re-work bus, and upgrade metering, and install a control house. | 2018-06-11 | 2019-04-12 | 2019-04-11 |  | 4091536 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42773747 | IPC 138-kV Substation | Cass | IPC 138 kV: Install two 14.4 MVAR, 138 kV, cap banks at IPC 138 kV sub and new control house. | 2018-07-09 | 2018-12-05 | 2018-12-13 |  | 1976871 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42707036 | Vernon Station (SPP): Breaker Replacement | Vernon/Wilbarger | Replace 69-kV Circuit Breaker 122 | 2018-07-02 | 2019-05-01 |  |  | 797621 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within existing property
42626676 | Cass Tap T-line | Cass | Install new three 3-pole anchor bolted galvanized Deadend Structures to loop line into new Cass Tap Box Bay station. | 2018-09-10 | 2019-03-22 | 2019-03-19 |  | 1114632 |  |  | 99 | 138 |  | 0.13 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel 3-Pole | 100 | 0.13 |  |  | 16 TAC 25.101 (c)(5)(A) | Within existing property
42624844 | Munz City T-line | Cass | Reterminated T-line into Munz City Station, two 3-pole anchor bolted galvanized Deadend Structures. Project will require temporary shoo fly to be removed after new termination is complete. | 2018-08-20 | 2019-04-12 | 2019-04-11 |  | 1033315 |  |  | 99 | 138 |  | 0.09 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel 3-Pole | 100 | 0.09 |  |  | 16 TAC 25.101 (c)(5)(A) | Within existing property Temporary ROW acquired for shoo fly
42625874 | Buford Survey Tap to Cookville Tap 69-kV Line Rebuild | Morris,Titus | Rebuild and Reconductor Buford Survey Tap to Cookville Tap 69-kV T-Line to 138-kV standards but will continue to be operated at 69 kV. | 2019-01-02 | 2019-05-31 |  |  | 6710455 |  |  | 98 | 69 |  | 6.28 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel Mono Pole | Varies | 6.28 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42625876 | Cookville Tap to Cookville 69-kV Line Rebuild | Titus | Rebuild and Reconductor Cookville Tap to Cookville 69-kV T-Line to 138-kV standards but will continue to be operated at 69 kV. | 2019-01-02 | 2019-05-31 |  |  | 2695312 |  |  | 98 | 69 |  | 1.8 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel Mono Pole | Varies | 1.8 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42677363 | Jenkins REC T- Lone Star Tap 69-kV Line Rebuild | Lone Star/Morris | Rebuild and Reconductor Jenkins REC T to Lone Star Tap 69-kV transmission line to 138-kV standards but will continue to be operated at 69 kV. | 2019-01-15 | 2019-08-01 |  |  | 2943000 |  |  | 10 | 69 |  | 6.96 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel Mono Pole | Various | 6.96 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42763999 | Pirkey- Tenaska Rusk County 345-kV Line Relocate | Harrison | Relocate a 1.50 mile section of the existing SWEPCO Pirkey-Tenaska Rusk County 345-kV transmission line to facilitate advancement of mining at Sabine Mine. Relocation occurs between Pirkey Substation and Lebrock Substation. | 2019-01-07 | 2019-06-14 |  |  | 9048389 |  |  | 15 | 345 |  | 2.7 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, single pole | 150 | 1.5 | 150 | 2.7 | 16 TAC 25.101 (c)(5)(E) | Landowner Consent Obtained
42626683 | North New Boston 138-kV Substation | New Boston/Bowie | Remote End work at North New Boston 138-kV Substation to match relays at Muntz City Substation. Replace existing CCVTs with carrier accessories, and line trap and tuner (on phase A) for the 138-kV Munz City line terminal. Install surge arresters on the Munz City line terminals. | 2019-01-02 | 2019-02-22 |  |  | 812872 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42626678 | West Atlanta 138-kV Substation | Cass | Remote End work at West Atlanta 138-kV Substation to match relays at Cass Tap Switch Station. The upgrade includes one- three phase CCVT/SA combo support structure, three CCVTs, one CCVT junction box, three surge arresters, and upgraded relaying for line protection and breaker control. | 2019-01-02 | 2019-03-22 | 2019-03-19 |  | 773818 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42872933 | Richmond Rd. - NW Texarkana SWAEC Tap 69-kV Line Rebuild | Texarkana/Bowie | Rebuild and Reconductor 1.10 miles of the NW Texarkana SWAEC Tap to Richmond Road 69-kV T-Line to 138-kV standards but will continue to be operated at 69 kV. | 2020-12-01 | 2021-05-31 |  |  | 2046020 |  |  | 0 | 69 |  | 1.1 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole | Varies | 1.1 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42896414 | Hill Lake | Panola | Hill Lake 138-kV Extension: Terminate the Logansport - Rock Hill - Tenaha 138-kV transmission line with double-circuit structures into new Hill Lake Station | 2019-03-26 | 2019-08-31 |  |  | 1680114 |  |  | 0 |  | 138 | 0.5 | 1272 ACSR 54/19 (Pheasant) | Steel, Single Pole |  |  | 100 | 0.25 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
42782325 | Hallsville South POD 138-kV Box Bay | Harrison | Install 138-kV Station Box Bay (Low Bay), with 2-3000A, Auto-sectionalized switches, 1- Scada controlled tap switch, and 1-combo unit maintenance switch. Install fence, grid, and rock and tie grid with URECC. | 2019-04-22 | 2019-09-27 |  |  | 3053090 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Written consent acquired to begin construction activites
42896004 | Hill Lake | Panola | Hill Lake 138-kV Station: Construct a new 138-kV High Side In/Out Switching Station with metering to serve new gas pumping station | 2019-05-20 | 2019-08-31 |  |  | 2177850 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(A)(3) | Landowner Consent Acquired
42872899 | DeKalb to Buford Survey (Corp Property) 69-kV Line Rebuild | Morris | Rebuild and Reconductor DeKalb to Buford Survey (Corp Property) 69-kV T-Line to 138-kV Standards but will continue to be operated at 69-kV. | 2019-06-03 | 2019-11-08 |  |  | 7425055 |  |  | 0 | 69 |  | 2 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole | Varies | 2 |  |  | 16 TAC 25.101 (c)(5)(B) | This Project is a 2 mile section on ACE Property of the Dekalb-Buford Survey 69-kV Rebuild previously reported on Project 42625879. Permitting by ACE took longer than expected so this 2 mile section was broken out of the Project. Utilizing existing easements Landowners previoulsy noticed
42879422 | Brandy Branch 138-kV Box Bay | Harrison | Terminate the Knox Lee - Pirkey 138-kV transmission line into the Brandy Branch 138-kV POD Box Bay. This will also include the temporary hard tap for the customer. | 2019-07-15 | 2020-03-26 |  |  | 386742 |  |  | 0 | 138 |  | 0.19 | Bundled CURLEW 1033.5 ACSR/SD TYPE 5 42/7 | Steel, Single Pole | Varies | 0.19 |  |  | 16 TAC 25.101 (c)(5)(A) | Transmission line within Company-Owned propertiy. No additional easement required.
42938267 | IPC 138-kV Expansion: T-Station Asset | Cass | Install one bi-lvl bus support and bus work to get to the new switch in front of the circuit switcher. | 2019-08-01 | 2020-03-30 |  |  | 335446 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(A)(3) | Within station property
42872872 | Mt. Pleasant to Cookville Tap 69-kV Line Rebuild | Mt. Pleasant/Titus | Rebuild and Reconductor Mt. Pleasant to Cookville Tap 69-kV T-Line to 138-kV Standards but will continue to be operated at 69 kV. | 2019-07-04 | 2019-04-09 |  |  | 8771835 |  |  | 0 | 69 |  | 8.16 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole | Variues | 8.16 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.