## MonthlyReportForm
Utility Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
16T65211 CL/MP | Watermill - Trinidad 345 kV Line: Tricorner Line Work | City of Seagoville, Dallas County | In support of the Tricorner Substation rebuild, two double-circuit tower structures must be raised on the Watermill – Trinidad 345 kV line. Once the Tricorner Substation rebuild is complete, this line will be reterminated in the substation. | 2018-09-17 | 2018-11-18 | 2018-11-19 | 438393.52 | 438460.01 |  |  | 100 | 345 | na | 0.25 | 2-959.6 kcmil ACSS/TW | Steel Towers | 150 | 0.25 | na | na | 25.101(c)(5)(B)
16T65210 CL/MP | Elkton - Tricorner 345 kV Line: Tricorner Line Work | City of Seagoville, Dallas County | In support of the Tricorner Substation rebuild, one double-circuit tower structure must be raised on the Elkton - Tricorner 345 kV line. Once the Tricorner Substation rebuild is complete, this line will be reterminated in the substation. | 2018-09-17 | 2018-12-12 | 2018-12-12 | 329451.26 | 329516.67 |  |  | 100 | 345 | na | 0.25 | 2-795 ACSR | Steel Towers | 150 | 0.25 | na | na | 25.101(c)(5)(B)
16T65209 CL/MP | Seagoville - Tricorner 345 kV Line: Tricorner Line Work | City of Seagoville, Dallas County | In support of the Tricorner Substation rebuild, one steel tower and one two-pole steel deadend must be raised on the Seagoville - Tricorner 345 kV line. Once the Tricorner Substation rebuild is complete, this line will be reterminated in the substation. | 2018-09-17 | 2018-10-31 | 2018-10-31 | 927712.66 | 979625.72 |  |  | 100 | 345 | na | 0.35 | 2-795 ACSR & 2-959.6 ACSS/TW | Steel Towers and Steel Poles | 250 | 0.35 | na | na | 25.101(c)(5)(B)
17T63124 JM/JO | Wink to Culberson 138 kV: West of Pecos Point of Interconnection | City of Orla | Establish a point of interconnection to the West of the Pecos Solar LLC generating facility from the Riverton Switching Station on the Wink - Riverton - Culberson 138 kV transmission line. | 2019-07-25 | 2019-09-30 | 2019-09-30 | 650000 | 650000 |  |  | 100 | na | 138 | 0.9 | 795 ACSR | Steel Poles | na | na | 70 | 0.71 | 25.101(c)(5)(A)
17T62095 BC | Bryan Ave - Forest Hill Sw. 69 kV Line: CMPC System Hardening | Fort Worth, Tarrant County | Relocate and replace 3 structures across I-35W for CMPC System Hardening | 2018-04-30 | 2018-10-15 | 2018-10-15 | 442203.84 | 338447 |  |  | 100 | 69 | na | 0.05 | 556.5 kcmil ACSR | Steel Poles | Varies | 0.05 | na | na | 25.101(c)(5)(B)
17T62098 BC | Handley - Everman 138 kV Line: CMPC System Hardening | Fort Worth, Tarrant County | Relocate and replace 3 structures across I-30 for CMPC System Hardening | 2018-05-06 | 2018-11-29 | 2018-11-29 | 493522 | 171599 |  |  | 100 | 138 | na | 0.1 | 336.4 kcmil ACSR | Concrete Poles | Varies | 0.1 | na | na | 25.101(c)(5)(B)
18T62048 BC | Forest Hill Sw. - Bourland 138 kV Line: Marrs Sw. Line Work | Fort Worth, Tarrant County | Relocate structures to cut-in Marrs Switching Station | 2018-08-15 | 2018-10-01 | 2018-10-01 | 321673.91 | 365119 |  |  | 100 | 138 | na | 0.16 | 959.6 ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(A)
18T62049 BC | Marrs Sw. - Forest Hill Sw. 138 kV Line: Marrs Sw. Line Work | Fort Worth, Tarrant County | Relocate structures to cut-in Marrs Switching Station | 2018-08-15 | 2018-10-20 | 2018-10-20 | 239482 | 210447 |  |  | 100 | 138 | na | 0.15 | 959.6 ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(A)
18T62050 BC | Forest Hill Sw. - Rolling Hills 138 kV Line: Marrs Sw. Line Work | Fort Worth, Tarrant County | Relocate structures to cut-in Marrs Switching Station | 2018-08-15 | 2018-10-13 | 2018-10-13 | 348803 | 519242 |  |  | 100 | 138 | na | 0.16 | 959.6 ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(A)
18T62051 18T62052 BC | Forest Hill Sw. - Everman NO. 3 & NO. 4 138 kV Line: Marrs Sw. Line Work | Fort Worth, Tarrant County | Relocate structures to cut-in Marrs Switching Station | 2018-08-15 | 2018-10-20 | 2018-10-20 | 483837 | 775575 |  |  | 100 | 138 | na | 0.14 | 959.6 ACSS/TW | Steel poles | na | na | na | na | 25.101(c)(5)(A)
16T65092 MK/MP | Cedar Hill - Liggett 138 kV Line: Upgrade Venus Tap - Liggett Section | City of Grand Prairie, Dallas County | Upgrade the 5.5 mile section of Cedar Hill Switch - Liggett Switch 138 kV Line of double-circuit steel lattice towers and single-circuit wood h-frame structures. | 2019-01-14 | 2019-12-31 |  | 10342023 | 8063582 |  |  | 90 | 138 | na | 7.2 | 1926.9 ACSS/TW | Steel Poles | 100 | 7.2 | na | na | 25.101(c)(5)(B)
16T65168 MK/MP | Cedar Hill - Liggett 138 kV Line: Shady Grove 138 kV Line Loop | City of Grand Prairie, Dallas County | Rebuild the Shady Grove 138 kV Line Loop as part of upgrading the Cedar Hill Switch Station - Liggett 138 kV Line. The existing .5 mile line loop structures will be upgraded to steel poles. | 2018-08-03 | 2018-11-30 | 2018-11-30 | 1079973 | 1621146 |  |  | 100 | 138 | na | 0.5 | 1926.9 ACSS/TW | Steel Poles | 60 | 0.5 | na | na | 25.101(c)(5)(B)
16T62098 PO/EA | Wedgewood Sw. Sta. – Forest Hill 138 kV Line Upgrade | Fort Worth/Tarrant | Rebuild and upgrade the Wedgewood Sw. Sta. – Forest Hill Sw. Sta. 138 kV Transmission Line. This upgrade will be 7 miles of new double-circuit 959.6 kcmil ACSS/TW/HS operated at a maximum temperature of 180°C and 1649 amps. | 2018-04-02 | 2018-11-30 | 11/31/2018 | 1079973 | 6083475 |  |  | 100 | 138 | 138 | 14 | 959.6 kcmil ACSS/TW | Steel and Concrete Poles | Varies | 7 | na | na | 25.101(c)(5)(B)
16T62147 PO/EA | Everman Sw. Sta. – Forest Hill 138 kV Line Reconductor | Fort Worth/Tarrant | Reconductor the north circuit only on the Everman Sw. Sta. – Forest Hill Sw. Sta. 138 kV Transmission Line. The south circuit will be tied into the relocated Forest Hill Sw. Sta. and relocated termination at Everman Sw. Sta., which will require new structures. | 2018-02-15 | 2018-10-06 | 2018-10-06 | 1785666 | 1785666 |  |  | 100 | 138 | 138 | 2 | 959.6 kcmil ACSS/TW | Steel Poles | Varies | 2 | na | na | 25.101(c)(5)(B)
16T62114 JS/BC | Crowley - Bourland (Cresson) 69 kV Line Rebuild | City of Crowley, Tarrant County | Rebuild the 9.54 mile Crowley - Cresson section of the Forest Hill - Cresson 69 kV line as the Crowley - Bourland 138 kV line. | 2018-06-01 | 2018-10-01 | 2018-10-01 | 8069282 | 8602917 |  |  | 100 | 69 | 138 | 9.5 | 959.6 kcmil ACSS/TW | Steel Poles | Varies | 9.54 | Varies | na | 25.101(c)(5)(B)
17T65141 CB/DN | Watermill Sw Sta - Simpson Stuart 138 kV Ln - Upgrade 8.4 Miles | City of Dallas, Dallas County | Upgrade the Watermill Switch Station - Simpson Stuart 138 kV Line section of the Cedar Hill - Watermill 138 kV Line. | 2018-10-01 | 2018-12-07 | 2018-12-08 | 3017807 | 3861938 |  |  | 100 | 138 | 138 | 8.4 | 959.6 kcmil ACSS/TW | Steel Poles and Existing Lattice Towers | Varies | 8.4 | Varies | na | 25.101(c)(5)(B)
15T62065 SEI/MK | Graham - Archer City 69 kV | City of Graham, Young County | Replace existing wood pole H-frames with Two (2) new single-circuit, concrete H-frame tangent structures (Str. 36/7 & 36/8). | 2020-03-09 | 2020-03-21 |  | 266075.7 | 253850 |  |  | 0 | 69 | na | 0.38826 | 4/0 ACSS | Concrete H-frames | 100 | 0.38826 | na | na | 25.101(c)(5)(B)
15T65114 LT/AB | Cedar Hill - South Hampton OPGW | City of Dallas, Dallas County | This project is to install OPGW on the Cedar Hill - South Hampton 138 kV Line. The existing line is six and six tenth (6.6) miles of single and double-circuit lattice towers and steel monopoles with 3/8" EHS Shield Wire. The final build will replace the existing 3/8" & 7/16" EHS Shield Wire with 0.546" OPGW 48 count fiber. No changes to the existing conductor and structures is required. | 2017-03-06 | 2018-11-27 | 2018-11-27 | 924349 | 924349 |  |  | 100 | 138 | 138 | 6.6 | OPGW | Steel towers and steel poles | Varies | 6.6 | na | na | 25.101(c)(5)(B) | Replacing shield wire with optical ground wire (OPGW)
17T64042 RJ 0PT38881 | Trinidad-Kaufman Crossarm Replacement | City of Kaufman, Kaufman and Henderson Counties | Replace approximately 352 wood cross arms with steel cross arms on the Trinidad - Kaufman 138 kV line. The existing line is 37 miles of primarily single-circuit wood H-frame structures with wood cross-arms. Any degraded wood poles may be replaced. Cross bracing will be installed as necessary to meet current NESC strength requirements. | 01/14/2019 | 2019-11-01 |  | 2,151,752 | 2141137 |  |  | 50 | 138 | na | 37 | 1033.5 ACSR | Wood H-Frames | 70 | 37 | na | na | 25.101(c)(5)(B)
16T64077 IA | Elm Mott - Waco/Waco East 138 kV Line | Waco/McLennan County | Upgrade the existing 11.5-mile Elm Mott – Waco Northeast Tap 138 kV line section. | 2017-11-06 | 2018-11-15 | 2018-11-15 | 6000000 | 7515225 |  |  | 100 | 138 | 138 | 11.5 | 1233.6 kcmil ACSS/TW | Steel Monopoles | Varies | 11.5 | na | na | 25.101(c)(5)(B)
16T65110 JC/RS | Amelia St. Sw. Sta. - E Levee Sta. 138 kV Line | Dallas County | Rebuild the Amelia St. Sw. Sta. - E. Levee Sta. 138 kV Line. The existing line is three miles of single/double-circuit steel monopoles. | 2018-03-01 | 2018-12-31 | 2018-12-31 | 6349699 | 6349699 |  |  | 100 | 138 | 138 | 3 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 3 | na | na | 25.101(c)(5)(B)
17T64073 BC/DN | Hutto Sw. - Taylor 138 kV Line - Upgrade 10.1 mi | Williamson County | Upgrade the Hutto Sw. Sta - Taylor 138 kV Line. The existing line is a single-circuit on double-circuit steel and concrete monopoles. | 2018-08-10 | 2018-12-31 | 2018-12-31 | 6373852 | 5277550 |  |  | 100 | 138 | 138 | 10.1 | 1926.9 kcmil ACSS/TW | Steel & Concrete Poles | 70 | 10.1 | na | na | 25.101(c)(5)(B)
17T61030 0PT37516 SEI/MK | TxDOT US 175 Relocation, Athens-Jacksonville 69 kV | City of Jacksonville, Cherokee County | Relocate a portion of the Athens - Jacksonville 69 kV Transmission Line. Removal and installation of four (4) new single-circuit street structures at the request of TxDOT | 2018-11-26 | 2018-12-02 | 2018-12-02 | 400372.92 | 356183 |  |  | 100 | 69 | na | 0.40133 | 4/0 ACSR | Concrete Poles | centerline | 0.40133 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
17T64027 JM/DN | Groesbeck - Mexia Phase II 138 kV Line: Rebuild from Groesbeck Main to Mexia | City of Groesbeck and Mexia & Limestone County and Falls County | Rebuild and upgrade approximately 12 miles of the 138 kV transmission line from Groesbeck Main to Mexia. | 2018-03-26 | 2018-12-31 | 2018-12-31 | 9407697 | 10200000 |  |  | 100 | 138 | na | 12 | 959.6 kcmil ACSS/TW | Steel Poles | 50 | 12 | na | na | 25.101(c)(5)(B)
17T65164 SM | Norwood - Denton Drive 138 kV: Install OPGW | Dallas/Dallas | Replace 3/8" shield wire with OPGW on the Norwood - Denton Drive138 kV Transmission Line. | 2019-01-14 | 2020-03-15 |  | 318269.74 | 318270 |  |  | 15 | 138 | 138 | 3.9 | OPGW | Steel Poles | 100 | 3.9 | na | na | 25.101(c)(5)(B)
17T63126 JD/EA | Yucca Drive Sw. Sta. - AEP Barilla Junction 138 kV Line: Rebuild STR 8/5 - AEP Barilla Junction 18/1 | Monahans / Ward County | Upgrade the Oncor-owned portion of the Yucca Drive Sw. Sta. – AEP Barilla Junction 138 kV Line with a conductor rated at 3200 A or greater. The construction will split into two phases; this WA covers the cost associated with the second construction phase which starts from Structure 8/5 through structure 18/1. | 2018-07-31 | 2018-10-20 | 2018-10-20 | 10391431.3146 | 10391431 |  |  | 100 | 138 | 138 | 9.6 | 959.6 kcmil ACSS/HS/TW | Steel Poles | 75/80 | 6.2 | na | na | 25.101(c)(5)(B)
17T62153 DN | Mitchell Bend - Rocky Creek HT Upgrade | City of Cresson & Grandbury, Hood & Somervell County | Upgrade the Mitchell Bend - Benbrook Junction portion of the Comanche Peak - Benbrook 345 kV Line for High Temperature operation. | 2018-03-01 | 2019-04-30 | 2019-04-30 | 7264911.98 | 7267945 |  |  | 100 | 345 | 345 | 25.1 7.8 | (2) 795 kcmil ACSR & (2) 1590 kcmil ACSR | Steel Lattice | 150 | 25.1 7.8 | na | na | 25.101(c)(5)(B)
0PT37693 DN/WB | Comanche Peak - Wolf Hollow 345kV line Reconductor | City of Granbury, Somervell County | Reconductor south circuits of the Comanche Peak - Benbrook 345 kV Line into Wolf Hollow S.W. | 2018-09-15 | 2018-12-22 | 2018-12-22 | 3871145 | 3871145 |  |  | 100 | 345 | 345 | 7.8 | (2) 1590 kcmil ACSR | Steel Lattice | 150 | 7.8 | na | na | 25.101(c)(5)(B)
17T65143 CB/EH 0PT38735 | Cedar Crest Switching Station - Industrial Blvd Switching Station - Wall Street Switching Station 138 kV Line Upgrade | City of Dallas, Dallas County | Upgrade the 3.1-mile Cedar Crest Sw. Sta. – Industrial Blvd Sw. Sta. double-circuit line and the 0.3-mile Industrial Blvd Sw. Sta. – Wall Street Double-circuit line with a conductor rated 1649 A or greater. Upgrade all 138 kV line terminal and associated equipment to meet or exceed 2000 A. | 2018-04-02 | 2019-12-31 |  | 3164089 | 3105152 |  |  | 75 | 138 | 138 | 3.5 | 959.6 kcmil ACSS/TW | Steel or Concrete Poles | Varies | 3.5 | Varies | na | 25.101(c)(5)(B)
17T65216 CB/EH 0PT38736 | Cedar Crest Switching Station - Wall Street Switching Station 69 kV Line Upgrade | City of Dallas, Dallas County | Upgrade the Cedar Crest Sw. Sta. – Wall Street 69 kV line for 138 kV operations, it will continue to be operated at 69 kV until Compton Street and Wall Street are converted to 138 kV operation. | 2018-04-02 | 2019-12-31 |  | 2643096 | 2324328 |  |  | 75 | 69 | 69 | 3.5 | 959.6 kcmil ACSS/TW | Steel or Concrete Poles | Varies | 3.5 | Varies | na | 25.101(c)(5)(B)
16T65089 KD/RS | Carrollton NW - Crown Road 138 kV Line Rebuild | City of Dallas, Dallas County | Upgrade the 7.1 mile Carrollton NW - Crown Road double-circuit line. Upgrade the 138 kV terminal equipment to meet or exceed 2000 A. | 2018-02-19 | 2019-01-07 | 2019-01-07 | 13126555 | 13126555 |  |  | 100 | 138 | 138 | 14.2 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | na | 7.1 | Varies | na | 25.101(c)(5)(B)
18T65013 JC/AB | Denton Dr. Sw. Sta. - Maple Ave. Sta.138 kV Line | City of Dallas, Dallas County | Rebuild the Denton Drive Station to Maple Avenue Station. The distribution underbuild will be transferred to the new steel monopoles. | 2018-02-12 | 2018-12-31 | 2018-12-31 | 8082746 | 8127335 |  |  | 100 | 69 | 138 | 3 | 795 kcmil ACSR | Steel Poles | Varies | 2 | na | na | 25.101(c)(5)(B)
18T64006 BMcD/CL | Flat Branch (LaTexo) 138 kV POI | Houston County | Install a new 138 kV point of interconnection for Houston County Electric (HCEC) to their existing Latexo 138 kV Substation on the Lufkin Switch - Crockett 138 kV Line. HCEC has requested to switch grids. They are currently in SPP and wish to switch to ERCOT. Install three line sectionalizing switches. | 2018-04-01 | 2020-10-15 |  | 800000 | 726000 |  |  | 80 | 138 | na | 0.06 | 795 kcmil ACSR | Steel Poles | 100 | na | 100 | 0.06 | 25.101(c)(5)(A)
18T64007 BMcD/CL | Jim English (Berea) 138 kV POI | Houston County | Install a new 138 kV point of interconnection for Houston County Electric (HCEC) to their existing Berea 138 kV Substation on the Lufkin Switch - Crockett 138 kV Line. HCEC has requested to switch grids. They are currently in SPP and wish to switch to ERCOT. Install three line sectionalizing switches. | 2018-04-16 | 2020-10-15 |  | 800000 | 900000 |  |  | 90 | 138 | na | 0.06 | 795 kcmil ACSR | Steel Poles | 100 | na | 100 | 0.06 | 25.101(c)(5)(A)
18T61024 SM/DN | Crane - N Odessa 69 kV Relocation | City of Odessa, Ector County | This project covers removing the existing wood H-frames and installing new concrete poles on the Crane - North Odessa 69 kV Line due to modifications being made to widen University Blvd, Odessa, TX. | 2018-12-10 | 2019-01-30 | 2019-01-30 | 210727 | 210727 |  |  | 100 | 69 | na | 0.2 | 4/0 ACSR | Concrete Poles | 50 | 0.15 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the City of Odessa and is 50% reimbursable.
18T65055 CL/AC | Panda Sherman Interconnect 138 kV Line: Stone Creek Switch Line Work | City of Sherman, Grayson County | Reterminate the Panda Sherman - Payne 138 kV Line at the newly constructed Stone Creek Switch utilizing 2 steel monopoles. | 2018-03-22 | 2018-10-21 | 2018-10-23 | 967000 | 967000 |  |  | 100 | 138 | 138 | 0.2 | 2-1926.9 kcmil ACSS/TW | Steel Poles | 70 | 0.2 | na | na | 25.101(c)(5)(B)
18T65056 CL/AC | Collin - Payne 138 kV Line: Stone Creek Switch Line Work | City of Sherman, Grayson County | Reterminate the Collin - Payne 138 kV Line at the newly constructed Stone Creek Switch. | 2018-03-22 | 2018-10-22 | 2018-10-22 | 574300 | 574300 |  |  | 100 | 138 | 138 | 0.2 | 1926.9 kcmil ACSS/TW | Steel Poles | 70 | 0.2 | na | na | 25.101(c)(5)(B)
18T65060 CL/AC | Valley (Sherman NW) - Payne 138 kV Line: Stone Creek Switch Line Work | City of Sherman, Grayson County | Reterminate the Valley (Sherman NW) - Payne 138 kV Line at the newly constructed Stone Creek Switch. | 2018-09-01 | 2018-10-21 | 2018-10-21 | 484960 | 593000 |  |  | 100 | 138 | 138 | 0.2 | 1926.9 kcmil ACSS/TW | Steel Poles | 70 | 0.2 | na | na | 25.101(c)(5)(B)
18T65062 CL/AC | Gainesville Dixon St - Payne 69 kV Line: Stone Creek Switch Line Work | City of Sherman, Grayson County | Reterminate the Gainesville Dixon St - Payne 69 kV Line at the newly constructed Stone Creek Switch. | 2018-09-10 | 2019-02-14 | 2019-02-14 | 353400 | 390000 |  |  | 100 | 69 | 69 | 0.15 | 959.6 kcmil ACSS/TW | Steel Poles | 70 | 0.2 | na | na | 25.101(c)(5)(B)
18T65061 CL/AC | Jordan Whitesboro - Payne 138 kV Line: Stone Creek Switch Line Work | City of Sherman, Grayson County | Reterminate the Jordan Whitesboro - Payne 138 kV Line at the newly constructed Stone Creek Switch. | 2018-09-24 | 2018-10-21 | 2018-10-21 | 672300 | 672300 |  |  | 100 | 138 | 138 | 0.1 | 1926.9 kcmil ACSS/TW | Steel Poles | 70 | 0.1 | na | na | 25.101(c)(5)(B)
18T65063 CL/AC | Stone Creek - Payne 138 kV Line: Stone Creek Switch Line Work | City of Sherman, Grayson County | Create a new line that connects existing Payne Substation to the newly constructed Stone Creek Switch. | 2018-09-17 | 2018-11-18 | 2018-11-20 | 450000 | 560000 |  |  | 100 | 138 | 138 | 0.2 | 1926.9 kcmil ACSS/TW | Steel Poles | 70 | 0.2 | na | na | 25.101(c)(5)(B)
18T65059 CL/AC | Valley (Sherman E) - Payne 138 kV Line: Stone Creek Switch Line Work | City of Sherman, Grayson County | Reterminate the Valley (Sherman E) - Payne 138 kV Line at the newly constructed Stone Creek Switch. | 2018-09-17 | 2018-11-11 | 2018-11-11 | 653300 | 701000 |  |  | 100 | 138 | 138 | 0.4 | 1926.9 kcmil ACSS/TW | Steel Poles | 70 | 0.4 | na | na | 25.101(c)(5)(B)
18T65058 CL/AC | Bonham - Payne 69 kV Line: Stone Creek Switch Line Work | City of Sherman, Grayson County | Reterminate the Bonham - Payne 69 kV Line at the newly constructed Stone Creek Switch. | 2018-09-17 | 2018-11-30 | 2018-12-08 | 351500 | 535000 |  |  | 100 | 69 | 69 | 0.2 | 959.6 kcmil ACSS/TW | Steel Poles | 70 | 0.2 | na | na | 25.101(c)(5)(B)
18T65064 CL/AC | Anna Sw - Payne 138 kV Line: Stone Creek Switch Line Work | City of Sherman, Grayson County | Reterminate the Anna Sw - Payne 138 kV Line at the newly constructed Stone Creek Switch. | 2018-09-17 | 2018-10-27 | 2018-10-27 | 380700 | 380700 |  |  | 100 | 138 | 138 | 0.2 | Bundled 959.6 kcmil ACSS/TW | Steel Poles | 70 | 0.2 | na | na | 25.101(c)(5)(B)
17T65205 CC | Royse Switch - Garland Oates: Line Work To Establish Creekside Substation | City of Rowlett, Dallas/Rockwall Counties | Line Loop to tap into the existing Royse Sw – Garland Oates 138 kV line | 2018-04-16 | 2018-12-01 | 2018-12-01 | 784365 | 1246447 |  |  | 100 | 138 | 138 | 0.22 | (2) 959 ACSS/TW | Steel Poles | 50 | 0.22 | na | na | 25.101(c)(5)(A)
17T63157 RJ/RS | Morgan Creek Switch - Barber Lake Switch (East) 138 kV Line CMPC System Hardening | Colorado City, Mitchell County | Replace two (2) single-circuit wood H frames with two (2) single-circuit concrete H frames. | 2018-10-01 | 2018-12-12 | 2018-12-12 | 298772.49 | 299386 |  |  | 100 | 138 | 138 | 0.1 | 1-636 ACSR | Concrete H-Frame | 50 | 0.1 | na | na | 25.101(c)(5)(B)
18T64039 JL | Trinidad Sw - Long Lake 138 kV Line: CMPC Line Hardening US-287 | Anderson County | Rebuild two (2) single-circuit wood H frames with two (2) single-circuit concrete H frames at US-287 crossing. | 2018-10-20 | 2018-10-22 | 2018-10-22 | 324391 | 324391 |  |  | 100 | 138 | 138 | 0.1 | 336 kcmil ACSR | Concrete H-Frame | 50 | 0.1 | na | na | 25.101(c)(5)(B)
18T61034 SEI/MK 0PT37605 | TxDOT Relocation, Liggett-Saginaw 138 kV Line | City of Irving, Dallas County | Install new double-circuit, steel tangent structures. Remove four (4) existing double-circuit steel tangent structures. | 2019-11-01 | 2019-12-31 |  | 1193327.68 | 1193327.68 |  |  | 0 | 138 | na | 1.1239 | 1033.5 kcmil ACSR | Steel Poles | 140 | 0.56193 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
18T61033 SEI/MK 0PT37604 | TxDOT Relocation, Liggett-Hackberry 138 kV Line | City of Irving, Dallas County | Install new double-circuit, steel tangent structures. Remove four (4) existing double-circuit steel tangent structures. | 2019-10-16 | 2019-12-31 |  | 1193327.68 | 1193327.68 |  |  | 0 | 138 | na | 1.1239 | 1033.5 kcmil ACSR | Steel Poles | 140 | 0.56193 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
18T64043 OR | Shamburger Sw - Hideaway Lake 138 kV Line: Cut-In to Est Greys Lake | City of Tyler, Smith County | This project is to construct a 1.25 double-circuit tap loop line off of the existing Shamburger Sw to Hideaway Lake 138 kV Line. | 2018-08-06 | 2018-10-09 | 2018-10-09 | 2737770 | 2837941 |  |  | 100 | 138 | na | 1.3 | 959.6 ACSS/TW/HS | Steel Poles | na | 0.5 | 110 | 0.96 | 25.101(c)(5)(A)
17T64136 JL | Lake Creek Switch - Waco West 138 kV Line: CMPC Major Highway Crossing Hardening | McLennan County | Rebuild two (2) single-circuit wood H frames with two (2) single-circuit concrete H frames at I-35 crossing. | 2018-11-12 | 2018-11-15 | 2018-11-15 | 312090 | 312090 |  |  | 100 | 138 | 138 | 0.1 | 2-636 kcmil ACSR | Concrete H-frame | 100 | 0.1 | na | na | 25.101(c)(5)(B)
17T63143 CB/AB | Morgan Creek-McDonald Rd 138 kV Line Modification | Mitchell County | The scope of work consists of replacing one (1) wood H-frame tangent with taller concrete H-frame Tangent and replacing one (1) wood Tangent H-frame with two (2) Steel three-pole Tangent deadends. The structure replacement locations are indicated on the attached map. The conductor will remain 636 ACSR with (1) one conductor per phase and two (2) 3/8 EHS shield wires. | 2018-10-10 | 2018-11-02 | 2018-11-02 | 595109.51 | 675000 |  |  | 100 | 138 | na | 0.25 | 636 ACSR | Concrete H-frame and self supporting steel three-pole | 50 | 0.25 | na | na | 25.101(c)(5)(B)
18T63122 BC/JO | Riverton Sw. - Tunstill POD: Arroyo Bluff POD 138 kV Line | City of Orla, Reeves County | Install 0.75 miles of single-circuit capable steel and concrete structures utilizing 1926.9 kcmil ACSS/TW. | 2018-08-01 | 2018-12-10 | 2018-12-10 | 1026240 | 1026240 |  |  | 100 | na | 138 | 0.08 | 1926.9 kcmil ACSS/TW | Concrete & Steel Poles | na | na | 75 | 0.8 | 25.101(c)(5)(A)
18T63101 JM/CW | Barstow NW - Culberson 138 kV Line: Pecone POI | Reeves County | Establish a point of interconnection to ORYX Delaware Oil Transport’s Pecos Station on the southern circuit of the Barstow NW - Culberson 138 kV transmission line by way of TNMP. The point of interconnection will be located in the Barstow NW - Maverick Draw line section between structures 4/1 and 4/3. | 2018-09-24 | 2018-10-17 | 2018-10-17 | 1245919.86 | 1251369 |  |  | 100 | 138 | 138 | 0.24 | 1926.9 ACSS/TW/HS | Steel Poles | 70 | na | 100 | 0.24 | 25.101(c)(5)(A)
16T64126 JC/RS | Herty North - Nacogdoches 138 kV Line: Retermination | Nacogdoches County | Reterminate the Herty N. – Nacogdoches SE Sta. 138 kV Line into the relocated Nacogdoches SE Sw. Station. | 2018-11-01 | 2018-12-14 | 2018-12-14 | 552429 | 552429 |  |  | 100 | 138 | 138 | 0.25 | 959.6 kcmil, ACSS/TW | Steel Monopoles | Station | na | na | na | 25.101(c)(5)(A)
16T64140 JC/RS | Lufkin - Nacogdoches 138 kV Line: Nacogdoches SE Sw. Line Work | Nacogdoches County | Reterminate the Lufkin – Nacogdoches 138 kV Line into the relocated Nacogdoches SE Sw. Station. | 2018-11-01 | 2019-03-17 | 2019-03-17 | 798501 | 798501 |  |  | 100 | 138 | 138 | 0.3 | 1926.9 kcmil ACSS/TW | Steel Monopoles | Station | na | na | na | 25.101(c)(5)(A)
16T64125 JC/RS | Chireno - Nacogdoches 138 kV Line: Retermination | Nacogdoches County | Reterminate the Chireno – Nacogdoches SE Sta. 138 kV Line into the relocated Nacogdoches SE Sw. Station. | 2018-11-01 | 2018-12-15 | 2018-12-15 | 782098 | 782098 |  |  | 100 | 138 | 138 | 0.35 | 959.6 kcmil, ACSS/TW | Steel Monopoles | Station | na | na | na | 25.101(c)(5)(A)
16T64124 JC/RS | Nacogdoches N - Nacogdoches SE 138 kV: Retermination | Nacogdoches County | Reterminate the Nacogdoches N. – Nacogdoches SE Sta. 138 kV Line into the relocated Nacogdoches SE Sw. Station. | 2018-11-02 | 2018-12-19 | 2018-12-19 | 659849 | 659849 |  |  | 100 | 138 | 138 | 0.35 | 1926.9 kcmil ACSS/TW | Steel Monopoles | Station | na | na | na | 25.101(c)(5)(A)
16T64086 JC/RS | Nacogdoches N - Nacogdoches SE 138 kV Rebuild | Nacogdoches County | Rebuild the existing 6.8 mile Nacogdoches N. – Nacogdoches SE Sta. 138 kV Line on new double-circuit steel monopoles. | 2018-07-05 | 2018-12-19 | 2018-12-19 | 8857335 | 8857335 |  |  | 100 | 138 | 138 | 13.6 | 1926.9 kcmil ACSS/TW | Steel Monopoles | 100 | 6.8 | na | na | 25.101(c)(5)(B)
17T65228 MK/MP | Cedar Hill - Liggett 138 kV Line: Rebuild Cedar Hill - Venus Tap | City of Grand Prairie, Dallas County | Rebuild the Cedar Hill - Venus Tap 138 kV Line section of the Cedar Hill - Liggett 138 kV Line. The existing line is 5.5 miles of double-circuit steel lattice towers and single-circuit wood h-frame structures. The final build will utilize 11 single-circuit steel monopoles and 42 double-circuit steel monopoles. | 2018-02-15 | 2018-11-28 | 2018-11-28 | 3167599 | 3285401 |  |  | 100 | 138 | na | 5.5 | 1926.9 ACSS/TW | Steel Poles | 100 | 5.5 | na | na | 25.101(c)(5)(B)
18T63110 SP/JO | Wink - Notrees Sw. 138 kV Line: Magwalt POD | City of Kermit, Winkler county | Install a 138 kV point-of-delivery (POD) for Atlas Sand's North Substation on the Wink – Notrees 138 kV Line. | 2019-03-01 | 2019-04-03 | 2019-04-03 | 978561.69 | 978562 |  |  | 100 | 138 | na | 0.3 | 336.4 kcmil ASCR | Concrete/Wood Poles | 50 | na | 75 | 0.01 | 25.101(c)(5)(A)
18T63100 SP/JO | Moss - Yucca Drive Sw. 138 kV Line: Penwell POD | City of Monahans, Ward County | Install a 138 kV point-of-delivery (POD) for Atlas Sand's South Substation on the Moss - Yucca Drive 138 kV Line. | 2018-09-04 | 2018-10-19 | 2018-10-19 | 987064.2 | 987064 |  |  | 100 | 138 | na | 0.1 | 795 kcmil ACSR | Concrete/Wood Poles | 75 | na | 102.5 | 0.01 | 25.101(c)(5)(A)
18T62059 CH | Hicks SW - Elizabeth Creek 138 kV Line: Blue Dove Sub POI to Wellington (BEC) | Tarrant County | This project is to cut-in the Hicks Switching Station - Elizabeth Creek 138 KV Line to the new Blue Dove 138 kV Substation. | 2018-10-10 | 2018-11-21 | 2018-11-21 | 503302.22 | 503302.22 |  |  | 100 | na | 138 | 5.5 | 959.6 kcmil ACSS/TW | Steel or Concrete Poles | 50 | 5.5 | 50 | na | 25.101(c)(5)(A)
18T63020 CH | Phillips Andrews - Fullerton Sw 138 kV Line | Andrews County | This project is to rebuild and upgrade the existing Fullerton to Phillips Andrews 69kV line to 138 kV with double-circuit capable structures. | 2018-09-25 | 2018-12-15 | 2018-12-15 | 6022479.98 | 6022479.98 |  |  | 100 | na | 138 | 5.5 | 959.6 kcmil ACSS/TW | Steel or Concrete Poles | 50 | 5.5 | 50 | na | 25.101(c)(5)(B)
18T61038 SEI/MK | TxDOT Relocation, Judd Court 138 kV Tap Line | City of Garland, Dallas County | Install new single-circuit, steel dead end and tangent structures. Remove four (4) existing single-circuit steel tangent structures. | 2019-01-14 | 2019-04-02 | 2019-04-02 | 875226.27 | 875226.27 |  |  | 100 | 138 | na | 0.47386 | 336.4 kcmil ACSR and 959.6 kcmil ACSS/TW | Steel Monopole Structures | na | na | na | na | 25.101(C)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
18T61039 SEI/MK | TxDOT Relocation, Kirkland Park-Centerville Sw. 138 kV Line | City of Garland, Dallas County | Install new double-circuit, steel tangent structures. Remove nine (9) existing double-circuit steel tangent structures. | 2018-12-17 | 2019-12-31 |  | 1755049.01 | 3445119 |  |  | 25 | 138 | na | 2.0958 | 1033.5 kcmil ACSR | Steel Monopole Structures | Varies | 1.0479 | na | na | 25.101(C)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
17T61078 SEI/MK | AEP Lotebush - Blake Draw 138 kV Line | City of Coyanosa, Pecos County | Install new single-circuit, steel dead end structures. Remove existing single-circuit temporary wood pole structures. | 2019-01-29 | 2019-04-22 | 2019-04-22 | 400000 | 400000 |  |  | 100 | 138 | na | 0.11856 | 959.6 kcmil ACSS/TW | Steel Monopole Structures | Varies | 0.11856 | na | na | 25.101(C)(5)(B)
18T64035 EH/CM | Montfort - Corsicana 138 kV Line: Corsicana Sw. Station line Work | Navarro County | This project is to re-route the existing 138 kV Montfort line to the new terminal at the Corsicana Station. | 2018-11-12 | 2018-11-20 | 2018-11-20 | 119018.94 | 119018.94 |  |  | 100 | 138 | 138 | 0.5 | 1033 kcmil ACSR | Steel Poles | Station | na | na | na | 25.101(c)(5)(A)
15T64031 EH/CM | Corsicana - Mildred 69 kV Line Rebuild to 138 kV Line | Navarro County | This project is to rebuild the Corsicana - Mildred 69 kV line to a 138 kV line. | 2019-01-03 | 2019-06-28 | 2019-06-28 | 11854408.55 | 14093244 |  |  | 100 | 69 | 138 | 9.5 | 959.6 kcmil ACSS/TW | Steel Poles | 50 | 9.5 | na | na | 25.101(c)(5)(B)
18T65209 EH/CM | Navarro -Mildred 69 kV Line Rebuild to 138 kV Line | Navarro County | This project is to rebuild the Navarro - Mildred 69 kV line to a 138 kV line. | 2018-09-01 | 2018-12-18 | 2018-12-18 | 3078089.69 | 3223280 |  |  | 100 | 69 | 138 | 2 | 959.6 kcmil ACSS/TW | Steel Poles | 50 | 2 | na | na | 25.101(c)(5)(B)
18T62090 EH/CM | Trinidad - Hillsboro 138 kV Line: Navarro Substation line Work | Navarro County | This project is to re-route the existing 138 kV Trinidad - Hillsboro line into the Navarro Substation to accommodate the upgrade to Navarro-Mildred from 69 kV to 138 kV. | 2018-09-01 | 2018-11-12 | 2018-11-12 | 492893.21 | 506500 |  |  | 100 | 138 | 138 | 0.2 | 959.6 kcmil ACSS/TW | Steel Poles | 100 | 0.2 | na | na | 25.101(c)(5)(B)
18T65183 CM/EH | Blackland Tap 138 kV | City of Fate, Rockwall County | This project is to re-route the existing 138 kV Royse Sw Sta-Terrell SW Sta 138 kV Line at the new Blackland Substation. | 2019-01-09 | 2019-02-28 | 2019-02-28 | 302015.83 | 302015.83 |  |  | 100 | 138 | 138 | 0.1 | 959.6 kcmil ACSS/TW | Steel Poles | 100 | 0.1 | na | na | 25.101(c)(5)(A)
18T64014 BMcD/CL | Lufkin Switch - Crockett 138 kV Line Re-Termination | City of Crockett, Houston County | Modification of the existing Lufkin Switch - Crockett 138 kV Line into the new line terminal being built as a part of the Crockett Switch upgrade and expansion project. This re-termination will be 0.24 miles of single-circuit construction with one circuit of 1590 kcmil ACSR conductor installed. | 2018-09-04 | 2018-11-01 | 2018-11-01 | 360000 | 355000 |  |  | 100 | 138 | na | 0.24 | 1590 kcmil ACSR | Steel/Concrete Poles | 100 | 0.24 | na | na | 25.101(c)(5)(A)
18T64015 BMcD/CL | Jewett Switch - Crockett 138 kV Line Re-Termination | City of Crockett, Houston County | Modification of the existing Jewett Switch - Crockett 138 kV Line into the new line terminal being built as a part of the Crockett Switch upgrade and expansion project. | 2018-10-22 | 2018-12-19 | 2018-12-19 | 350000 | 330000 |  |  | 100 | 138 | na | 0.1 | 959.6 kcmil ACSS/TW | Steel Pole | 100 | 0.1 | na | na | 25.101(c)(5)(A)
18T65224 CL/AC | Valley - Anna Sw 345 kV Line: Raise Towers | City of Anna, Collin County | Raise two (2) steel tangent towers to provide electrical clearance to the proposed rebuild of the Van Alstyne - Anna Sw 138 kV line. | 2018-11-27 | 2019-01-25 | 2019-01-25 | 693160 | 830000 |  |  | 100 | 345 | 345 | 0.2 | Bundled 959 ACSS/TW | Steel Towers | 170 | na | na | na | 25.101(c)(5)(B)
18T65005 CL/AC | Payne - Anna Sw 138 kV Line: Rebuild Van Alstyne to Anna Switch | Cities of Van Alstyne, Anna, Grayson and Collin Counties | Rebuild and upgrade a portion of the Payne - Anna Sw 138 kV Transmission Line. | 2019-01-21 | 2019-05-04 | 2019-05-04 | 11415500 | 13175000 |  |  | 100 | 138 | 138 | 7.5 | Bundled 959 ACSS/TW | Steel Poles | Varies | 7.5 | na | na | 25.101(c)(5)(B)
18T65057 CL/AC | Valley - Sherman S Tie - 138 kV Line Tie | City of Sherman, Grayson County | Connect the Valley 138 kV Line and the Sherman South 138 kV Line to create one new line that goes from Valley to Sherman South. This new connection is due to the construction of the new Stone Creek Switch. | 2018-10-28 | 2018-11-01 | 2018-11-01 | 479400 | 500000 |  |  | 100 | 138 | 138 | 0.3 | 1926.9 kcmil ACSS/TW | Steel Poles | Varies | 0.25 | na | na | 25.101(c)(5)(A)
18T62047 JHL/JO | White Settlement - Hilltop SW. STA. (BEPC) 69 kV Line: Rebuild | Tarrant County | Converting the 1.3-mile 69 kV line to 138 kV from White Settlement to the intersection of the White Settlement – Hilltop 69 kV and Eagle Mountain – Calmont 138 kV Lines. Connect the 138 kV line to Eagle Mountain – Calmont 138 kV Line. | 2018-07-15 | 2018-11-27 | 2018-11-27 | 1287147.11 | 1287147 |  |  | 100 | 69 | 138 | 1.3 | 959.6 ACSS/TW | Steel monopoles | 100 | 1.3 | na | na | 25.101(c)(5)(B)
0PT04371 DN | Wink Sw. Sta. – Yukon Sw. Sta. 138 kV adding 2nd Circuit | Winkler County/Odessa County | The scope of the work entails adding the second circuit of the newly constructed Yukon Sw. Sta. to Wink Sw. Sta. | 2018-04-15 | 2019-06-30 | 2019-06-30 | 6500000 | 10421193 |  |  | 100 | 138 | 138 | 36 | 1926.9 ACSS/TW | Steel Monopoles | 50 | 36 | na | na | 25.101(c)(5)(C)
17T65219 WW/JO | Northaven - Morrison Lane 138 kV Line: Northaven Line Work | City of Dallas, Dallas County | Reterminate the Northaven-Morrison Lane 138 kV Transmission Line at the Northaven Switch Station. | 2018-08-20 | 2018-12-22 | 2018-12-22 | 431711.14 | 473292.93 |  |  | 100 | 138 | 138 | 0.1 | 959 ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(B) | Projects exists entirely within Northaven Substation
17T65218 WW/JO | Northaven - Kirkland Park 138 kV Line: Northaven Line Work | City of Dallas, Dallas County | Reterminate the Northaven-Kirkland Park 138 kV Transmission Line at the Northaven Switch Station. | 2018-11-10 | 2019-03-23 | 2019-03-23 | 832746.33 | 759106.64 |  |  | 100 | 138 | 138 | 0.1 | 959 ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(B) | Projects exists entirely within Northaven Substation
05T64082 JS/AB | Temple - Belton 138 kV Line - Rebuild Sections | Bell County | Upgrade the Temple – Belton 138 kV line is a hardening project for Oncor. Three (3) different priority areas will be reviewed as part of this project. The upgraded areas will be rebuilt utilizing 138 kV single-circuit concrete H-Frames predominantly. | 2018-09-15 | 2018-10-26 | 2018-10-26 | 1252937.1375 | 1487312 |  |  | 100 | 138 | 138 | 0.87 | 795 kcmil ACSS | Concrete H-Frames | Centerline | 0.87 | na | na | 25.101(c)(5)(B)
18T62137 BP/IA | Hicks Sw. Sta. - Saginaw 138 kV Double-Circuit Line | City of Saginaw, Tarrant County | Reconductor both circuits of the Hicks Sw. Sta. - Saginaw 138 kV line, including the Fossil Creek Tap. | 2018-10-01 | 2018-12-15 | 2018-12-15 | 5492151.12 | 5282592 |  |  | 100 | 138 | na | 19.6 | 959.6 kcmil ACSS/TW/E3X | Lattice Towers and Steel Poles | 75 | 9.8 | na | na | 25.101(c)(5)(B)
18T64091 CL/BMcD | Jewett Switch - Crockett 138 kV Line: Rebuild Grapeland Magnolia Tap to Crockett | Crockett and Houston County | Rebuild the 9.2 mile section from Grapeland Magnolia Tap to Crockett of the Jewett - Crockett 138 kV Line using double-circuit monopole construction with only one circuit installed. | 2018-10-01 | 2019-05-14 | 2019-05-14 | 9845000 | 9931000 |  |  | 100 | 138 | 138 | 9.2 | 959.6 kcmil ACSS/TW | Steel Poles | 100 | 9.2 | na | na | 25.101(c)(5)(B)
0PT37338 JM/DN | Wichita Falls - Burkburnett 69 kV: Rebuild from Wichita Falls North to 2/5 | Wichita Falls, Wichita County | Rebuild and upgrade the Wichita Falls - Burkburnett 69 kV line. | 2019-01-15 | 2019-03-18 | 2019-03-18 | 2644756 | 2950000 |  |  | 100 | 69 | na | 1.58 | 959.6 MCM ACSS/TW | Steel Poles | 50 | 1.58 | na | na | 25.101(c)(5)(B)
18T65070 CM/EH | Rockwall South - Forney Switch 138 kV Line Rebuild | Rockwall and Kaufman Counties | Rebuild the Rockwall South - Forney Switch 138 kV line. | 2018-08-30 | 2018-12-31 | 2018-12-31 | 6819216 | 6819216 |  |  | 100 | 138 | 138 | 7.9 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 7.9 | na | na | 25.101(c)(5)(B) | WA split from Royse Switch -Forney, WA 17T65012
18T62153 JM/JO | Leon Sw. Sta. - Ranger Gulf 69 kV Line: Lake Leon POI | Eastland County, TX | To establish a point of interconnection to Brazos Electric Power Cooperative (BEC) on the Leon Sw. Sta. - Ranger Gulf 69 kV Line. | 2/29/2019 | 2019-05-16 | 2019-05-16 | 927278.32 | 1020000 |  |  | 100 | 69 | na | 0.1 | 959.6 ACSS/TW | Concrete poles and Steel H-Frame Switch | 50 | 0.1 | na | na | 25.101(c)(5)(A)
17T62069 KF/DN 0PT38781 | Everman Switch - Cedar Hill Switch 345 kV Line (Courtland-Cedar Hill Section): HT Upgrade | City of Arlington, Tarrant County | Upgrade the Courtland - Cedar Hill Switch section of Everman Switch - Cedar Hill Switch 345 kV Line. | 2018-09-15 | 2019-05-16 | 2019-05-16 | 4455604 | 4800000 |  |  | 100 | 345 | na | 20.66 | 795 kcmil ACSR | Steel Lattice | 150 | 11.3 | na | na | 25.101(c)(5)(B) | WA split from Courtland - Cedar Hill, WA 17T62069
18T63165 KF/DN | Permian Basin - Odessa EHV 138 kV Line: Yarbrough Substation Cut-in | Crane County | Relocate structures to cut-in Yarbrough Substation | 2018-09-25 | 2018-12-05 | 2018-12-05 | 1542308 | 1542308 |  |  | 100 | 138 | na | 0.05 | 795 kcmil ACSR | Steel Poles | na | na | na | na | 25.101(c)(5)(A)
0PT37192 SP | Rivercrest Switch - Sulphur Springs East Tap 138 kV Line : CMPC Line Hardening | City of Sulphur Springs, Hopkins County | This is a CMPC Project that covers the cost to rebuild a section of the Rivercrest Switch - Sulphur Springs East Tap 138 kV Line in Hopkins County. The section is 0.1 miles of single-circuit wood H-Frames. | 2019-10-14 | 2019-10-18 |  | 681893 | 681893 |  |  | 1 | 138 | na | 0.1 | 336.4 kcmil ACSR | Steel H-Frames | 100 | na | na | na | 25.101(c)(5)(B)
0PT37181 AF/AB | Scyene Road Sub - Parkdale Switch 138 kV Line | City of Dallas, Dallas County | Replace existing 7/16" shield wire with OPGW 0.546 diameter | 2018-11-27 | 2018-12-31 | 2018-12-31 | 718445.08 | 708810 |  |  | 100 | 138 | na | 3.25 | na | Steel Tower | 125' | 3.25 | na | na | 25.101(c)(5)(B) | Replacing shield wire with optical ground wire (OPGW). This project is tied to WA#0PT37183. The project was originally 6.02 miles long and went from Parkdale Sw - Prairie Creek Switch. The project has been broken into two (2) separate projects.
0PT37183 AF/AB | Scyene Road Sub - Prairie Creek Switch 138 kV Line | City of Dallas, Dallas County | Replace existing 7/16" shield wire with OPGW 0.546 diameter | 2018-11-27 | 2018-12-31 | 2018-12-31 | 634764.72 | 595623 |  |  | 100 | 138 | na | 2.77 | na | Steel Tower | 125 | 2.77 | na | na | 25.101(c)(5)(B) | Replacing shield wire with optical ground wire (OPGW). This project is tied to WA#0PT37181. The project was originally 6.02 miles long and went from Parkdale Sw - Prairie Creek Switch. The project has been broken into two (2) separate projects.
17T63206 AF/SEI | Eskota SW. - Sweetwater Creek NO. 2 : 69 kV CMPC Line Hardening | City of Sweetwater, County of Nolan | Relocate and replace 6 structures across Interstate 20 for CMPC System Hardening | 2020-04-01 | 2020-04-30 |  | 588652.67 | 706000 |  |  | 0 | 69 | na | 0.1 | ACSR 4/0 | Steel Monopole, Wood Monopole | 50 | 0.1 | na | na | 25.101(c)(5)(B)
0PT37196 AF/SEI | Eskota Switch - Sweetwater Creek POI 69 kV Line | City of Sweetwater, County of Nolan | Relocate and replace 4 structures across Interstate 20 for CMPC System Hardening | 2020-06-01 | 2020-06-30 |  | 708375.72 |  |  |  | 0 | 69 | na | 0.1 | ACSR 4/0 | Concrete Monopole, Wood Monopole | 50 | 0.1 | na | na | 25.101(c)(5)(B)
17T63211 GD/SEI | Sweetwater Downtown Tap 138 KV Line: CMPC System Hardening | City of Sweetwater, County of Nolan | Rebuild a section of the Eskota Switch – Morgan Creek Switch Downtown Tap 138 kV Line in Nolan County. The section is 0.1 miles of single-circuit wood monopoles with single post insulators. | 2019-10-30 | 2019-11-30 |  | 483277 | 300000 |  |  | 0 | 138 | na | 0.24 | 336.4 kcmil ACSR | Concrete Monopole | 50 | 0.24 | na | na | 25.101c(5)(B)
17T63207 BB SEI | Colorado City - China Grove Sw. 69 kV Line: CMPC System Hardening | City of Colorado City, Mitchell County | Relocate and replace 3 structures across I-20 for CMPC System Hardening | 2019-09-03 | 2019-09-19 | 2019-09-19 | 524709 | 524709 |  |  | 100 | 69 | na | 0.3 | 4/0 ACSR | Concrete Poles | 50 | 0.3 | na | na | 25.101(c)(5)(B)
0PT37296 DD | Forest Grove Switch - Canton Switch 138 kV Line : CMPC System Hardening | City of Canton, Van Zandt County | Relocate and replace 2 structures across I-20 for CMPC Hardening. | 2019-05-06 | 2019-05-11 | 2019-05-11 | 629033.47 | 629033 |  |  | 100 | 138 | na | 0.1 | 336.4 kcmil ACSR | Concrete H-Frames | 100 | 0.1 | na | na | 25.101(c)(5)(B)
17T64134 DD | Canton Tap Switch - Tyler Switch 138 kV Line: CMPC System Hardening | City of Van, Van Zandt County | Relocate and replace 2 structures across I-20 for CMPC Hardening. | 2019-04-29 | 2019-05-05 | 2019-05-05 | 526577 | 526577 |  |  | 100 | 138 | na | 0.1 | 636 kcmil ACSR | Concrete H-Frames | 100 | 0.1 | na | na | 25.101(c)(5)(B)
17T63209 SF | Eskota SW. - Flintkote -U.S. Gypsum 69 kV Line: CMPC Line Hardening | City of Sweetwater, Nolan County | This Work Authorization (WA) covers the cost to rebuild a section of the Eskota Sw. - Flintkote - U.S. Gypsum 69 kV line in Nolan County. | 2019-07-08 | 2019-08-02 | 2019-08-05 | 1040085 | 1040085 |  |  | 100 | 69 | 69 | 0.6 | 1/0 ACSR | Steel Poles & Concrete Poles | 50 | na | Varies | na | 25.101(c)(5)(B) | Replacing wood structures with Steel & Concrete as part of CMPC hardening project
18T65015 SM/DN | NW Carrolton Switch - Lakepointe Switch (TNMP) 138 kV Line: Rebuild | City of Carrollton, Denton County | This project covers the rebuild of the 2.3-mile, Oncor portion of the 2.4-mile NW Carrollton - Lakepoint (TNMP) 138 kV Line using a conductor 3200 A or greater. | 2018-09-19 | 2019-03-23 | 2019-03-23 | 9154972 | 9154972 |  |  | 100 | 138 | 138 | 2.3 | 959.6 kcmil ACSS/TW | Steel Poles | 70 | 2.3 | 70 | na | 25.101(c)(5)(B)
0PT37441 JM/DN | Burkburnett - Sheppard AFB 69 kV Tap: Line Relocation | City of Wichita Falls, Wichita County | Relocate a section of this line to accommodate new base entrance construction onto Sheppard AFB. | 2019-07-10 | 2019-07-19 | 2019-07-19 | 500000 | 500000 |  |  | 100 | 69 | na | 0.32 | 4/0 ACSR | Wood Poles | na | na | na | na | 25.101(c)(5)(D) | Relocation is at the request of Sheppard Air Force Base and is 100% reimbursable by the United States Air Force.
18T63125 JO/JM | Wink - Culberson 138 kV Line: Rustler Hills POD for Chevron Hayhurst | Culberson County | Establish a point of delivery to Chevron's Hayhurst on the northern circuit of the Wink - Culberson 138 kV transmission line. The point of delivery will be located in the Screwbean Tap - Black River line section. | 2018-11-10 | 2018-12-09 | 2018-12-09 | 1100000 | 1100000 |  |  | 100 | 138 | 138 | 0.1 | 795 ACSR | Steel Poles/ H-frame Switch | 50 | na | 70 | 0.1 | 25.101(c)(5)(A)
16T62080 | Burleson-Mansfield 138 kV Line | City of Burleson, Tarrant County | Rebuild the ten miles of single-circuit line currently utilizing wood H-Frames with 795 ACSR conductor. | 2018-09-25 | 2018-12-31 | 2018-12-31 | 15083320 | 16200000 |  |  | 100 | 138 | 138 | 10 | 1926.9 kcmil ACSS/TW | Steel Poles | 50 | 10 | na | na | 25.101(c)(5)(B)
0PT37335 CM/EH | Blackland Sw. - RCEC Blackland Sub 138 kV Line | City of Fate, Rockwall County | Connect the new Blackland Switch to the new RCEC Blackland Substation. | 2019-01-09 | 2019-06-26 | 2019-06-26 | 411416 | 411416 |  |  | 100 | 138 | 138 | 0.1 | 959.6 kcmil ACSS/TW | Steel Poles | 100 | 0.1 | na | na | 25.101(c)(5)(A) | Waiting on REC to complete their work in order for Oncor to complete station T-Line connection.
18T63007 SM/DN | Fisher Rd. Sw. Sta. - Wichita Falls 138 kV: Retermination | City of Wichita Falls, Wichita County | Rebuild the 138 kV switchyard in a ring bus arrangement and relocating the load-serving transformers #3 and #4 to the Burnett Switch – Fisher Road 138 kV Line at Burnett Switch. | 2018-10-01 | 2018-11-08 | 2018-11-08 | 908063 | 715000 |  |  | 100 | 138 | 138 | 0.3 | 959.6 kcmil ACSS/TW | Steel Poles | 50 | 0.2 | na | na | 25.101(c)(5)(B) | On Oncor Substation Property
18T62161 SM/DN | South Wichita - Wichita Falls 138 kV: Retermination | City of Wichita Falls, Wichita County | Reterminate the South Wichita Falls Switch - Wichita Falls Switch 138 kV Line at Burnett Switch 138 kV (Formally Wichita Falls Switch). This retermination will be 0.3 miles of single-circuit construction utilizing standard two monopoles construction. | 2018-10-01 | 2018-11-08 | 2018-11-08 | 880543 | 880543 |  |  | 100 | 138 | 138 | 0.2 | 959.6 kcmil ACSS/TW | Steel Poles | 50 | 0.2 | na | na | 25.101(c)(5)(B) | On Oncor Substation Property
18T63150 SB/JO | Arco - Crane 138 kV Line: POD | Crane County | Establish a point of delivery to Oryx Midstream Services' Crane Substation on the Arco - Crane 138 kV Transmission line. The point of delivery will be located between structures 8/6 and 8/7 and will include a 0.96 mile extension to the new substation location. | 2018-09-17 | 2018-11-01 | 2018-11-01 | 1551080.75 | 2200000 |  |  | 100 | 138 | 138 | 0.96 | 795 kcmil ACSR | Steel and Concrete Poles | 75 | na | 100 | 0.96 | 25.101(c)(5)(A) | Installation of interconnection is at the request of Oryx Midstream Services.
0PT37350 GB/MK | Lufkin Switch - Nacogdoches Switch 138 kV line | City of Nacogdoches, Nacogdoches County | Remove two (2) wood H-Frame structures 17/7A & 17/8 and relocate one (1) wood H-Frame structure 17/8 in the City of Nacogdoches. | 2018-11-01 | 2018-12-29 | 2018-12-29 | 150000 | 127000 |  |  | 100 | 138 | na | 0.2 | 636 kcmil ASCR | Wood H-Frame | 100 | na | na | na | 25.101 (c)(5)(E)
0PT37267 CW/ KF | Benbrook Switch - Wedgewood Switch 138 kV Line North Tap: Rebuild | City of Fort Worth, Tarrant County | Upgrade the conductor on the 0.2 mile Benbrook North Tap 138 kV Line, in order to relieve heavy winter loads | 2018-10-01 | 2018-12-01 | 2018-12-01 | 544042 | 522549 |  |  | 100 | 138 | na | 0.2 | 795 kcmil ACSR | Steel Monopoles | 100 | na | 100 | na | 25.101(c)(5)(B)
0PT37473 SF/IA | Calmont Sub - Hilltop Switch 69 kV Line : Pole Replacement | City of White Settlement Tarrant County | Rebuild the 0.1 mile section of the Calmont Sub. - Hilltop SW. line by replacing one (1) single-circuit wood guyed deadend structure with one (1) single-circuit concrete monopole structure. | 2018-11-01 | 2018-11-21 | 2018-11-21 | 128520.48 | 222000 |  |  | 100 | 69 | na | 0.1 | 556 kcmil ACSR | Concrete Pole | 25 | na | 25 | na | 25.101(c)(5)(B)
0PT37357 JL | Morgan Creek Switch - Sun Switch 138 kV Line: CMPC Major Highway Crossing Hardening | Mitchell County | Rebuild two (2) single-circuit wood H frames with two (2) single-circuit concrete H frames at I-20 crossing. | 2019-03-08 | 2019-03-15 | 2019-03-15 | 254525 | 258532 |  |  | 100 | 138 | na | 0.1 | 636 kcmil ACSR | Concrete H-frame | 75 | 0.1 | na | na | 25.101(c)(5)(B)
0PT37317 JM/JO | Wink Switch - Culberson Switch 138 kV Line : Cut In Castile Hills Sub | Culberson County | This cut in will be located in the Screwbean Tap - Black River line section. This work will support the establishment of the new Castile Hills substation. | 2018-11-15 | 2018-12-20 | 2018-12-20 | 1400000 | 1400000 |  |  | 100 | 138 | na | 0.33 | 1926.9 ACSS/TW/HS | Steel Poles | 50 | na | na | 0.33 | 25.101(c)(5)(A)
0PT04014 JM/JO | Wink Switch - Culberson Switch 138 kV Line: Cut In Horseshoe Springs Switch | Culberson County | This cut in will be located in the Screwbean Tap - Black River line section. This work will support the establishment of the new Horseshoe Springs Switch. | 2019-02-25 | 2019-03-22 | 2019-03-22 | 1700000 | 1950000 |  |  | 100 | 138 | na | 0.4 | 1926.9 ACSS/TW/HS | Steel Poles | 50 | na | na | 0.4 | 25.101(c)(5)(A)
0PT37714 JM/JO | Build Horseshoe Springs Switch – Horseshoe Draw STATCOM 138 kV Line | Culberson County | Build the Horseshoe Springs Switch – Horseshoe Draw STATCOM 138 kV Line. | 2019-03-13 | 2019-04-01 | 2019-04-01 | 340000 | 450000 |  |  | 100 | 138 | na | 0.13 | 1926.9 ACSS/TW/HS | Steel Poles | 50 | na | na | na | 25.101(c)(5)(A)
0PT37567 JM/JO | Wink Switch - Culberson Switch 138 kV Line : Anderson Ranch POI Switch Upgrades | Loving County | Upgrade the switches on H-frame switch structure 21/2 located in the Loving – Elmar line section from 2000 A to 3200 A. | 2018-09-19 | 2018-10-01 | 2018-10-01 | 300000 | 300000 |  |  | 100 | 138 | na | na | 1926.9 ACSS/TW/HS | Steel Poles | 90 | na | na | na | 25.101(c)(5)(A)
0PT37649 JC/AB | Denton Dr. Sw. Sta. - Lakemont Sta.138 kV Tie In | City of Dallas, Dallas County | Tie in the Lakemont 138 kV Line into the Denton Dr. Switch Station. | 2019-02-27 | 2019-04-30 | 2019-04-30 | 178411 | 178411 |  |  | 100 | 69 | 138 | 0.1 | 795 kcmil ACSR | na | na | na | na | na | 25.101(c)(5)(A)
0PT37650 JC/AB | Denton Dr. Sw. Sta. - Empire Central Sta.138 kV Tie In | City of Dallas, Dallas County | Tie in the Empire Central 138 kV Line into the Denton Dr. Switch Station. | 2018-10-01 | 2018-12-30 | 2018-12-30 | 178411 | 178411 |  |  | 100 | 69 | 138 | 0.1 | 795 kcmil ACSR | Steel Monopoles | na | na | na | na | 25.101(c)(5)(A)
17T65243 JC/RS | Norwood Sw Sta - Amelia St 138 kV Line: Rebuild Record Cross Cut In | Dallas County | Cut in the Record Crossing Station into the Norwood Sw Sta - Amelia St 138 kV Line on new steel monopoles. | 2019-01-04 | 2019-01-31 | 2019-01-31 | 1038520 | 1038520 |  |  | 100 | 138 | 138 | 0.8 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 0.8 | na | na | 25.101(c)(5)(B)
0PT37389 OER/JFO | DFW D West - DFW E East UG Fiber Installation | Tarrant County | Install 1.4 mile of UG fiber from DFW D West to DFW E East on the Liggett - Euless 138 kV Line. | 2018-11-15 | 2019-04-15 | 2019-04-15 | 565552 | 565552 |  |  | 100 | 0 | 0 | 1.4 | ADSS Fiber | UG | na | 1.1 | 30 | 0.31 | 25.101(c)(5)(B)
18T64063 RJ | Cathey Creek Sub (formerly Holland) Emergency Capacitors | City of Holland, Bell County | Rebuild a section of the Temple Sub - Holland Sub 69 Kv line to establish the new Cathey Creek capacitor bank | 2018-10-17 | 2018-12-21 | 2018-12-21 | 404283.98 | 450000 |  |  | 100 | 69 | na | 0.3 | 959.6 kcmil ACSS/TW | Steel and Concrete Poles | 50 | 0.3 | na | na | 25.101(c)(5)(B)
17T62061 KF/EH | Paris - Rivercrest/Tenaska 138 kV Line (Paris - Rivercrest Section): Rebuild | City of Paris, Lamar County | Rebuild a 6 mile section of the Paris-Rivercrest/Tenaska 138 kV Line from single-circuit to double-circuit. | 2019-01-01 | 2019-04-20 | 2019-04-20 | 6900000 | 7000000 |  |  | 100 | 138 | na | 6 | 959.6 kcmil ACSS/TW | Steel Monopoles | 100 | 6 | na | na | 25.101(c)(5)(B)
14T62120 JM/AB | Handley - Everman (Bowen W Tap) | City of Fort Worth, Tarrant County | Rebuild one span and improve the clearance on the Bowen West Tap Line 138 kV Line. | 2019-01-14 | 2019-01-31 | 2019-01-31 | 358776 | 425000 |  |  | 100 | 138 | na | 0.5 | Bundled 336.4 ACSR | Steel monopoles and concrete H-frame | 100 | 0.5 | na | na | 25.101(c)(5)(B)
15T63127 JM/AB | Big Spring W - Stanton East | City of Big Spring/ Howard, Martin and Midland Counties | Rebuild seven spans and improve the clearance on the Big Spring - Stanton 138 kV Line. | 2018-11-27 | 2018-12-19 | 2018-12-19 | 497000 | 675000 |  |  | 100 | 138 | na | 1 | 4/0 ACSR and 959.6 ACSS/TW | Steel monopoles and concrete H-frame | 100 | 1 | na | na | 25.101(c)(5)(B)
19T64005 SB | Round Rock - Round Rock South 138 kV Line: Round Rock Sw. Station Line Work | City of Round Rock, Williamson County | Reconfigure line work associated with Round Rock Switch Station. | 2019-03-18 | 2019-05-30 | 2019-06-10 | 350000 | 455000 |  |  | 100 | 138 | 138 | 0.02 | 959.6 kcmil ACSS/TW Bundled 795 ACSR Bundled 1590 KCMIL ACSR | Steel Pole | 400 | 0.08 | na | na | 25.101(c)(5)(B)
0PT04139 SB | Lonesome Draw 138 kV Tap | Upton County | Build approximately 0.9 miles of greenfield to establish Lonesome Draw 138 kV Substation. | 2019-02-01 | 2019-03-22 | 2019-03-22 | 1200000 | 2009502 |  |  | 100 | 138 | 138 | 0.9 | 959.6 kcmil ACSS/TW | Steel Poles | na | na | 100 | 0.9 | 25.101(c)(5)(A)
0PT04123 SB | Forney - Tri Corner Switch 345 kV Line - Double: Circuit Reconductor | City of Forney, City of Seagoville, Dallas County, Kaufman County | Upgrade Forney Station to Tri Corner Station, as well as the spans into Seagoville Station. | 2019-12-01 | 2020-12-31 |  | 232000 |  |  |  | 0 | 345 | 345 | 15 | 959.6 kcmil ACSS/TW | Steel Towers | 180 | 15 | na | na | 25.101(c)(5)(A)
0PT37763 KF/DN | Handley Switch - Liggett Sw 138 kV Line: Sub Angle Replacement | City of North Richland Hills, Tarrant County | Replace leg extension members and one stub angle on the Handley Switch - Liggett Switch 138 kV Line due to public-vehicle impact damage on Tuesday, 8/7/2018 at approximately 1:00am. | 2018-08-07 | 2018-10-08 | 2018-10-08 | 450000 | 350000 |  |  | 100 | 138 | na | na | 959.6 kcmil ACSS/TW | Steel Lattice Towers | 100 | na | na | na | 25.101(c)(3) | Emergency maintenance work
0PT37637 JM/DN | Wichita Falls - Pleasant Valley 138 kV Line: Raise Structure | City of Wichita Falls, Wichita County | Raise and move structure 7/3 on the Wichita Falls - Pleasant Valley 138 kV Line | 2019-01-03 | 2019-01-22 | 2019-01-22 | 182983.58 | 195000 |  |  | 100 | 69 | na | 0.1 | 795 ACSR | Steel Tower | na | 0.1 | na | na | 25.101(c)(5)(B)
0PT38246 AF/JO | Midessa South Sw. – Midland East 138 kV Line: Trail Junction Point-of-Delivery (POD) for Chevron USA | City of Midland, County of Midland | Establish a point of delivery to Chevron's substation on the southern circuit of the Midessa South Sw. - Midland East 138 kV transmission line. The point of delivery will be located approximately 6.4 miles northeast of the Midessa South Switch. | 2019-04-15 | 2019-05-14 | 2019-05-14 | 1018539 | 1100000 |  |  | 100 | 138 | na | 0.1 | ACSR 795 | Steel Monopole, | 70 | 0.1 | na | na | 25.101(c)(5)(A)
0PT04156 AF/BC | Hutto Sw. - Gilleland Creek Sw. 138 kV Line: Bird Nest Sub Line Work | City of Pflugerville, County of Travis | Modify Hutto Switch - Gilleland Creek 138 kV line to accommodate construction of the new Bird Nest Substation. | 2019-09-03 | 2019-11-23 |  | 883029 | 1200000 |  |  | 7 | 138 | na | 0.4 | 1926.9 ACSS/TW/HS | Steel, Monopole | 70 | 0.4 | na | na | 25.101(c)(5)(A) | This line work is to support the establishment of Bird Nest substation in Pflugerville, TX.
16T65165 0TP39960 KD/RS | Crown Road - Norwood Switching Station 138 kV Line Rebuild | City of Dallas, Dallas County | Upgrade the 9.1 mile Crown Road - Norwood Switching Station double-circuit line. Upgrade the 138 kV terminal equipment to meet or exceed 2000 A. | 2018-12-10 | 2020-06-30 |  | 12229402 | 16300813 |  |  | 45 | 138 | 138 | 18.2 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | Varies | 9.1 | Varies | na | 25.101(c)(5)(B)
16T65090 KD/JO 16T65186 | Northaven Switching Station - Preston Road North 138 kV Line Rebuild | City of Dallas, Dallas County | Upgrade the 6.1 mile Northaven Switching Station - Preston Road North double-circuit line. Upgrade the 138 kV terminal equipment to meet or exceed 2000 A. | 2019-01-21 | 2019-05-15 | 2019-05-15 | 11705282 | 13705282 |  |  | 100 | 138 | 138 | 12.2 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | Varies | 6.1 | Varies | na | 25.101(c)(5)(B) | The original project was Northaven-Renner (16T65090), and it was split so that we now have Northaven-Preston Road North (16T65186) and Preston Road North-Renner (16T65090). The WA that should now be associated with this project on the PUC Report is 16T65186.
0PT38376 SP/CL | McDonald Road Switch - Spraberry Switch 138 kV Line: Retermination | City of Big Springs & City of Garden City, Glasscock County | Convert the McDonald Road Switch - Spraberry Switch 69 kV Line to 138 kV and reterminate the line into McDonald Road Switch. | 2019-07-31 | 2019-09-30 | 2019-09-30 | 1808351.15 | 1440116 |  |  | 100 | 69 | 138 | 0.3 | 959.6 kcmil ACSS/TW | Steel Monopoles | 50 | 0.3 | na | na | 25.101(c)(5)(B)
0PT37659 SP/CL | Garden City Sub - Midkiff Switch 69 kV Line: Rebuild | City of Garden City, Glasscock County & Regan County | Rebuild the 16 mile existing 69 kV line to double-circuit 69 kV on one side and 138 kV on the other to connect the 138 kV Shipwreck Substation. | 2019-04-15 | 2019-08-31 | 2019-08-31 | 20611032.06 | 20064430 |  |  | 100 | 69 | 138 | 16 | 959.6 kcmil ACSS/TW | Steel Monopoles | 50 | 15 | na | na | 25.101(c)(5)(A) | This line work supports the establishment of Shipwreck Sub 138 kv in Big Springs, TX.
0PT38345 CZ | Leon - Ranger Gulf 69 kV line: Adjust Line for Cap Bank Installation | City of Ranger, Eastland County | Replacing existing H-frame with a 3-pole as a request of the new capacitor bank at Ranger Substation. | 2019-02-20 | 2019-03-07 | 2019-03-11 | 253993 | 250000 |  |  | 100 | 69 | na | 0.1 | 4/0 ACSR | Steel Poles | 275 | 0.1 | na | na | 25.101(c)(5)(B)
0PT04278 CZ | Anna Switch - McKinney Sub 138 kV line: Cut-In to Weston Sub | City of Mckinney, Collin County | Relocating Structure associated with establishing Weston Substation | 2020-03-15 | 2020-05-01 |  | 146533 |  |  |  | 0 | 138 | na | 0.1 | 1233.6 ACSS/TW | Steel Pole | 100 | 0.1 | na | na | 25.101(c)(5)(B)
0PT37271 BB | Big Spring Switch - Buzzard Draw Switch 69 kV Line: Knott Sub Line Work | Howard County | This cut in will be located in the Big Spring Sw - Buzzard Draw line section. This work will support the establishment of the new Knott substation. | 2019-02-18 | 2019-06-28 | 2019-06-30 | 550000 | 550000 |  |  | 100 | 69 | na | 0.4 | 4/0 ACSR and 959.6 ACSS/TW | Steel Monopole | 50 | 0.4 | na | na | 25.101(c)(5)(A)
0PT04280 BB | Grandview Tap 138 kV Line: Parks Bell Ranch Sub Line Work | Ector County | This cut in will be located in the Grandview Tap line section of the Moss Switch - Midland County Northwest 138 kV Line. This work will support the establishment of the new Parks Bell Ranch substation. | 2019-04-15 | 2019-05-15 | 2019-05-15 | 1400000 | 1400000 |  |  | 100 | 138 | na | 0.5 | 1926.9 ACSS/TW | Steel Monopole | 175 | 0.4 | na | na | 25.101(c)(5)(A)
0PT37439 BB | Waco West Switch - Lake Creek Switch 138 kV Line: Line work to connect the Du Puy Sub | Waco/McLennan County | This cut in will be located in the Waco West Sw. - Lake Creek Sw. section. This work will support the establishment of the new Du Puy substation. | 2019-10-15 | 2019-11-16 |  | 350000 | 450000 |  |  | 0 | 138 | na | 0.01 | 1926.9 ACSS/TW | Steel Poles | 100 | 0.1 | na | na | 25.101(c)(5)(A)
0PT37666 CL | Andrews County South - Littman 138 kV Line: Jumbo Hills Wind Interconnect | City of Andrews, Andrews County | Establish a generator interconnection by building a .4 mile looping in and out of Nelson Switch. | 2019-08-26 | 2019-11-22 |  | 1602400 | 1602400 |  |  | 20 | 138 | na | 70 | 959.6 kcmil ACSS/TW | Steel Poles | 200 | na | 0.4 | 0.4 | 25.101(c)(5)(A)
0PT37652 CL | Moss Switch - Odessa EHV 345 kV Line: Moss Switch Line Work | City of Odessa, Ector County | Reterminate the existing Odessa EHV line coming into Moss as well as establish a new terminal connection for the future Riverton line. This work is required to accommodate the installation of a second autotransformer. | 2019-02-16 | 2019-05-15 | 2019-05-15 | 2577400 | 3077644 |  |  | 100 | 345 | na | 0.25 | Bundled 1926.9 kcmil ACSS/TW | Steel Poles | 150 | 0.25 | na | na | 25.101(c)(5)(A)
0PT04048 BMcD/CL | Grapeland Magnolia 138 kV Tap | Houston County | Install a new 138 kV tap point for the existing Grapeland Magnolia 138 kV Substation on the Jewett Switch - Crockett Switch 138 kV Line. Install three line sectionalizing switches. | 2019-04-10 | 2019-05-14 | 2019-05-14 | 440000 | 760000 |  |  | 100 | 138 | na | 1.4 | 959.6 kcmil ACSS/TW | Steel Poles | 100 | 1.4 | na | na | 25.101(c)(5)(A)
16T62099 BMcD/IA | Structure 4/5 - North Main Switch (West) 138 kV Line | City of Fort Worth, Tarrant County | Rebuild the structure 4/5 - North Main Switch (West Ckt) section of the Saginaw - Denton Ave - North Main Switch 138 kV line. The project consists of rebuilding the West circuit of the 2.1 mile line from structure 4/5 - Heritage. The rebuilt line will support 959.6 kcmil ACSS/TW conductor on double-circuit steel monopole structures. | 2019-02-11 | 2019-11-30 |  | 3840000 | 3840000 |  |  | 42 | 69/138 | 138 | 2.1 | 959.6 kcmil ACSS/TW | Steel Poles | Varies | 2.1 | na | na | 25.101(c)(5)(B)
18T62003 BMcD/IA | Structure 4/5 - North Main Switch (East) 138 kV Line | City of Fort Worth, Tarrant County | Rebuild the structure 4/5 - North Main Switch (East Ckt) section of the North Main Switch - Richland Hills 138 kV line. The project consists of rebuilding the West circuit of the 2.1 mile line from structure 4/5 - North Main Switch. The rebuilt line will support 959.6 kcmil ACSS/TW conductor on double-circuit steel monopole structures. | 2019-02-11 | 2020-03-13 |  | 1040000 | 1040000 |  |  | 63 | 69/138 | 138 | 2.1 | 959.6 kcmil ACSS/TW | Steel Poles | Varies | 2.1 | na | na | 25.101(c)(5)(B)
0PT37349 SEI/MK | IH 635 Lake Hubbard-Centerville 345 kV Ferguson Relocation, Lake Hubbard-Centerville 345kV Line | City of Dallas, Dallas County | Relocation with new single-circuit, steel monopole dead end structure and remove existing single-circuit, steel monopole tangent structure. | 2019-01-14 | 2019-03-31 | 2019-03-31 | 415945 | 611482 |  |  | 100 | 345 | na | 0.22027 | 959 ACSS/TW "Suwannee" (Bundled) | Steel Monopole Structures | Varies | 0.22027 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
0PT37467 SEI/MK | IH 635 Lake Hubbard-Centerville 345kV LA Prada Relocation, Lake Hubbard-Centerville 345kV Line | City of Dallas, Dallas County | Relocation with new single-circuit, steel monopole dead end and tangent structures and remove existing single-circuit, steel monopole dead end and tangent structures. | 2019-01-14 | 2019-03-31 | 2019-03-31 | 1042688 | 1286451 |  |  | 100 | 345 | na | 0.46212 | 959 ACSS/TW "Suwannee" (Bundled) | Steel Monopole Structures | Varies | 0.46212 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
0PT37508 SEI/MK | IH 635 Lake Hubbard-Centerville 138 kV Relocation, Lake Hubbard-Centerville 138 kV Line | City of Dallas, Dallas County | Relocation with new single-circuit, steel monopole dead end and tangent structures and remove existing single-circuit, steel lattice tower dead end and tangent structures. | 2018-12-11 | 2019-05-21 | 2019-05-21 | 858655 | 1186735 |  |  | 100 | 138 | na | 1.1833 | 1926 ACSS/TW "Cumberland" (Non-Bundled) & 1431 ACSR "Plover" (Non-Bundled) | Steel Monopole Structures | Varies | 0.59167 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
0PT37509 SEI/MK | IH 635 Parkdale-Lake Hubbard 138 kV Relocation, Parkdale-Lake Hubbard 138 kV Line | City of Dallas, Dallas County | Relocation with new single-circuit, steel monopole dead end and tangent structures and remove existing single-circuit, steel lattice tower dead end and tangent structures. | 2019-01-14 | 2019-05-30 | 2019-05-30 | 853205 | 1267433 |  |  | 100 | 138 | na | 1.1951 | 1926 ACSS/TW "Cumberland" (Non-Bundled) & 1431 ACSR "Plover" (Non-Bundled) | Steel Monopole Structures | Varies | 0.59754 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
0PT37510 SEI/MK | IH 635 Royal Relocation, Hackberry/Northlake-Grapevine Ball St. 138 kV Line | City of Dallas, Dallas County | Relocation with new double-circuit, steel monopole dead end and tangent structures and remove existing double-circuit, steel monopole dead end and tangent structures. | 2019-11-28 | 2019-05-01 | 2019-05-01 | 1974592 | 1565355 |  |  | 100 | 138 | na | 0.55871 | 1926 ACSS/TW "Cumberland" (Non-Bundled) | Steel Monopole Structures | Varies | 0.55871 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
0PT37514 SEI/MK | SH 121 Collin County Outer Loop 138 kV Relocation, Payne-Royce 138 kV Line | City of Anna, Collin County | Relocation with new single-circuit, concrete H-frame tangent structures and remove existing single-circuit, wood H-frame tangent structures. | 2019-03-15 | 2019-04-04 | 2019-04-04 | 305413 | 252413 |  |  | 100 | 138 | na | 0.30436 | 795 ACSR "Drake" (Non-Bundled) | Concrete H-frame Structures | 70 | 0.30436 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
0PT37513 SEI/MK | SH 121 Collin County Outer Loop 345 kV Relocation, Anna Switch.-Valley Jct. 34 5kV Line | City of Anna, Collin County | Relocation with new double-circuit, steel monopole tangent structure and remove existing double-circuit, steel monopole tangent structure. | 2019-03-24 | 2019-04-01 | 2019-04-01 | 432295 | 379511 |  |  | 100 | 345 | na | 0.65152 | 1590 ACSR "Falcon" (Bundled) | Steel Monopole Structures | 110 | 0.32576 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
0PT37670 SEI/MK | SH 6 Deleon 69 kV Relocation, Leon-Dublin 69 kV Line | City of DeLeon, Comanche County | Relocation with new single-circuit, steel and wood dead end and tangent structures and remove existing single-circuit, wood dead end and tangent structures. | 2019-03-15 | 2019-06-24 | 2019-06-24 | 2273845 | 1537760 |  |  | 100 | 69 | na | 1.3841 | Number 2-3 Strand CU (Non-Bundled) & 336.4 ACSR "Linnet" (Non-Bundled) | Steel Monopole & Wood Structures | na | na | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation.
0PT04279 SEI/BC | Rental Car Substation Tap, Liggett-Hackberry 138 kV | City of Irving, Dallas County | Relocation with new double-circuit, steel dead end structures and remove existing double-circuit, steel dead end structures. Relocation will loop into and out of new Rental Car Substation. | 2019-04-08 | 2019-05-30 | 2019-06-05 | 1478015.77 | 1625063 |  |  | 100 | 138 | na | 0.38144 | 1033 ACSR "Curlew" (Bundled) & 959 ACSS/TW "Suwannee" (Bundled) | Steel Monopole | 100 | 0.19072 | na | na | 25.101(c)(5)(A)
0PT38446 SEI/BC | Rental Car Substation Relocation, Liggett-Saginaw 138 kV | City of Irving, Dallas County | Relocation with new double-circuit, steel dead end and small angles structures and remove existing double-circuit, steel dead end and tangent structures. | 2019-03-15 | 2019-05-01 | 2019-05-01 | 1449277.51 | 1687773 |  |  | 100 | 138 | na | 0.92083 | 1033 ACSR "Curlew" (Bundled) | Steel Monopole | 100 | 0.46042 | na | na | 25.101(c)(5)(B)
0PT04374 0PT38764 OER/DN | Wink - Notrees Sw 138 kV Line: Rebuild | City of Wink, Winkler County | Rebuild the 27.8-mile Wink Sw. Sta. - No Trees Sw. Sta. 138 kV Line using a conductor rated 2569 A or greater. Use double-circuit 138 kV structures with one circuit in place. Upgrade all line terminal and associated equipment to meet or exceed 2000 A. | 2/5/2019 7/15/2019 | 10/10/2019 12/13/2019 |  | 36645152 | 37500000 |  |  | 99 15 | 138 | na | 27.8 | 1926.9 ACSS/TW/HS | Steel Poles | 50 | 27.8 | na | na | 25.101(c)(5)(B)
17T64062 BC/IA | 138 kV Tap to Round Rock SE - Reconductor 3.4 mi | City of Pflugerville, Williamson County & Travis Counties | Upgrade the 138 kV Tap to Round Rock SE. The existing line is a double-circuit on steel and concrete monopoles that are to be reused. | 2019-01-02 | 2019-03-13 | 2019-03-13 | 3777758.47 | 3200000 |  |  | 100 | 138 | 138 | 6.8 | 1233.6 kcmil ACSS/TW | Steel & Concrete Poles | 70 | 3.4 | na | na | 25.101(c)(5)(B)
19T65004 SM/EDH | Tri Corner Switch - Watermill Switch 345 kV Line: Reconductor | Cities of Lancaster and Seagoville, Dallas County | Reconductor 11.5 miles from Tri Corner Switch – Watermill Switch 345 kV South circuit. | 2019-02-04 | 2020-02-15 |  | 10189806.17 | 10189806.17 |  |  | 40 | 345 | na | 11.5 | (2)959.6 kcmil ACSS/TW - Bundle Suwannee | Steel Towers | 165 | 11.5 | na | na | 25.101(c)(5)(B)
0PT38079 BB/KF | China Grove - Radium 138 kV Line: Sunoco POD | Colorado City, Mitchell County | Build a 0.6 mile line extension in the China Grove Switch - Raduim 138 kV Line to serve the Sunoco Pipeline facilities. | 2019-06-24 | 2019-08-12 | 2019-08-12 | 2600000 | 2600000 |  |  | 100 | 138 | na | 0.6 | 959.6 ACSS/TW | Steel Poles | na | na | 75 | 0.6 | 25.101(c)(5)(A)
0PT37645 DD/CL | Moss Switch - Wolf Switch 138 kV Line: Moss Switch Line Work | City of Odessa, Ector County | Reterminate the Moss Switch - Wolf Switch 138 kV line at Moss Switch Station to accommodate a second 345 kV autotransformer. | 2019-02-15 | 2019-03-20 | 2019-03-20 | 737385.56 | 1315454 |  |  | 100 | 138 | na | 0.1 | 959.6 kcmil ACSS/TW | Steel Poles | na | 0.1 | na | na | 25.101(c)(5)(A)
0PT04409 DD/JO | Pecos Trail POD (Edwards Ranch 138 kV Point of Delivery): Establish POD for Wisconsin Proppants | City of Monahans, Ward County | Re-route the Wolf Switch – Odessa EHV 138 kV line into the Pecos Trail POD. | 2019-02-25 | 2019-04-05 | 2019-04-05 | 1701827.97 | 1896053 |  |  | 100 | 138 | na | 0.2 | 1926.9 kcmil ACSS/TW | Steel and Concrete Poles | 75 | 0.1 | 75 | 0.1 | 25.101(c)(5)(A)
18T62138 MK/PO | General Motors - International Airport Sub 138 kV Line: Reconductor | City of Arlington, Tarrant County | Reconductor the west circuit of the General Motors - International Airport Substation 138 kV Line. | 2019-02-01 | 2019-04-26 | 2019-04-26 | 3112888.91 | 4486635 |  |  | 100 | 138 | 138 | 5.65 | 1926.9 kcmil ACSS/TW | Steel Poles | Varies | 5.65 | na | na | 25.101(c)(5)(B)
19T62002 MK/PO | Sherry Switch Station - General Motors Substation 138 kV: Reconductor | City of Arlington, Tarrant County | Reconductor the west circuit of the Sherry Switch Station - General Motors Substation 138 kV Line. | 2019-09-18 | 2019-11-27 |  | 2353682.32 | 3809556 |  |  | 17 | 138 | 138 | 2.35 | 1926.9 kcmil ACSS/TW | Steel Poles | Varies | 2.35 | na | na | 25.101(c)(5)(B)
0PT37243 MK/PO | Sherry Switch - International Switch 138 kV Line: Replace 3/8" Shield Wire with OPGW Brookhollow 138 kV Line Tap | City of Arlington, Tarrant County | The existing 3/8" EHS Steel Shield Wire will be replaced with 0.546" OD 48 count OPGW on the Brookhollow 138 kV Line Tap section of the Sherry Switch Station - International Airport Sub 138 kV Line. | 2019-04-15 | 2019-04-29 | 2019-04-29 | 156081.06 | 202113 |  |  | 100 | 138 | 138 | 0.3 | OPGW | na | Varies | 0.3 | na | na | 25.101(c)(5)(B)
0PT37248 DN/EH | Benbrook Junction - Rocky Creek Sw HT Upgrade | City of Benbrook, Tarrant County | Upgrade the 8 miles, Benbrook Junction to Rocky Creek portion of the Mitchell Bend - Rocky Creek 345 kV Line for High Temperature operation. | 2019-06-30 | 2020-02-26 |  | 13662232 | 13662232 |  |  | 10 | 345 | 345 | 8 | (2) 1590 kcmil ACSS | Steel Poles | 100 | 8 | na | na | 25.101(c)(5)(B)
0PT37557 SP/CL | Spraberry Switch - Garden City Sub 69 kV Line: Rebuild | City of Garden City, Glasscock County | Rebuild the 0.2 mile existing Spraberry Switch to Garden City Sub 69 kV Line in order to convert the 69 kV circuit to 138 kV and reterminate into McDonald Road Switch. | 2019-09-09 | 2019-09-24 |  | 799293 | 775165 |  |  | 100 | 69 | 138 | 0.2 | 959.6 kcmil ACSS/TW | Steel Monopoles | 50 | 0.2 | na | na | 25.101(c)(5)(A) | This line work supports the establishment of Shipwreck Sub 138 kV in Big Springs, TX and the retermination into McDonald Road Switch. Project to be energized 10/15/19.
0PT38124 - DM/OR | Sardis Sw (BEPC) - Sterrett Sw 138 kV Line : Raise Structures | Ellis County | Raise and replace structures 30/2 and 30/3 with wood H-Frames. | 2019-02-25 | 2019-03-02 | 2019-03-02 | 206497.66 | 272451 |  |  | 100 | 138 | 138 | 0.1 | 795 ACSS Drake | Wood H-Frame | na |  | 107 | na | 25.101(c)(5)(B)
0PT04149 OER | Texaco Mabee - Texaco Mabee Tap 138 kV Dckt Line: Cut-in Mariensfield | City of Andrews, Andrews County | Cut-in the Texaco Mabee - Texaco Mabee Tap 138 kV Line in order to establish the proposed Mariensfield Substation. | 2019-01-14 | 2019-02-11 | 2019-02-11 | 1000000 | 404789 |  |  | 100 | 138 | na | 0.3 | 959.6 ACSS/TW/HS Suwannee | Steel Poles | 50 | 0.25 | 75 | 0.5 | 25.101(c)(5)(A)
0PT37318 CL/MP | Venus Switch - Sardis Switch 138 kV Line: Establish New Kemp Ranch Switch Station | City of Venus, Ellis County | Reterminate the two circuits of the Venus Switch - Sardis Switch 138 kV Line to the newly constructed Kemp Ranch Switch Station. This line will no longer connect at Venus Switch Station. | 2019-06-10 | 2019-12-31 |  | 2340759 | 2340792 |  |  | 20 | 138 | na | 0.4 | (2)-959.6 kcmil ACSS/TW/E3X | Lattice Towers and Steel Poles | 100 | 0.1 | 100 | 0.4 | 25.101(c)(5)(A)
0PT38090 CL/MP | Kemp Ranch Switch - Genus #1 138 kV Line | City of Venus , Ellis County | Build a new line connecting the newly constructed Kemp Ranch Switch Station and the newly constructed Genus Substation. | 2019-06-10 | 2019-12-31 |  | 839798 | 839798 |  |  | 95 | 138 | na | 0.2 | 959.6 kcmil ACSS/TW/E3X | Steel Poles | na | na | 100 | 0.2 | 25.101(c)(5)(A)
0PT38091 CL/MP | Kemp Ranch Switch - Genus #2 138 kV Line | City of Venus, Ellis County | Build a new line connecting the newly constructed Kemp Ranch Switch Station and the newly constructed Genus Substation. | 2019-06-10 | 2019-12-31 |  | 754553 | 754553 |  |  | 95 | 138 | na | 0.3 | 959.6 kcmil ACSS/TW/E3X | Steel Poles | na | na | 100 | 0.3 | 25.101(c)(5)(A)
0PT38077 CL/MP | Venus Switch - Kemp Ranch Switch 138 kV Line: Establish Kemp Ranch Switch Station | City of Venus, Ellis County | Build a new line connecting the existing Venus Switch Station and the new constructed Kemp Ranch Switch Station. | 2019-06-10 | 2019-12-31 |  | 1643551 | 1643551 |  |  | 20 | 138 | na | 0.5 | (2)-959.6 kcmil ACSS/TW/E3X | Steel Poles | na | na | 75 | 0.5 | 25.101(c)(5)(A)
0PT38076 CL/MP | Alvarado - Venus - Kemp Ranch Switch Station 138 kV Line: Establish Kemp Ranch Switch Station | City of Venus, Ellis County | Build a new line connecting the existing Venus Switch Station and the new constructed Kemp Ranch Switch Station. | 2019-06-10 | 2019-12-31 |  | 1634409 | 1634409 |  |  | 20 | 138 | na | 0.4 | (2)-959.6 kcmil ACSS/TW/E3X | Steel Poles | na | na | 75 | 0.4 | 25.101(c)(5)(B)
0PT37241 MK/PO | Handley Switch – Liggett Switch 138 kV Line: Retermination at International Airport Substation | City of Euless, Tarrant County | Reterminate the existing double-circuit Handley - Liggett line and the circuits coming from Sherry Switch Station, into the International Airport Substation. | 2019-02-04 | 2019-03-24 | 2019-03-24 | 1630148.52 | 1624239 |  |  | 100 | 138 | 138 | 0.38 | 1926.9 kcmil ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(B) | Project is within International Airport Substation
0PT38703 GD | Yucca drive - Crane switch 69 kV Line | Odessa and Crane County | Replace a pole required to accommodate a new auto transformer at Barnsley Substation. | 2019-04-15 | 2019-09-27 | 2019-09-27 | 300000 | 300000 |  |  | 100 | 69 | 69 | 0.1 | 959.6 kcmil ACSS | Steel Pole | na | na |  | 0.1 | 25.101(c)(5)(A)
0PT38369 GD | Roanoke Switch - Euless Switch 138 kV Line | Forth Worth and Tarrant County | Install a single-circuit steel monopole on the Roanoke Switch - Euless Switch 138 kV double-circuit line. | 2019-10-16 | 2019-12-01 |  | 175852.21 | 180000 |  |  | 0 | 138 | 138 | 0.1 | 1033.5 ACSS | Steel Pole | na | na |  | 0.1 | 25.101(c)(5)(B)
0PT38572 GD | Graham Switch - Morgan Creek Switch 345 kV Line: 345 kV Lattice Hardening | Sweetwater City and Jones County | Harden a section of the Graham – Morgan Creek Switch 345 kV Line in Jones County. | 2019-12-31 | 2020-01-31 |  | 709609.37 |  |  |  | 0 | 345 | 345 | 0.2 | 1926.9 kcmil ACSS/TW | Lattice Steel Towers | 140 | 0.2 | 140 | 0.2 | 25.101(c)(5)(B)
0PT38584 GD | Graham Switch - Morgan Creek Switch 345 kV Line: 345 kV Lattice Hardening | Sweetwater City and Fisher County | Harden a section of the Graham – Morgan Creek 345 kV Line in Fisher County. | 2019-11-01 | 2020-01-31 |  | 733491.13 | 920000 |  |  | 0 | 345 | 345 | 0.2 | 1926.9 kcmil ACSS/TW | Lattice Steel Towers | 140 | 0.2 | 140 | 0.2 | 25.101(c)(5)(B)
18T62004 BMcD/IA | Structure 4/5 - Springdale (North) 138 kV Line | City of Fort Worth, Tarrant County | Rebuild the structure 4/5 - Springdale (North Ckt) section of the Saginaw - Springdale - Richland Hills 138 kV line. The project consists of rebuilding the North circuit of the 2.6 mile line from structure 4/5 - Springdale. | 2019-02-18 | 2019-06-30 | 2019-06-30 | 2335000 | 2335000 |  |  | 100 | 69/138 | 138 | 2.6 | 959.6 kcmil ACSS/TW | Steel Poles | Varies | 2.6 | na | na | 25.101(c)(5)(B)
18T62005 BMcD/IA | Structure 4/5 - Springdale (South) 138 kV Line | City of Fort Worth, Tarrant County | Rebuild the structure 4/5 - Springdale (South Ckt) section of the North Main Switch - Richland Hills 138 kV line. The project consists of rebuilding the South circuit of the 2.6 mile line from structure 4/5 - Springdale. | 2019-02-18 | 2019-06-30 | 2019-06-30 | 690000 | 690000 |  |  | 100 | 69/138 | 138 | 2.6 | 959.6 kcmil ACSS/TW | Steel Poles | Varies | 2.6 | na | na | 25.101(c)(5)(B)
0PT38583 0PT39653 CZ | Spraberry-Garden City East Sub 138 kV Line: Re-establish 69 kV Line South circuit and Cut-In to 138 kV line North Circuit | City of Midland/Midland County | Replacing (1) structure with a monopole, removing (3) structures, and a cut-In to the new station in support of establishing the new 138 kV Tex-Harvey Substation and the decommissioning of the existing 69 kV Tex-Harvey Substation | 4/1/2019 10/21/2019 | 4/15/2019 10/252019 | 2019-04-15 | 538549 | 538549 |  |  | 100 0 | 69/138 | na | 0.02 | 959.6 kcmil ACSS/TW | Steel Poles | 400 | 0.1 | na | na | 25.101(c)(5)(A) | South Circuit is 69 kV and North Circuit is 138 kV
18T63112 SEI/MK | AEP Lotebush-Coyanosa NW 138 kV Installation, Lotebush-Coyanosa NW 138kV Line | City of Coyanosa, Pecos County | Installation of new double-circuit, steel monopole dead end structures and concrete tangent structures. The installation is at the request of the Oncor. | 2019-07-22 | 2019-11-15 |  | 2902452 | 2500000 |  |  | 75 | na | 138 | 1.817 | 959 kcmil ACSS/TW "Suwannee" (Non-Bundled) | Steel and Concrete Monopole Structures | na | 0 | 80 | 0.90852 | 25.101(c)(5)(A)
0PT37574 CC | Norwood - E Levee 138 kV Line: Establish Knights Branch POD for UT Southwestern Medical Center | City of Dallas, Dallas County | Establish a point of delivery to Knights Branch sub on Norwood - E Levee 138 kV transmission line. The point of delivery will be located approximately 360 feet east of existing UTSWMC POD | 2019-04-01 | 2019-09-30 | 2019-09-30 | 1527554 | 1527554 |  |  | 100 | 138 | 138 | 0.5 | 1926 kcmil ACSS/TW | Steel Poles | 100 | 0.5 | na | na | 25.101(c)(5)(A)
0PT37679 DM/KF | Trinidad Switch - Long Lake 138 kV Line: Holly Ervin 138 kV POD | City of Palestine, Anderson County | Build a point of interconnection for Atmos Pipeline. | 2019-09-09 | 2019-10-04 | 2019-10-04 | 852139.22 | 1200661.92 |  |  | 100 | 138 | na | 0.6 | 795 kcmil ACSR/Drake | Steel H-Frame Switch/ H-Frame Tangents | 100 | na | na | na | 25.101(c)(5)(A)
16T62072 IA | Saginaw - North Main 138 kV Line: Cut in to new North Main Substation | City of Fort Worth, Tarrant County | Build a cut in to Oncor North Main Sub Station on the Saginaw - North Main 138 kV Line. The Interconnect will be between the existing heritage station and the new North Main Sub Station. | 2019-03-02 | 2020-02-14 |  | 697036.76 | 697037 |  |  | 56 | 138 | na | 0.1 | 959.6 kcmil ACSS/TW | Steel Poles | 50 | 0.1 | na | na | 25.101(c)(5)(A)
16T62077 IA | Connect North Main Sub To North Main Switch | City of Fort Worth, Tarrant County | Connect the North Main Substation to North Main Switch on the Randol Mill - North Main 138 kV Line. The initial line will be between the existing North Main Switch and the new North Main Sub Station. | 2019-03-02 | 2020-02-21 |  | 659044.01 | 1057827 |  |  | 62 | 138 | na | 0.3 | 959.6 kcmil ACSS/TW | Steel Poles | 50 | 0.3 | na | na | 25.101(c)(5)(A)
0PT37277 OER/DN | Temple - Minerva 69 kV Line: Relocation | City of Temple, Bell County | Relocate approximately 0.75 miles of the Teple - Minverva 69 kV Line in order to accommodate Waste Management's proposed landfill. | 2019-07-18 | 2019-12-31 |  | 931000 | 1141647 |  |  | 50 | 69 | na | 0.6 | 959.6 kcmil ACSS/TW | Steel/Concrete Poles | 100 | 0.75 | 100 | 0.6 | 25.101(c)(5)(D)
0PT37364 OER/EH | Liggett Sw - Norwood Sw 138 kV Line: Norwood Retermination | City of Dallas, Dallas County | Reterminate the Liggett - Norwood Sw (North Circuit) and install one (1) SCSP inline deadend between Str 7/2 and the proposed H-Frame station deadend on the North Circuit. | 2019-04-15 | 2019-12-31 |  | 351000 | 351000 |  |  | 15 | 138 | na | 0.1 | 959.6 kcmil ACSS/TW | Steel Poles | Varies | na | na | na | 25.101(c)(5)(B)
0PT38413 JM/JO | Battalion POD 138 kV Loop Line | City of Killeen, TX / Bell County | Construct a 138 kV loop line off the Killeen Park St. 138 kV Line to aide in establishing the Battalion POD. | 2019-06-03 | 2019-12-15 |  | 2500000 | 2700000 |  |  | 100 | na | 138 kV | 0.8 | 1-959.6 ACSS/TW/HS | Steel Poles | na | na | 70 | 0.8 | 25.101(c)(5)(A)
0PT38341 JM/JO | Killeen Park Street 138 kV Line: Modifications to Serve Battalion POD | City of Killeen, TX / Bell County | Add a second circuit to the existing Killeen Park St. 138 kV Tap Line to aide in establishing the Battalion POD. | 2019-06-03 | 2019-07-18 | 2019-07-18 | 1800000 | 1950000 |  |  | 100 | 138 | 138 kV | 1.2 | 1-959.6 ACSS/TW/HS | Steel Poles | 30 | 1.2 | 50 | na | 25.101(c)(5)(C)
0PT38070 AB/JM | Wink - Culberson 138 kV Line: Modify for Riverton - Sand Lake 345 kV Line | Reeves County | Modify the Wink - Culberson 138 kV transmission line due to the new construction of the Riverton – Sand Lake 345 kV line | 2019-10-21 | 2019-11-11 |  | 1300000 | 1600000 |  |  | 0 | 138 | na | 0.25 | 1926.9 ACSS/TW/HS | Steel Poles | 50 | na | 160 | 0.26 | 25.101(c)(5)(D)
0PT37287JM/IA | Valley Switch - Paris Switch 345 kV Line: Relocate for the Lower Bois d'Arc Creek Reservoir | Fannin County | Rebuild and raise the Valley – Paris 345 kV line at the request of the North Texas Municipal Water District in order to accommodate the proposed Lower Bois d’Arc Creek Reservoir. | 2019-07-15 | 2020-05-14 |  | 18300000 | 20500000 |  |  | 15 | 345 | na | 12.8 | (2) 1926.9 ACSS/TW/HS Bundled | Steel Poles | 150 | 6.4 | na | na | 25.101(c)(5)(E)
0PT37288 JM/IA | Valley Switch - Paris Switch 138 kV Line: Relocate for the Lower Bois d'Arc Creek Reservoir | Fannin County | Rebuild and raise the Valley – Paris 138 kV line at the request of the North Texas Municipal Water District in order to accommodate the proposed Lower Bois d’Arc Creek Reservoir. | 2019-07-15 | 2020-05-14 |  | 7200000 | 8750000 |  |  | 15 | 138 | na | 6.62 | 1926.9 ACSS/TW/HS | Steel Poles | 100 | 6.62 | na | na | 25.101(c)(5)(E)
0PT04089 JM/JO | Wink Switch - Culberson Switch 138 kV Line: Cut In Quarry Field Switch | Culberson County | This cut in will be located in the Elmar - Mason line section. This work will support the establishment of the new Quarry Field Switch. | 2019-09-04 | 2019-10-25 |  | 2650000 | 2900000 |  |  | 50 | 138 | na | 0.96 | 1926.9 ACSS/TW/HS | Steel Poles | 50 | na | 70 | 0.96 | 25.101(c)(5)(A)
0PT37680 JM/JO | Build Quarry Field Switch – Rondo STATCOM 138 kV Line | Culberson County | Build the Quarry Field Switch – Rondo STATCOM 138 kV Line. | 2019-08-29 | 2019-11-01 |  | 420000 | 500000 |  |  | 50 | 138 | na | 0.18 | 1926.9 ACSS/TW/HS | Steel Poles | 50 | na | 70 | 0.18 | 25.101(c)(5)(A)
0PT38473 JO/JM | Rebuild Screwbean Tap - Screwbean Sub 138 kV Line | Culberson County | Rebuild 0.2 miles of the Screwbean Tap - Scewbean Sub Line to accommodate the new transformer being installed in the Screwbean Sub, utilizing 1926.9 ACSS/TW "Cumberland". | 2019-11-04 | 2019-11-22 |  | 740000 | 900000 |  |  | 0 | 138 | na | 0.23 | 1926.9 ACSS/TW/HS | Steel Poles | na | na | 150/ 100 | 0.23 | 25.101(c)(5)(B)
0PT37752 JO/JM | Wink - Culberson 138 kV Line: Boulder POD for Anadarko Haley | Loving County | Install three motor operated 138 kV 3200 A line sectionalizing switches as a part of installing a 138 kV point-of-interconnection (POD) for Anadarko's Petroleum Corporation on the north circuit of the Wink – Culberson 138 kV Double-circuit Line. The POD will be located 1.4 miles west of the Loving Substation | 2019-10-21 | 2019-11-16 |  | 1700000 | 1850000 |  |  | 0 | 138 | na | 0.25 | 1926.9 ACSS/TW/HS | Steel Poles/ H-frame Switch | 50 | na | 70 | 0.25 | 25.101(c)(5)(A)
0PT37216 SF | Corsicana Switch - Trinidad Switch 138 kV Line : Trinidad Retermination | City of Trinidad Henderson County | Reterminate the Corsicana SW. - Trinidad SW. 138 kV Line at Trinidad in Henderson County | 2019-04-01 | 2019-05-24 | 2019-05-24 | 1500000 | 1500000 |  |  | 100 | 69 | 138 | 0.3 | 795 ACSR | Wood, Steel & Concrete Poles | 100 | 0.3 | na | na | 25.101(c)(5)(B)
0PT04154 SP/KF | Arco (DME) Switch - Collin Switch 138 kV Line: Establish Blagg Sub | City of Denton, Denton County | Cut-in approximately 0.7 miles of the Arco (DME) Switch - Collin Switch 138 kV line to establish Blagg Sub. | 2020-02-15 | 2020-02-22 |  | 2117860.39 |  |  |  | 0 | 138 | 138 | 0.2 | 1926.9 ACSS/TW | Steel Monopoles | 70 | 0.1 | na | na | 25.101(c)(5)(A)
0PT38108 JM/AB | Trinidad Switch Station - Kaufman Northwest 138 kV Line: Terminate into Mankin Switch | City of Trinidad, Henderson County | Terminate the Mankin Switch on the Trinidad Switch Station - Kaufman Northwest 138 kV Line to accommodate the Mankin Switch point of delivery | 2019-04-08 | 2019-05-14 | 2019-05-14 | 650000 | 800000 |  |  | 100 | 138 | 138 | 0.2 | 1926.9 ACSS/TW/HS | Steel Poles | 70 | 0.2 | 70 | 0.2 | 25.101(c)(5)(A)
0PT38669 SEI/MK | Relocate Martin Marietta, Chico-Jacksboro 69 kV Line | City of Chico, Wise County | Relocate structures 13/2 through 14/1 on Chico-Jacksboro 69 kV Line at the request of Martin Marietta. | 2019-08-05 | 2019-10-25 |  | 1686384.95 | 1546139 |  |  | 75 | 69 | na | 1.3 | 795 ACSR | Steel Monopole Structures | 100 | 1.078 | 100 | 1.3 | 25.101(c)(5)(D) | This project is 100% reimbursable by Martin Marietta. Relocation results in existing line being .2 miles longer in length.
0PT38670 SEI/MK | Relocate Martin Marietta, Bridgeport-Chico 138 kV Line | City of Chico, Wise County | Relocate structures 4/9 through 6/5 on Bridgeport - Chico 138 kV Line at the request of Martin Marietta. | 2019-08-23 | 2019-11-07 |  | 1686384.95 | 1546159 |  |  | 50 | 138 | na | 1.3 | 795 ACSR | Steel Monopole Structures | 100 | 1.078 | 100 | 1.3 | 25.101(c)(5)(D) | This project is 100% reimbursable by Martin Marietta. Relocation results in existing line being .2 miles longer in length.
18T64092 SM/BMcD | Jewett Switch - Crockett 138 kV Line: Rebuild Pleasant Springs to Grapeland Magnolia Tap | Crockett and Houston/Leon Counties | Rebuild the 14.0 mile section from Pleasant Springs to Grapeland Magnolia Tap of the Jewett - Crockett 138 kV Line using double-circuit monopole construction with only one circuit installed. | 2019-05-16 | 2019-12-31 |  | 13000000 | 17500000 |  |  | 40 | 138 | 138 | 14 | 959.6 kcmil ACSS/TW | Steel Poles | 100 | 14 | na | na | 25.101(c)(5)(B)
0PT38731CZ | Falcon Seaboard Switch-Midland East Sub 345 kV Line: Hardening 44/5 & 44/4 | City of Big Springs, Howard County | Rebuild a section from Falcon Seaboard Switch to Midland East Substation 345 kV Line by replacing two lattice H frames with two deadend towers. | 2020-03-15 | 2020-03-20 |  | 813755 |  |  |  | 0 | 345 | na | 0.2 | (2) 795 ACSR | Steel Towers | 150 | 0.2 | na | na | 25.101(c)(5)(B)
0PT38350 JL | Valley Switch - Payne Switch #3 138 kV Line: CMPC Line Hardening | Fannin County | Rebuild approximately 0.6 miles of the Valley Switch - Payne Switch #3 138 kV Line. | 2019-09-17 | 2019-11-15 |  | 720654 | 735488 |  |  | 25 | 138 | 138 | 0.6 | 959.6 ACSS/TW/HS | Steel Poles | 100 | 0.6 | na | na | 25.101(c)(5)(B)
0PT37464 JL | Valley Switch - Payne Switch #4 138 kV Line: CMPC Line Hardening | Fannin County | Rebuild approximately 0.6 miles of the Valley Switch - Payne Switch #4 138 kV Line. | 2019-10-16 | 2019-10-31 |  | 845310 | 863514 |  |  | 0 | 138 | 138 | 0.6 | 959.6 ACSS/TW/HS | Steel Poles | 100 | 0.6 | na | na | 25.101(c)(5)(B)
0PT37395 DM/JD | Rivercrest Switch - Sulphur Springs 138 kV Line : Monticello Sw. Tap (CMPC) | City of Mount Vernon, Franklin County | Relocate and replace structures 4/3 and 4/4 on the Rivercrest - Sulphur Springs 138 kV line: Monticello Sw. Tap. | 2019-08-12 | 2019-08-16 | 2019-08-16 | 394204.53 | 394204.53 |  |  | 100 | 138 | na | 0.3 | 959 ACSS | Wood H-Frame | 90 | na | na | na | 25.101(c)(5)(B)
17T64107 JM/AB | Mankin Switch Station - TRWD Station 138 kV Line | City of Trinidad, Henderson County | Build the Mankin Switch Station – Tarrant Regional Water District (TRWD) Station 138 kV line section to the TRWD point of delivery | 2019-04-15 | 2019-09-12 |  | 900000 | 1100000 |  |  | 100 | na | 138 | 0.6 | 959.6 ACSS/TW/HS | Steel Poles | na | na | 70 | 0.6 | 25.101(c)(5)(A)
0PT38605 AF/BC | Forest Grove Sw - Canton Sw 138 kv Ln: Rebd Forest Grove Sw - Eustace | City of Athens, Henderson County | Rebuild 4.47 miles of existing wood H-frame and 3-pole structures with new double-circuit capable steel monopoles utilizing | 2019-05-16 | 2019-12-01 |  | 4605058 | 6400000 |  |  | 40 | 138 | na | 4.5 | 1926.9 kcmil ACSS/TW | Steel Poles | 160 | 4.47 | na | na | 25.101(c)(5)(B)
19T63003 CH | Cowden North - Odessa North 69 kV Line: 138 kV Rebuild | City of Odessa, Ector County | Rebuild the 10.3-mile Cowden North – Odessa North Sw. Sta. 69 kV Line section using a conductor rated 1649 A or greater. | 2019-05-20 | 2019-09-16 | 2019-09-16 | 8891636 | 8891636 |  |  | 100 | 69 | 138 | 12.3 | 959.6 kcmil ACSS/TW | Steel Poles | 50 | 12.3 | na | na | 25.101(c)(5)(B)
0PT37331 RJ | Sweetwater no. 2 Sub - Colorado City Sub 69 kV Line: Rebuild | City of Loraine, Mitchell County | Replace four (4) single-circuit wood monopoles with four (4) single-circuit steel & concrete poles. | 2019-05-20 | 2019-05-27 | 2019-05-27 | 562307 | 562307 |  |  | 100 | 69 | na | 0.1 | 4/0 kcmil ACSR | Steel Poles | Varies | 0.1 | na | na | 25.101(c)(5)(B)
0PT38590 CW | Paint Creek Switch - China Grove Switch 138 kV Line: Relocation | City of Stamford, Jones County | Relocate the Paint Creek Switch - China Grove Switch 138 kV Line at the request of AEP, due to a new line being constructed under our existing infrastructure. Poles 83/5, 83/6, and 83/7 will be relocated and utilize a taller single-circuit H-frame structure. | 2019-04-15 | 2019-04-20 | 2019-04-20 | 222222 | 250000 |  |  | 100 | 138 | 138 | 0.3 | 636 MCM ACSR “Grosbeak” | Wood H-frames | 50 | 0.3 | na | na | 25.101(c)(5)(D)
0PT38389 CW | Fisher Road Switch - Oklaunion Tie 345 kV Line : Hardening 14/6 & 15/1 | City of Wichita Falls, Wichita County | Rebuild a section of the Fisher Road Switch - Oklaunion Tie 345 kV Line in Wichita County. Replace two (2) H-frame lattice structures (14/6 & 15/1) | 2019-10-21 | 2019-12-04 |  | 782557 | 968532 |  |  | 0 | 345 | 345 | 0.2 | 2 - 795 MCM ACSR “Drake" | Lattice Towers | 150 | 0.2 | na | na | 25.101(c)(5)(B)
0PT38654 CW | Fisher Road Switch - Oklaunion Tie 345 kV Line : Hardening 2/2 & 2/3 | City of Wichita Falls, Wichita County | Rebuild a section of the Fisher Road Switch - Oklaunion Tie 345 kV Line in Wichita County. Replace two (2) H-frame lattice structures (2/2 & 2/3) | 2019-10-21 | 2019-11-18 |  | 792887 | 945824 |  |  | 0 | 345 | 345 | 0.2 | 2 - 795 MCM ACSR “Drake" | Lattice Towers | 150 | 0.2 | na | na | 25.101(c)(5)(B)
0PT38698 CW | Fisher Road Switch - Oklaunion Tie 345 kV Line : Hardening 1/1 | City of Wichita Falls, Wichita County | Rebuild a section of the Fisher Road Switch - Oklaunion Tie 345 kV Line in Wichita County. Replace one (1) H-frame lattice structure (1/1) | 2019-10-21 | 2019-11-18 |  | 359954 | 509118 |  |  | 0 | 345 | 345 | 0.2 | 2 - 795 MCM ACSR “Drake" | Lattice Towers | 150 | 0.2 | na | na | 25.101(c)(5)(B)
0PT38726 CW | Forest Grove Switch - Canton Switch 138 kV Line : Rebuild Mabank Tap - Eustace SE Switch | City of Eustace, Henderson County | Rebuild the Mabank Tap - Eustace SE Switch section of the Forest Grove Switch – Canton Switch 138 kV Line to allow the integration of RCEC. | 2019-06-01 | 2019-11-29 |  | 7000000 | 9798629 |  |  | 75 | 138 | 138 | 6 | 1926.9 MCM ACSS/TW/HS “Cumberland” | Steel Pole, Steel 3 - Pole | 100 | 6 | na | na | 25.101(c)(5)(B)
0PT38720 CW | Elkton Switch - Palestine South Switch 138 kV Line : Blackburn Switch (Apollo) 138 kV POI | City of Cuney, Cherokee County | Establish a 138 kV point of interconnection for the Blackburn 138 kV Sw. Sta. located in the Elkton Sw. Sta. – Palestine South Sw. Sta. 138 kV Line. Install 4 monopoles to install the Blackburn 138 kV point of interconnection, which will accommodate the RCEC integration. | 2019-09-30 | 2019-11-22 |  | 953860 | 971502 |  |  | 50 | 138 | 138 | 0.4 | 2 - 795 MCM ACSR “Drake” and 959 MCM ACSS/TW "Suwannee" | Steel and Concrete Monopole | 100 | 0.4 | na | na | 25.101(c)(5)(A)
0PT38080 DM/JO | Enterprise Pipeline 138 kV POD: Construct two 138 kV lines from Quarry Field 138 kV Switch to Enterprise GC LLC | City of Mentone, Loving County | Install two 138 kV point-of-deliveries (PODs) for Enterprise GC LLC out of Quarry Field 138 kV Switch. Install two 3200 A, 138 kV circuit breakers at Quarry Field Switch. The PODs will be located approximately 1 mile east from Quarry Field Switch. | 2019-07-29 | 2019-11-19 |  | 2636926.73 | 2636927 |  |  | 15 | na | 138 | 1 | 959.6 kcmil ACSS/TW | Steel Poles | na | na | 70 | 1 | 25.101(c)(5)(A)
0PT38393 MR/CW | Falcon Seaboard Switch-Midland East Sub 345 kV Line: Hardening 55/2 | City of Stanton, Martin County | Replace structure 55/2 with a deadend structure to harden the line. | 2020-05-11 | 2020-05-29 |  | 488000 |  |  |  | 0 | 345 | 345 | 0.4 | 2 - 795 MCM ACSR “Drake" | Lattice Towers | 150 | 0.4 | na | na | 25.101(c)(5)(B)
0PT38728 CW/ AF | Palestine Switch - Palestine South Switch 138 kV Line: Reconductor | City of Palestine, Anderson County | Reconductor the 1.4-mile Palestine South Switch - Palestine 138 kV Line | 2019-09-16 | 2019-10-31 |  | 597383 | 722000 |  |  | 5 | 138 | na | 1.4 | 795 ACSR "Drake" | Steel monopoles | 70 | 1.4 | na | na | 25.101(c)(5)(B)
0PT38872 AF/KF | Minerva Sub - Robertson Switch 138 kV Line : Structure Relocation | City of Milano, Milam County | This is a CMPC project to relocate structure 32/2 due to erosion by the Little River on the Minerva Sub - Robertson Switch 138kV line. | 2019-10-18 | 2019-10-31 |  | 665094 | 222000 |  |  | 0 | 138 | na | 0.4 | 795 ACSR "Drake" | Steel monopoles | 70 | 0.4 | na | na | 25.101(c)(5)(B)
0PT38582 AF/CW | Falcon Seaboard Switch - Midland East Sub 345 kV Line : Hardening 63/1 & 63/2 | City of Midland, County of Midland | Rebuild a section of the Falcon Seaboard Switch - Midland East Sub 345 kV Line in Midland County. Replace two (2) H-frame lattice structures (63/1 & 63/2) adjacent to I-20 with deadend towers. | 2020-03-01 | 2020-06-30 |  | 800172 |  |  |  | 0 | 345 | na | 0.2 | 2 - ACSR 795 "Drake" | Lattice Steel Towers | 150 | 0.2 | na | na | 25.101(c)(5)(B)
0PT38587 AF/CW | Falcon Seaboard Switch - Midland East Sub 345 kV Line: Hardening 35/4 & 35/5 | City of Big Spring, County of Howard | Rebuild a section of the Falcon Seaboard Switch - Midland East Sub 345 kV Line in Howard County. | 2020-03-15 | 2020-03-20 |  | 776453 |  |  |  | 0 | 345 | na | 0.2 | 2 - 795 ACSR "Drake" | Lattice Steel Towers | 150 | 0.2 | na | na | 25.101(c)(5)(B)
0PT04019 PO/BC | Village Creek Tap - Bowen 138 kV Line: Rebuild | City of Arlington, Tarrant County | Rebuild the Village Creek Tap – Bowen 138 kV Line as a double-circuit line. | 2019-07-09 | 2019-09-13 | 2019-09-13 | 5111631.35 | 5111631 |  |  | 100 | 138 | 138 | 2.4 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 1.2 | na | na | 25.101(c)(5)(B)
0PT38496 PO/BC | Bowen East 138 kV Tap Line: Conductor Removal | City of Arlington, Tarrant County | Remove the Bowen East 138 kV Tap Line. | 2020-05-15 | 2020-06-30 |  | 224817.55 | 224818 |  |  | 0 | 138 | na | 1.7 | na | na | na | na | na | na | 25.101(c)(5)(B)
18T62093 0PT39362 JM/EH | Lake Wichita SW. STA. - Holliday 69 kV Line Conversion to 138 kV | Archer County | Convert the 10.8-mile Lake Wichita Sw. Sta. – Holliday 69 kV Line to 138 kV and terminate at Bowman. Move and raise tower 3/6 to provide necessary horizontal and vertical clearance for the upgraded Lake Wichita to Holliday 138 kV line. | 2019-07-22 | 2019-12-31 |  | 17106248 | 17950000 |  |  | 10 | 69 | 138 | 10.1 | 959.6 ACSS/TW/HS | Steel monopoles | 50 | 10.1 | na | na | 25.101(c)(5)(B)
0PT39015 JM/EH | Holliday Sub - Archer City Sub 69 kV Line : Reterminate at Holliday | Archer County | Reterminate line at Holliday Sub in association with Holliday Station expansion to allow room for new 138 kV yard. | 2019-06-20 | 2019-07-15 | 2019-07-15 | 541775 | 585000 |  |  | 100 | 69 | na | 0.1 | 336 ACSR | Wood and steel poles | 50 | 0.1 | na | na | 25.101(c)(5)(E)
0PT04050 SM/BMcD | Pleasant Springs 138 kV POI | Leon County | Install a new 138 kV point of interconnection for Houston County Electric (HCEC) to their existing Pleasant Springs 138 kV Substation on the Jewett Switch - Crockett Switch 138 kV Line. | 2019-08-19 | 2019-11-15 |  | 200000 | 315000 |  |  | 10 | 138 | na | 0.1 | 795 kcmil ACSR | Steel Poles | 100 | 0.1 | na | na | 25.101(c)(5)(A)
0PT38456 17T65128 0PT38387 OER/LH/AS | TI-Schroeder 138 kV UG Line: Increase double-circuit Section Ampacity | City of Dallas, Dallas County | Rebuild to increase the ampacity of the 0.5 mile double-circuit TI - Schroeder 138 kV UG Line section. | 2019-07-22 | 2020-06-01 |  | 29613898 | 30000000 |  |  | 25 | 138 | 138 | 0.5 | 3-3500 kcmil Cu HPFF, 2-6000 kcmil Cu XLPE | Underground Transmission Line | 100 | 0.45 | na | na | 25.101(c)(5)(B)
0PT38808 JL/SP/EH | Sandow Switch - Temple Switch 138 kV Line: Storm Restoration | City of Buckholts, Milam County | Rebuild approximately 0.2 miles of the Sandow Switch - Temple Switch 138 kV Line due to Storm Damage. | 2018-12-09 | 2019-10-15 |  | 298835.06 | 1882456.31 |  |  | 0 | 138 | na | 0.2 | 2-1926.9 kcmil ACSS/TW | Steel Poles | 50 | 0.2 | na | na | 25.101(c)(3) | Emergency Storm Restoration
0PT38959 CZ/OR | Yucca Drive Sw-Culberson Sw 138 kV Line: Cut-In to Barstow Northwest Sub | City of Pecos, Ward County | Reconfigure line to accommodate the expansion of Barstow Northwest Substation by utilizing one new deadend monopoles | 2019-10-16 | 2019-11-22 |  | 295580 | 330000 |  |  | 0 | 138 | na | 0.04 | 1926.9 Cumberland | Steel Poles | 80 | 0.1 | na | na | 25.101(c)(5)(A)
0PT37683 TC/BC | Lake Creek Switch - Tradinghouse Switch (East Ckt) 345 kV Line: Lake Hall Sw. Line Work | City of Hallsburg, McLennan County | Cut in the Lake Hall Switch (Prairie Hill Wind Interconnect) into the Lake Creek Sw. - Tradinghouse Sw. (East) 345 kV Line. | 2019-03-01 | 2020-04-30 |  | 849108 | 1008746 |  |  | 0 | 345 | na | 0.1 | 959.6 kcmil ACSS/TW/HS | Lattice Steel Towers | 170 | 0.1 | na | na | 25.101(c)(5)(A)
0PT04399 DD | Thorntonville Sub: Line work associated with establishing Thorntonville Sub | City of Monahans, Ward County | Relocate and install structures to cut in the Permian Basin - Crane 69 kV Line to establish the new Thorntonville Sub. | 2019-07-15 | 2019-10-05 |  | 913304 | 1421935.69 |  |  | 100 | 69 | 69 | 0.5 | 959.6 MCM ACSS/TW/HS “Suwannee” | Steel poles | 50 | na | 50 | na | 25.101(c)(5)(A)
0PT39236 DN | Navy Lake POD 69kV Line | Archer County | This project is to construct the tap from the Cotton Wood Rd Switch - Navy Kickpaoo Switch 69kV line to Navy Kickapoo Switch - Navy Kickapoo 69 kV line to serve Texas Express Pipe Line at Navy Kickapoo POD. | 2019-07-15 | 2019-07-31 | 2019-07-31 | 1000000 | 850000 |  |  | 100 | 69 | 69 | 0.1 | 4/0 kcmil ACSR | Woods or Concrete Poles | Varies | na | Varies | 0.1 | 25.101(c)(5)(A)
0PT38586 | Buzzard Draw Switch - Gunsight Switch 138 kV Line: Howden (Surge Operating) POD | City of Big Spring, Howard County | Install a new 138 kV point of delivery for Surge Energy's new 138 kV substation on the Buzzard Draw Switch - Gunsight Switch 138 kV Line. | 2019-10-18 | 2019-11-22 |  | 974000 | 974000 |  |  | 0 | 138 | na | 0.1 | 336 MCM ACSR | Steel/ Wood Poles | 75 | na | na | na | 25.101(c)(5)(A)
0PT38532 JM/SB | Yucca Switch - Moss Switch 138 kV Line: Shin Oak POD for Blackbeard Operating, LLC | Winkler County | Install a new 138 kV point of delivery (POD) for Blackbeard Operating, LLC on the Yucca Switch - Moss Switch 138 kV Line | 2019-08-26 | 2019-10-30 |  | 1200000 | 1200000 |  |  | 85 | 138 | 138 | 0.4 | 795 ACSR | Steel Poles | 75 | 0.2 | 75 | 0.2 | 25.101(c)(5)(A)
18T62143 KF/BMcD | Hackberry - Grapevine Ball St 138 kV Line: Cut-In at Vineyard Switch | City of Grapevine, Tarrant County | Separate and terminate the Northlake - Grapevine Ball Street 138 kV Line to establish the new Vineyard Switch. | 2019-11-11 | 2019-12-14 |  | 918748 | 1905000 |  |  | 0 | 138 | 138 | 0.33 | 1926.9 ACSS/TW | Steel Poles | Varies | 0.33 | Varies | na | 25.101(c)(5)(B)
18T62144 KF/BMcD | Southlake - Euless 138 kV Line: Cut-In at Vineyard Switch | City of Grapevine, Tarrant County | Separate and terminate the Roanoke Switch - Euless 138 kV Line to establish the new Vineyard Switch. | 2019-10-16 | 2019-12-18 |  | 1510549 | 2713000 |  |  | 0 | 138 | 138 | 0.85 | 1926.9 ACSS/TW | Steel Poles | Varies | 0.85 | Varies | na | 25.101(c)(5)(B)
0PT04098 KF/BMcD | Roanoke to Coppell (BEC) 138 kV Line: Cut-In at Vineyard Switch (West) | City of Grapevine, Tarrant County | Separate and terminate the Roanoke - Coppell (BEC) 138 kV Line to establish the new Vineyard Switch. | 2019-12-11 | 2020-03-17 |  | 400262 | 907000 |  |  | 0 | 138 | 138 | 0.13 | 1926.9 ACSS/TW | Steel Poles | Varies | 0.13 | Varies | na | 25.101(c)(5)(B)
0PT39498 CL/BMcD | Andrews Co South Switch - Littman Sub 138 kV Line : Lower 1/3 to 1/5 | City of Andrews, Andrews County | Lower structures 1/3 to 1/5 to accomodate the new Clearfork - Doghouse 345 kV Line. | 2019-10-16 | 2019-10-24 |  | 495649.35 | 535000 |  |  | 0 | 138 | 138 | 0.45 | 1926.9 ACSS/TW | Concrete Poles | 80 | 0.45 | 80 | na | 25.101(c)(5)(B)
0PT37564 JC/OR | Horseshoe Springs Sw - Owl Hills 138 kV Line: Cut-in to Est Alligator Draw | Orla City Reeves County | Cut in the new Alligator Draw Station utilizing the new structures on the Horseshoe Springs - Chimney Wells POD 138 kv Line. | 2019-08-30 | 2019-11-15 |  | 1600000 | 1373310 |  |  | 10 | na | 138 | 18.7 | 1926.9 kcmil ACSS/TW | Steel Poles | na | na | 70 | 0.3 | 25.101(c)(5)(A) | Greenfield Project
18T64117 TT/KF | Tyler - Tyler West 69kV to 138kV Rebuild | Tyler, Smith County | Rebuild the Tyler- Tyler West 69kV Line to 138kV designed to operate at 90C and 897 Amps. | 2019-05-02 | 2019-08-31 | 2019-08-31 | 2924331.77 | 3750952 |  |  | 100 | 69 | 138 | 1.9 | 795 kcmil 26/7 ACSR "Drake" | Steel Monopoles | Varies | na | Varies | na | 25.101(c)(5)(B)
0PT38852 OER/DN | Wink Switch - Notrees Switch 138 kV Line : Railside POD (Exxon) | City of Wink, Winkler County | This project is to provide two point of deliveries for Exxon Mobil Pipeline Company on the Wink - Notrees 138 kV Line. | 2019-10-28 | 2019-11-16 |  | 700000 | 700000 |  |  | 0 | na | 138 | 0.1 | 1926.9 kcmil ACSS/TW/HS | Steel Poles | na | na | 100 | 0.1 | 25.101(c)(5)(A)
0PT37221 OER | Means - Fullerton Switch 138 kV Line: Cut-In to Establish Blackbird Switch | City of Andrews, Andrews County | This project is to provide a point of interconnection for the customer's generator (Lapetus Energy Project, LLC) at Blackbird Sw | 2019-09-30 | 2019-11-08 |  | 1317334 | 1317334 |  |  | 5 | na | 138 | 0.48 | 959.6 ACSS/TW/HS | Steel Poles | na | na | 160 | 0.48 | 25.101(c)(5)(A)
0PT38849 MR/OR | Decatur Sub - Bowie Sub 69 kV Line: Bennett Road Switch Retermination | City of Decatur, Wise County | Install one deadend structure to reterminate the Decatur - Bowie 69 kV Line into Bennett Road Switch | 2019-10-18 | 2019-12-01 |  | 270280 | 317827 |  |  | 0 | 69 | 69 | 0.03 | 959 MCM ACSS/TW "Suwannee" | Steel Poles | 50 | 0.11 | na | na | 25.101(c)(5)(A) | Work being done on Oncor Substation Property
0PT39007 MR/OR | Decatur Sub - Oran Sub 69 kV Line: Bennett Road Switch Retermination | City of Decatur, Wise County | Install one deadend structure to reterminate the Decatur - West Chico - Oran 69 kV Line into Bennett Road Switch | 2019-10-16 | 2019-12-01 |  | 235794 | 265931 |  |  | 0 | 69 | 69 | 0.03 | 959 MCM ACSS/TW "Suwannee" | Steel Poles | 50 | 0.11 | na | na | 25.101(c)(5)(A) | Work being done on Oncor Substation Property
0PT38088 MR/EH | Wolf Switch - Moss Switch 138 kV Line: Establish Red Lakes Switch for Oberon Solar Interconnect | Ector County | Install four steel monopole structures to loop into new Red Lakes Switch for Oberon Solar Interconnect. | 2019-10-16 | 2019-11-15 |  | 1065942 | 1200000 |  |  | 0 | 138 | 138 | 0.15 | 1926.9 MCM ACSS/TW "Cumberland" | Steel Poles | Centerline | 0.11 | 150 | 0.04 | 25.101(c)(5)(A)
0PT38352 MR/BC | Graham Switch - Tonkawa Switch 345 kV Line: CMPC Hardening 133/3 &133/4 | Scurry County | Replace structures 133/3 & 133/4 with deadend structures to harden the line. | 2019-09-10 | 2019-11-01 |  | 795443 | 380000 |  |  | 34 | 345 | 345 | 0.2 | 2 - 795 MCM ACSR “Drake | Lattice Towers | 190 | 0.2 | na | na | 25.101(c)(5)(B)
0PT38380 TT/KF | Tyler West Sub - Tyler Switch 138kv Line: Upgrade | Tyler, Smith County | The Tyler West - Tyler Swith 138 kV line will be upgraded and hardened to prepare the idle line to be energized. | 2019-09-18 | 2019-11-30 |  | 1243914 | 2139599 |  |  | 5 | 138 | 138 | 5.3 | 795 kcmil 26/7 ACSR "Drake" | Steel Towers, Wood H-Frames, Concrete H-Frames, and Steel Monopoles | varies | na | varies | na | 25.101(c)(5)(B)
0PT38081 SB | No Trees Switch - Andrews County South Switch 138 kV Line: Rebuild | City of Wink, Winkler County | Rebuild the 8.8 miles of single-circuit wood h-frames. The final build will utilize double-circuit steel monopoles. | 2020-01-20 | 2020-02-29 |  | 17005546.49 |  |  |  | 0 | 138 | 138 | 8.8 | 1926 kcmil ACSS/TW | Steel and Concrete Poles | 50-125 | 8.8 | na | na | 25.101(c)(5)(B)
0PT04123 SB | Forney - Tri Corner Switch 345 kV Line - Double: Retermination | City of Forney, City of Seagoville, Dallas County, Kaufman County | Reterminate the Forney - Tri Corner 345 kV Line into Tri Corner station. | 2019-12-01 | 2020-06-30 |  | 232000 |  |  |  | 0 | 345 | 345 | 15 | 959.6 kcmil ACSS/TW | Steel Towers | 180 | 15 | na | na | 25.101(c)(5)(A)
0PT04329 SEI/CW | Installation for Canyon Wind POI, Scurry County South Switch-Canyon Wind 138 kV Line | City of Dunn, Scurry County | Installation with new single-circuit, steel monopole dead end structures. The installation is at the request of the Canyon Wind. | 2020-01-01 | 2020-12-31 |  | 1412751.89 |  |  |  | 0 | na | 138 | 0.28049 | 959 ACSS/TW "Suwannee" | Steel Monopole Structures | na | na | na | na | 25.101(c)(5)(A) | Structure installation is at the request of Canyon Wind.
0PT39809 SEI/BC | 2019 CMPC Odessa District, Paint Creek-China Grove 138 kV Line | City of Snyder, Scurry County | Modify highway crossing to improve the system reliability. | 2019-09-20 | 2019-10-31 |  | 606394.78 | 250400 |  |  | 66 | 138 | na | 0.27633 | 636 ACSR "Grosbeak" | Concrete H-frame Structures | 100 | 0.27633 | 100 | na | 25.101(c)(5)(B)
0PT39804 CW/SB | Yucca - Holt 138 kV Line: Raise Structure 10/1 | Winkler County | Raise structure 10/1 to aide in establishing the Shin Oak POD for Blackbeard Operating, LLC. | 2019-09-23 | 2019-09-28 | 2019-09-28 | 173157 | 175000 |  |  | 100 | 138 | 138 | 0.01 | 795 ACSR | Steel Poles | 75 | 0.1 | na | na | 25.101(c)(5)(B)
0PT39953 BB/DN | Athens Sub - Jacksonville Switch 69 kV Line: Reterm Jacksonville Switch | City of Jacksonville, Cherokee County | Determinate and reconfigure Athens Sub - Jacksonville Switch 69 kV transmission line into the rebuilt Jacksonville Switch Station. | 2019-09-16 | 2019-11-18 |  | 450000 | 450000 |  |  | 5 | 69 | na | 0.1 | 795 kmcill ACSR | Steel or Concrete Poles | 50 | varies | na | na | 25.101(c)(5)(A) | Work is being done on ONCOR property
0PT39956 BB/DN | Jacksonville Plant Sub - Jacksonville Switch 69 kV Line: Reterm | City of Jacksonville, Cherokee County | Reterminate the Jacksonville Plant - Jacksonville Tap - Jacksonville Switch 69 kV Line for the rebuild of the Jacksonville Switch Station. | 2019-09-16 | 2019-11-18 |  | 240000 | 240000 |  |  | 5 | 69 | na | 0.1 | 795 kmcill ACSR | Steel or Concrete Poles | 50 | na | na | na | 25.101(c)(5)(A) | Work is being done on ONCOR property
0PT39963 BB/DN | Jacksonville Plant South-Jacksonville Sw 69 kV Line: Reterm Jacksonville Switch | City of Jacksonville, Cherokee County | Reterminate the Jacksonville Plant - Beaumont Street Tap- Jacksonville Switch 69 kV Line for the rebuild of the Jacksonville Switch Station. | 2019-09-16 | 2019-11-18 |  | 138748 | 138748 |  |  | 5 | 69 | na | 0.1 | 795 kmcill ACSR | Steel or Concrete Poles | 50 | 0.2 | na | na | 25.101(c)(5)(A) | Work is being done on ONCOR property
17T65086 BB/KF | Collin Sw - Payne Sw 138 kV Line: (Redbud) Prolina POI Reroute | City of Prosper, Grayson County | Build a Point of Interconnect to Brazos Electric's 'Redbud Substation' on the Collin Switch - Stone Creek Switch 138 kV Line. | 2019-09-23 | 2019-10-31 |  | 905000 | 905000 |  |  | 34 | 138 | na | 0.2 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | 100 | 0.2 | na | na | 25.101(c)(5)(A)
0PT38421 BB/DN | Central Bluff Sw. - Holstein Solar I Sw. 345 kV Line: Construct transmission line for connection Holstein Solar | City of Sweetwater, Nolan County | Install a 345 kV point-of-interconnection (POI) for customer's generator ( Holstein Solar I) at Central Bluff Switch. | 2019-09-23 | 2019-10-31 |  | 580000 | 650000 |  |  | 1 | 345 | na | 0.2 | 795 kcmil ASCR | Steel or Concrete Poles | 150 | 0.1 | na | na | 25.101(c)(5)(A) | Work is being done on ONCOR property
0PT37440 BB/DN | Jacksonville Switch- Troup 69 kV Line: Reterminate and Reconfigure for Jacksonville Switch Rebuild | City of Jacksonville, Cherokee County | Utilize the existing Jacksonville Sw. Sta. – Structure 50/9 69 kV double-circuit line section to operate the Jacksonville Sw. Sta. – Athens 69 kV Line and Jacksonville Sw. Sta. – Troup 69 kV Line as a continuous circuit. Disconnect the Jacksonville Tap – Structure 50/9 69 kV line section and establish a Jacksonville Sw. Sta. – Carey Lake Tap – Jacksonville SES 69 kV Line. Reterminate the transmission line into the rebuilt Jacksonville Switch Station. Upgrade all line terminal and associated equipment to meet or exceed 2000 A. | 2019-10-21 | 2019-11-30 |  | 405000 | 425000 |  |  | 0 | 69 | na | 0.2 | 795 kcmil ASCR | Steel or Concrete Poles | 50 | 0.2 | na | na | 25.101(c)(5)(A) | Work is being done on ONCOR property
0PT38450 AB | Kirkland Park Sub - Ti Sub 138 kV Line: Replace 3/8 Ehs Shield Wire | City of Dallas, Dallas County | Replace the 3/8" EHS shield wire with OPGW on the Kirkland Park - Schroeder Road section of the Kirkland Park Sub - TI Sub 138 kV Line. | 2020-04-22 | 2020-05-15 |  | 514856.41 |  |  |  | 0 | 138 | na | 2.1 | OPGW | Steel Monopoles | 100 | 2.1 | na | na | 25.101(c)(5)(A)
0PT39714 JO/KD | Northaven Switch-Renner Switch 138 kV: Rebuild Alpha Rd. - Knoll Trl. | City of Dallas, Dallas County | Rebuild the 2.25 mile Alpha Road-Knoll Trail 138 kV double-circuit line using a conductor rated for 2569A or greater. | 2019-11-01 | 2020-01-31 |  | 6606401.32 | 6850000 |  |  | 0 | 138 | 138 | 4.5 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 2.25 | na | na | 25.101(c)(5)(B) | The original project was Northaven-Renner (16T65090), and it was split so that we now have Northaven-Alpha Road & Knoll Trail-Preston Road North (16T65186), Preston Road North-Renner (16T65090), and Alpha Road-Knoll Trail (0PT39714). The WA that should now be associated with this project on the PUC Report is 0PT39714.
0PT39736 CB/DN | Cedar Hill Switch - Camp Wisdom 138 kV Line: Replace Str T-1005 | City of Dallas, Dallas County | Repair structure T-1005 on the Camp Wisdom Road – Cedar Hill Switch 138 kV line. The damaged structure will be repaired using a field welded steel support sleeve. | 2019-07-30 | 2019-07-31 | 2019-07-31 | 87945 | 34664 |  |  | 100 | 138 | 138 | 0.1 | 972 kcmil ACAR | Steel Pole | na | na | na | na | 25.101(c)(5)(B) | Original project was to replace structure T-1005. Updated scope is to repair the structure using a field welded steel support sleeve.
0PT40097 SP/EH | NTUSU Tule Caynon Switch - Alibates Switch 345 kV Line: Storm Restoration | City of Lubbock | Replace broken OPGW damaged by lightning strikes | 2018-06-18 | 2018-06-20 | 2018-06-20 | 250476 | 250476 |  |  | 100 | 345 | na | 0.2 | 1926.9 kcmil ACSS/TW | Steel Towers | 175 | 0.22 | na | na | 25.101(c)(3) | Emergency Restoration
0PT37559 OER/JFO | Polk St Terminal - Polk St 138 kV Line : Terminations Replacement | City of Dallas, Dallas County | Replace existing terminations at Polk St Sub and Polk Terminal. | 2019-10-16 | 2019-11-02 |  | 690000 | 690000 |  |  | 0 | 138 | na | na | 600 kcmil Cu Phelps Dodge Cable | Underground Transmission Line | na | na | na | na | 25.101(c)(5)(B)
0PT38283 OER/JFO | Edgemere Sub - Bandera Sub 138 kV Line : Terminations Replacement | City of Dallas, Dallas County | Replace existing terminations at Edgermere Terminal and Bandera Sub. | 2019-10-28 | 2019-11-10 |  | 690000 | 690000 |  |  | 0 | 138 | na | na | 900 kcmil Alu Okonite Cable | Underground Transmission Line | na | na | na | na | 25.101(c)(5)(B)
0PT40192 KC/CL | Dog House - Prospero Solar 345 kV Line | Andrews County | Install one monopole and one span of wire to connect the customer line to Doghouse Switch. | 2020-01-06 | 2020-03-01 |  | 590033 |  |  |  | 0 | na | 345 | 0.3 | 959.6 kcmil ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(A)
0PT38448 AW/DD | Krum Tap Switch - Gainesville Sub 138 kV Line: Rippey Solar Interconnect | City of Gainesville, Cooke County | This project interconnects the Rippey Solar on the Krum Tap Sw - Gainesville Sub 138 kV Line at the Ray Roberts Switch. | 2020-09-15 | 2020-11-13 |  | 1015306 |  |  |  | 0 | 138 | 138 | 0.3 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 0.3 | na | na | 25.101(c)(5)(A)
0PT37229 DN/BC | Roanoke Switch - Saginaw Switch 138 kV Line: Reterminate to Deen Switch | City of Fort Worth, Tarrant County | Retermination of double-circuit (Roanoke/Euless) 138 kV line connecting to new Deen Sw. | 2019-11-04 | 2020-05-15 |  | 958557.96 | 958558 |  |  | 0 | 138 | 138 | 0.1 | 2-959.6 kcmil ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(B) | Below grade construction to start 10/1/2019, above grade construction to start 1/3/2020
0PT37237 DN/BC | Handley Switch - Saginaw Switch 138 kV Line: Reterminate to Deen Switch | City of Fort Worth, Tarrant County | Retermination of double-circuit (Handley) 138 kV line connecting to new Deen Sw. | 2019-11-04 | 2020-05-15 |  | 943604.37 | 943604 |  |  | 0 | 138 | 138 | 0.1 | 2-959.6 kcmil ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(B) | Below grade construction to start 10/1/2019, above grade construction to start 1/3/2020
0PT37236 DN/BC | Hicks Switch - Saginaw Switch 138 kV Line: Reterminate to Deen Switch | City of Fort Worth, Tarrant County | Retermination of double-circuit (Hicks) 138 kV line connecting to new Deen Sw. | 2019-11-04 | 2020-05-15 |  | 1387626.12 | 1387627 |  |  | 0 | 138 | 138 | 0.3 | 2-959.6 kcmil ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(B) | Below grade construction to start 10/1/2019, above grade construction to start 1/3/2020
0PT37238 DN/BC | Eagle Mountain Switch - Saginaw Switch 138 kV Line: Reterminate to Deen Switch | City of Fort Worth, Tarrant County | Retermination of double-circuit (Eagle Mtn.) 138 kV line connecting to new Deen Sw. | 2019-11-04 | 2020-05-15 |  | 1387626.12 | 1387627 |  |  | 0 | 138 | 138 | 0.3 | 2-959.6 kcmil ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(B) | Below grade construction to start 10/1/2019, above grade construction to start 1/3/2020
0PT37235 DN/BC | North Main Switch - Saginaw Switch 138 kV Line: Reterminate to Deen Switch | City of Fort Worth, Tarrant County | Retermination of double-circuit (N. Main) 138 kV line connecting to new Deen Sw. | 2019-11-04 | 2020-05-08 |  | 810689.33 | 810689 |  |  | 0 | 138 | 138 | 0.2 | 2-959.6 kcmil ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(B) | Below grade construction to start 10/1/2019, above grade construction to start 1/3/2020
0PT38778 JM/EA | Monticello Switch - Paris Switch 345 kV Line: Establish Woodard Switch | Lamar County | Establish a point of interconnection to the Impact Solar LLC generating facility by establishing Woodard Switch on the Monticello - Paris 345 kV transmission line. | 2020-01-27 | 2020-04-17 | [5 empty] | 0 | 345 | 345 | 0.25 | 2-959.6 kcmil ACSS/TW | Steel Towers | 170 | na | 370 | 0.25 | 25.101(c)(5)(A)
0PT38200 CL/MP | Carrollton East - Renner/Northaven 138 kV Line: Rebuild Farmers Branch Gillis - Structure T308A | City of Farmers Branch, Dallas County | Rebuild the 1.3 mile section of the Carollton East - Renner Sw/Northaven Sw 138 kV Line from Farmers Branch Gillis – Structure T308A using conductor greater than 1928A. Rebuild will end at structure T308A which is where the two circuits split to Renner and Northaven respectively. | 2019-11-10 | 2020-05-15 | [5 empty] | 0 | 138 | na | 1.3 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 1.3 | na | na | 25.101(c)(5)(B)
OPT38236 PO/EA | Lake Creek Switch - Waco East Switch 138 kV Line: Rebuild Lake Creek Switch - Waco Lasalle Sub | City of Waco, McLennan County | Rebuild of 7.6 mile 138 kV Line of single-circuit wooden h-frame structures to steel monopoles | 2019-11-01 | 2020-05-15 |  | 12773383 | 12773383 |  |  | 0 | 138 | 138 | 7.6 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 7.6 | na | na | 25.101(c)(5)(B) | Early start in November for foundations
0PT40107 PO/EA | Lake Creek Switch - Waco East Switch 138 kV Line: Rebuild Waco Lasalle Sub - Structure 1/9 section | City of Waco, McLennan County | Rebuild of 2.2 mile 138 kV Line of single-circuit wooden h-frame structures to steel monopoles | 2020-09-15 | 2020-12-31 | [5 empty] | 0 | 138 | 138 | 2.2 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 2.2 | na | na | 25.101(c)(5)(B)
0PT38347 CC/RS | Stephenville Switch - Comanche Switch 138 Kv Line : Cmpc H-frame Replacement | City of Comanche, Comanche County | This is a potential 2019 CMPC Corrosion and Erosion project. Background: A seasonal creek has eroded approx. 5' of soil around one of the legs of the wooden h-frame 10/2 to where it is now exposed significantly. This scope and estimate includes the cost of replacing the wooden h-frame with a more durable h-frame and contains a lot of access dollars due to its location. | 2019-10-07 | 2019-11-01 |  |  | 521762 |  |  | 25 | 138 | 138 | 0.2 | 636 ACSR | Steel Poles | 100 | 0.2 | na | na | 25.101(c)(3) | Emergency work to replace structure near Walnut Creek due to severe erosion.
0PT38497 DD/AB | Lake Creek (east) Switch - Tradinghouse Switch 345 Kv Line : Cmpc Erosion Control | City of Waco, McLennan County | This is a CMPC Erosion project to be completed in 2019. Tower foundations on either side of the crossing have been eroded and exposed. We will be reinforcing tower foundations to ensure a safe crossing. | 2019-10-31 | 2019-11-23 |  |  | 1000000 |  |  | 0 | 345 | 345 | 0.5 | 795 kcmil ACSR | DC Tangent Lattice | 100 | 0.5 | na | na | 25.101(c)(5)(B) | No construction on structures. Will only involve foundation reinforcement.
0PT39397 CW/JM | Wink Switch - Culberson Switch 138 kV Line: Long Pasture POD for BPX Energy Keystone | Reeves County | Establish a point of delivery to BPX Energy’s Keystone on the Wink - Culberson 138 kV transmission line. The point of delivery will be located in the Mason - Screwbean line section. | 2019-10-31 | 2019-11-22 |  |  | 1574155 |  |  | 0 | 138 | na | 0.35 | 959.6 ACSS/TW | Steel Poles/ H-frame Switch | 50 | na | 70 | 0.32 | 25.101(c)(5)(A)
0PT39077 CW/JM | Valley Switch - Paris Switch 138 kV Line: Allens Creek POI for Rayburn Lower Bois d'Arc Water Pump Station | Fannin County | Establish a point of interconnection to Rayburn Country Electric Cooperative’s Lower Bois d’Arc Creek Water Pump Station on the Valley - Paris 138 kV transmission line. | 2019-11-11 | 2020-02-01 |  |  | 1271785 |  |  | 0 | 138 | na | 0.4 | 959.6 ACSS/TW | Steel Poles/ H-frame Switch | 100 | na | 75 | 0.04 | 25.101(c)(5)(A)
0PT39500 CC/RS | Seagoville Switch - Crandall Sub 138 Kv Line : Cmpc Erosion Relocation | City of Seagoville, Dallas County | This project is a 2019 CMPC Corrosion/Erosion project. Structure 12/6 is a hybrid pole no located in the Trinity River due to severe erosion. | 2019-11-03 | 2019-11-22 |  |  | 1011727 |  |  | 0 | 138 | 138 | 0.2 | 795 ACSR | Steel Poles | 100 | 0.2 | 100 | 0.2 | 25.101(c)(5)(B) | Emergency work to replace two structures near the Trinity due to severe erosion, increased access charges.
18T62019 BMcD/BB | Springdale - Richland Hills (North Ckt) 138 kV Line | City of Fort Worth, Tarrant County | Rebuild the Springdale - Richland Hills (North Ckt) section of the Saginaw - Springdale - Richland Hills 138 kV line. The project consists of rebuilding the North circuit of the 3.7 mile line from Springdale - Str 7/3 N. | 2020-01-06 | 2020-06-30 | [5 empty] | 0 | 69/138 | 138 | 3.7 | 959.6 kcmil ACSS/TW | Steel Poles | Varies | 3.7 | na | na | 25.101(c)(5)(B)
18T62020 BMcD/BB | Springdale - Richland HiIls (South Ckt) 138 kV Line | City of Fort Worth, Tarrant County | Rebuild the Springdale - Richland Hills (South Ckt) section of the North Main Switch - Richland Hills 138 kV line. The project consists of rebuilding the South circuit of the 3.7 mile line from Str 3/5 S - 7/3 S. | 2020-01-06 | 2020-06-30 | [5 empty] | 0 | 69/138 | 138 | 3.7 | 959.6 kcmil ACSS/TW | Steel Poles | Varies | 3.7 | na | na | 25.101(c)(5)(B)
0PT40145 DN | Wolf Switch - Moss Switch 138 kV line: High Temp Upgrade | Ector & Ward County | Upgrade the Moss Switch – Wolf Switch 138 kV line for 120°C and 1146A, high temperature operation. | 2019-11-15 | 2020-06-01 |  |  | 1007917 |  |  | 0 | 138 | 138 | 31.42 | 795 kcmil ACSR | Wood H-Frames | 50 | 31.4 | na | na | 25.101(c)(5)(B)
0PT40963 BB | Handley Switch - Denton Avenue Sub 69 kV Line : CMPC System Hardening (Str. 3/5 & 3/6) | Tarrant County | Replace Structures 3/5 & 3/6 adjacent to I-30 in Arlington, TX consisting of existing single-circuit wooden H-frames with concrete H-frames. | 2019-12-01 | 2019-12-31 | [5 empty] | 0 | 69 | na | 0.1 | 300 kcmill ACSR | Concrete H-Frames | Varies | na | na | na | 25.101(c)(5)(B)
0PT38115 GD | Lewisville Switch (Brazos) - Lakepoint Switch (TNMP) Sub. 138 KV Line: Reconductor | City of Lewisville, Denton County | Upgrade 5.3 miles of the Lewisville Switch (BEC) – Lakepointe (TNMP) 138 KV Line using conductor 959.6 MCM ACSS "Suwanee” with E3X coating designed to operate at 1996 Amps and 200C. The existing 3/8" EHS shield wire will be replaced with 0.546" OD 48 count OPGW. Upgrade all line terminal and associated equipment to meet or exceed 1996 A. | 2019-12-31 | 2020-05-15 | [5 empty] | 55 | 138 | na | 5.3 | 959.6 kcmil ACSS/TW | Steel Towers | Varies | 5.3 | na | na | 25.101(c)(5)(A)
0PT39974 JM/CW | SL Pemkiff - Ringo 138kV Line: Slager Lake POD | Reagan County | Provide a 138 kV point-of-delivery (POD) for Sherrod on the Pemkiff - Ringo 138 kV line. The POD will be located approximately 1.8 miles east of the Pemkiff substation. | 2020-02-03 | 2020-05-15 | [5 empty] | 0 | 138 | na | 0.9 | 959.6 ACSS/TW | Steel Poles | na | na | 105 | 0.5 | 25.101(c)(5)(A)
0PT39620 JM/JO | Spraberry Switch - Midland East 138 kV Line : Cloverdale POD | City of Midland, Midland County | Provide a 138 kV point-of-delivery (POD) on the Spraberry Switch - Midland East 138 kV line. The POD will be located approximately 2.0 miles southeast of the Midland East Substation. | 2020-02-01 | 2020-06-30 | [5 empty] | 0 | 138 | na | 0.9 | 1926.9 ACSS/TW | Steel Poles | na | na | 70 | 0.9 | 25.101(c)(5)(A)
0PT40458 JM/CW | Ringgold Magnolia Tap – Beaver Creek Tap 69 kV Line: Install Barrel Springs (Oneok) POI | Clay County | Provide a 138 kV point-of-interconnect (POI) for TNMP's Oneok on the Ringgold Magnolia Tap - Beaver Creek Tap 69 kV line. The POI will be located approximately 2.6 circuit-miles from Beaver Creek Tap. | 2020-02-03 | 2020-05-15 | [5 empty] | 0 | 69 | na | 0.5 | 1/0 ACSR, 959.6 ACSS/TW | Steel Poles | na | na | 100 | 0.5 | 25.101(c)(5)(A)
0PT39894 CW/JM | McKenzie Draw Switch - Midland County Northwest/Midland East Switch 138 kV Line: Kelton Windmill POD | Martin County | Establish a point of delivery on the eastern circuit of the McKenzie Draw Switch - Midland County Northwest/Midland East Switch 138 kV transmission line. | 2019-11-30 | 2020-03-01 | [5 empty] | 0 | 138 | na | 0.29 | 1926.9 ACSS/TW/HS | Steel Poles/ H-frame Switch | 75 | na | 70 | 0.29 | 25.101(c)(5)(A)
0PT40457 JM/CW | Brown - Grady 138 kV Line: Lenorah POD | Martin County | Establish a point of delivery by establishing Lenorah Switch on the Brown - Grady 138 kV transmission line. | 2020-01-06 | 2020-05-15 | [5 empty] | 0 | 138 | 138 | 0.3 | 1-1926.9 kcmil ACSS/TW | Steel Monopoles | 70 | na | 70 | 0.3 | 25.101(c)(5)(A)
0PT39509 CZ/BB | Venus Switch-Sardis Switch 138 kV Line: Structure Replacement for Midlothian Hospital | City of Midlothian, Ellis County | Replace wood H-frame to a concrete H-frame for Midlothian Hospital | 2019-12-06 | 2019-12-17 | [5 empty] | 0 | 138 | na | 0.02 | 795 kcmil ACSR | Concrete H-Frame | 50 | 0.02 | na | na | 25.101(c)(5)(D) | This is a 100% reimbursable project by Methodist Hospital of Dallas
0PT39916 CZ/DN | McDonald Road-Big Spring Switch 138 kV Line: Loop into Hill Crest Sub | City of Big Spings, Howard County | Reconfigure McDonald Road-Big Springs Switch 138 kV line to loop into new Hill Crest Sub | 2019-12-15 | 2020-03-01 | [5 empty] | 0 | 138 | na | 0.02 | 1926.9 ACSS/TW | Steel DE Monopoles | 100 | 0.5 | na | na | 25.101(c)(5)(A)
0PT40226 CZ/DN | Big Spring Switch-Chalk 69 kV line: Modify Line for Hill Crest Sub | City of Big Spings, Howard County | Reconfigure Big Spring Switch-Chalk 69 kV Line to support the establishment of the new Hill Crest | 2019-12-15 | 2020-03-01 | [5 empty] | 0 | 69 | na | 0.02 | 1926.9 ACSS/TW | Steel DE 3-poles | 100 | 0.5 | na | na | 25.101(c)(5)(A)
Station
0PT39073 | Allens Creek POI: Establish 138 kV Point of Interconnection | Fannin County | Allens Creek POI: Establish 138 kV Point of Interconnection for Rayburn Interconnect, located in the Valley-Paris Sw. line. | 2019-12-02 | 2020-02-01 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37562 | Alligator Draw Sub : Establish station with two transformers and two feeder breakers. | City of Orla/Culberson County | Alligator Draw Sub : Establish station with two transformers and two feeder breakers on the new Horseshoe Springs Sw. Sta. Owl Hills 138 kV Line | 2019-09-16 | 2019-12-13 |  |  | 5725089 |  |  | 15 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT40140 | Andrews County South Switch : Install Auto #2 and establish the new Wink Switch terminal. Upgrade No Trees Switch line terminal for the existing Wink circuit. | City of Andrews, Andrews County | Install Auto #2 Install and establish the new Wink Switch terminal. Upgrade all line terminal and associated equipment for the existing No Trees – Wink line as a part of rebuilding the 8.8-mile No Trees Sw. Sta. - Andrews County South Sw. Sta. 138 kV Line. | 2019-08-26 | 2019-12-13 |  |  | 4699579 |  |  | 10 | 138/345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT01033 | Azle Sub: Install the third transformer with one feeder breaker | City of Azle/Tarrant County | Azle Sub: Install the third transformer with one feeder breaker | 2020-01-18 | 2020-03-21 | [5 empty] | 0 | 138/24.9 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37352 | Barstow Northwest Sub : Install Transformer #3 w/ two 21.6 kV feeder breakers and three feeder ties | City of Odessa/Ector County | Install Transformer with two feeder breakers and three feeder ties. | 2019-08-12 | 2019-11-15 |  |  | 2989092 |  |  | 30 | 138/21.6 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38409 | Battalion POD (Fort Hood East POD) : Establish a POD for Fort Hood East Substation to be constructed on the Fort Hood Army Base | Fort Hood Army Base | Establish a POD to serve the Fort Hood Army Base to provide a 138 kV point of delivery (POD) from Company's Killeen Fort Hood Switch - Killeen Switch 138 kV transmission line. | 2019-05-30 | 2019-08-21 | 2019-08-21 |  | 1157050 |  |  | 100 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38971 | Benbrook Sub : Create a loop in loop out, install FID's and install new Sub IV protection for transformer #1 and #2 | City of Fort Worth/Tarrant County | Create a loop in loop out, install FID's and install new protection for transformer #1 and #2 | 2019-09-16 | 2019-12-15 |  |  | 2399766 |  |  | 10 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37383 | Bennett Road Switch: Establish 69 kV ring bus | City of Decatur/ Wise County | Relocate the 138/69 kV from Decatur Switch by establishing a 69 kV yard at Bennett Road Switch. Install two (2) Circuit Breakers to Bowie and Oran. Expand the three Circuit Breaker 138 kV ring bus arrangement to a four Circuit Breaker ring bus arrangement. | 2019-06-10 | 2019-12-15 |  |  | 2192033.7 |  |  | 70 | 69/138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04157 | Bird Nest Sub formerly (Pflugerville South Substation) | City of Pflugerville/Travis | Establish Substation with one Transformer and Two Feeder Breakers | 2019-03-12 | 2019-11-23 |  |  | 3943117 |  |  | 3 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37341 | Blackbird Switch: Establish Station | City of Odessa/Andrews County | Establish station with a 3-breaker 138 kV ring bus arrangement to install a 138 kV point-of-interconnection (POI) for customer's generator. The POI will be located on the Andrews North Sw. Sta. - Fullerton Sw. Sta. 138 kV Line | 2019-08-06 | 2019-11-08 |  |  | 4169055 |  |  | 50 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38719 | Blackburn Switch: Establish station for a 138 kV point of interconnection | City of Jacksonville/Cherokee County | Establish a switching station in a 3-breaker 138 kV ring bus arrangement located in the Elkton Switch - Palestine South Switch 138 kV Line, approximately 17.2 miles south of Elkton Switch | 2019-05-27 | 2019-11-04 |  |  | 3510836 |  |  | 40 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37445 | Blackland POD: Station Demolition | City of Fate/Rockwall County | Remove Oncor owned equipment and structures from the Blackland POD. | 2020-01-14 | 2020-04-01 |  |  | 253048 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T65108 | Blackland Switch: Establish 138 kV station | City of Fate/Rockwall County | Install a 138 kV point of interconnection with a 3-breaker 138 kV ring bus arrangement on the Royse Sw. Sta. - Terrell Sw. Sta. 138 kV Line. | 2018-10-11 | 2019-10-31 |  |  | 5527820 |  |  | 97 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04155 | Blagg Sub: Establish Substation with one Transf. and Two Feeder Breakers: | City of Denton/ Denton County | Establish Substation with one Transf. and Two Feeder Breakers | 2019-11-01 | 2020-03-15 |  |  | 4763870 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38284 | Boulder POD : 138 kV Point of Delivery | City of Odessa | Establish Boulder a 138kV point of delivery for customer owned startion on the south circuit of the Wink – Culberson 138 kV Double-circuit Line. | 2019-11-18 | 2019-12-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04108 | Bowman Switch: 138 kV Line Terminal Additions | City of Wichita Falls/ Tarrant County | Install two circuit breakers. Move the existing Bowman - Lake Wichita 138 kV Line termination at Bowman from bus B to bus A. | 2019-06-01 | 2019-10-26 |  |  | 2088435 |  |  | 90 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT40126 | Brelyn Sub: (Coahoma West Sub) Establish substation | City of Coahoma/Howard County | Establish Substation with a one transformer with two Feeder Breakers | 2019-11-15 | 2020-05-31 |  |  | 4040613 |  |  | 0 | 138/21.6 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38723 | Canton Tap Switch: Canton Tap 138 kV Switching Station. Point of Interconnection | City of Canton/Van Zandt County | Establish a line terminal to connect Glenn Pine 138 kV Line. Upgrade and reconfigure all line terminal and associated equipment at Canton Tap Sw. Sta. to provide a 138 kV point of interconnection. | 2019-09-03 | 2019-10-26 |  |  | 500458 |  |  | 35 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT03966 | Canton Tap Switch: Modify Tyler Switch Line Relaying | City of Forney/Kaufman County | Modify relaying for ring bus terminal at Tyler Switch | 2020-06-15 | 2020-09-19 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39750 | Carrollton Frankford Rd Sub : Convert Station One and Two to 125 VDC and Replace Breakers | City of Carrollton/Denton County | Update protection, convert station one and two to 125 VDC and replace breakers | 2019-10-16 | 2019-12-15 |  |  | 597449 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T65033 | Carrollton NW Sub: Upgrade 138 kV Norwood & Lakepointe Lines | City of Carrollton, Denton County | Upgrade all terminal and associated equipment as a part of upgrading the NW Carrollton – Norwood Sw. Sta. 138 kV Double-circuit line. | 2018-11-15 | 2018-12-17 | 2018-12-17 |  | 435226 |  |  | 100 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3) | Associated with line project; substation is expected to be placed in service 06/2020
18T65029 | Cedar Crest Switch: Upgrade industrial line and replace bus diff panels | City of Dallas, Dallas County | Upgrade all line terminal and associated equipment to meet or exceed 2000 A. | 2018-12-03 | 2018-12-14 |  |  | 407403 |  |  | 100 | 69/138 | na | na | na | na | na | na | na | na | 25.83(a)(3) | Awaiting associated line work to energize
18T65018 | Centerville Switch: Upgrade line, auto and bus relaying | City of Dallas, Dallas County | Upgrade line, auto and bus relaying at Centerville Switch. | 2019-09-09 | 2019-12-15 |  |  | 1678074 |  |  | 10 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38420 | Central Bluff Switch : Install 345 kV breaker to provide Generator with one Point of Interconnection from a 345 kV breaker-and-a-half arrangement. | City of Blackwell, Nolan County | Install 345 kV breaker to provide Generator with one Point of Interconnection from a 345 kV breaker-and-a-half arrangement. | 2019-09-23 | 2019-11-01 |  |  | 1771933 |  |  | 20 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37566 | Chimney Well POD : Provide a 138 kV point-of-delivery (POD) | City of Odessa/ Ector County | Establish Chimney Well POD for customer owned station, a 138 kV on the Horseshoe Springs Sw - Owl Hills 138kV line. | 2019-10-16 | 2019-11-01 |  |  | 921244.66 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04158 | China Springs Substation: Install one Transf. #2 and 1-25 kV Feeder and install Distribution Automation on Feeders 2401 and 2403 | City of China Spring/McLennan County | Install Bank #2 with one Transformer and One Feeder Breaker. Includes installation of Distribution Automation on Feeders 2401 and 2403. | 2019-02-25 | 2019-11-27 |  |  | 1243074 |  |  | 60 | 138/24.9 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04000 | Collin Sw. Station 345/138 kV autotransformer #2 series reactor | City of Frisco/Collin County | Install a series reactor in series with the 345/138 kV autotransformer #2. | 2020-01-13 | 2020-04-15 | [5 empty] | 0 | 345/138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39490 | Comanche Peak 345 kV Switch : Upgrade Mitchell Bend to Double Breaker Double Bus | Glen Rose County | Upgrade Mitchell Bend line terminal to Double Breaker Double Bus | 2020-06-01 | 2020-12-20 | [5 empty] | 0 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38434 | Comanche Peak 345 kV: Upgrade Everman to double breaker double bus | City of Glen Rose/Somervell County | Install a new 345 kV breaker and breaker disconnect switch for the Everman line to make the bay double breaker, double bus. | 2019-12-04 | 2020-01-14 |  |  | 1340588.81 |  |  | 0 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
17T65036 | Crown Road Sub: Upgrade 138 kV line terminals | City of Dallas, Dallas County | Upgrade all terminal and associated equipment as a part of upgrading the NW Carrollton Norwood Switch 138 kV double-circuit line. | 2019-11-15 | 2019-11-01 |  |  | 264870 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04086 | Deen Switch: Establish Station to Replace Saginaw 138 kV Switch | City of Fort Worth/Tarrant County | Establish Deen Switch station by installing sixteen 138 kV circuit breakers in a breaker-and-a-half arrangement. | 2019-12-02 | 2020-05-15 |  |  | 15912850 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39812 | Dollarhide Sub: Modify bus to loop 138kV line in and out of station | City of Odessa/Winkler County | Modify bus to loop line in and out of station as a part of rebuilding the No Trees Switch - Andrews County South Switch 138 kV line. | 2020-01-06 | 2020-01-30 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37283 | Du Puy (Waco West) Sub : Replace Transformer by Rebuilding the Existing Substation | City of Waco/McLennan County | Establish Du Puy Substation with three transformers and ten feeder breakers. | 2019-08-16 | 2019-12-30 |  |  | 5906786 |  |  | 53 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38578 | Dunn POD : Provide a 138 kV point-of-delivery (POD) | City of Colorado City/ Mitchell County | Establish Dunn POD for customer owned stations for a 138 kV point of delivery, on the China Grove Radium 138 kV Line | 2019-07-29 | 2019-08-24 | 2019-09-19 |  | 551660 |  |  | 100 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04035 | Ennis Creek Switch: 138 kV Station Rebuild | City of Snyder/Scurry County | Rebuild the 138 kV Ennis Creek Switch with a 3-breaker 138 kV ring bus arrangement. | 2020-01-06 | 2020-03-14 | [5 empty] | 0 | 138/69 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39276 | Fate Sub: Establish Substation with one transformer and two feeder breakers | City of Fate/Rockwall County | Establish Substation with one transformer and two feeder breakers | 2019-12-01 | 2020-06-30 | [5 empty] | 0 | 138/24.9 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38216 | Fisher Road Switch : Replace 138 kV circuit breaker | City of Wichita Falls/ Tarrant County | Replace 138 kV circuit breaker | 2019-10-24 | 2019-11-04 |  |  | 216982 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38725 | Forest Grove Switch : Terminal Upgrade | City of Malakoff/Henderson County | Upgrade all line terminal and associated equipment to meet or exceed 2000 A. | 2019-11-01 | 2019-11-15 |  |  | 344369 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT03958 | Goddard Sub: Upgrade Line Terminal to 2000 A and Install FIDs on transformer #1 and #2 | City of Odessa/Midland County | Upgrade line terminal and associated equipment as part of the upgrade of Midland County Northwest Sw. Sta. - Midland East Sw. Sta. 138 kV Double-circuit Line. Install FIDs on transformer #1 and #2. | 2019-10-16 | 2019-12-31 |  |  | 1444304 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39341 | Heritage Sub : Convert transformer #1 to 138 kV and upgrade protection on CB | City of Fort Worth/ Tarrant County | Convert Transformer #1 to 138 kV and upgrade line protection on circuit breaker. | 2020-02-19 | 2020-03-05 |  |  | 187469 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39386 | Hicks Switch: Modification for interconnect and convert line communication for line to fiber | City of Fort Worth/Tarrant County | Modifications for interconnect and convert the line communication for line to fiber. | 2020-01-06 | 2020-03-14 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04057 | Hicks Switch: 13.8 kV Reactor Installation | City of Fort Worth/Tarrant County | Install 13.8 kV tertiary shunt reactors on Autotransformer #2 and installation of AC service to the new microwave center. | 2019-02-28 | 2019-09-13 | 2019-09-13 |  | 1016416 |  |  | 100 | 13.8 | na | 0.3 | na | na | na | na | na | na | 25.83(a)(3)
0PT04106 | Holliday Sub: 69 kV Terminal Upgrade to 138 kV | City of Holliday/Archer County | Upgrade the 69 kV Lake Wichita line terminal to 138 kV. | 2019-05-23 | 2019-10-30 |  |  | 3456242 |  |  | 90 | 69/138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38362 | Holly Ervin POD : Establish a 138 kV Point of Interconnection | City of Palestine/ Anderson County | Establish Holly Ervin POD for customer owned station, 138kV point of delivery on the Big Brown Tap - Long Lake 138kV line. | 2019-05-22 | 2019-10-16 |  |  | 1477517.87 |  |  | 95 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37618 | Horsehead Draw Sub (formerly Mentone Southwest Sub) : Establish one Substation Transformer and three feeder breakers | City of Odessa/Ector County | Establish station with one Transformer and three feeder breakers | 2019-03-18 | 2019-11-01 |  |  | 4043063 |  |  | 95 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
19T62005 | International Airport Sub: Replace 12.5 kV Substation | City of Fort Worth/Tarrant County | Rebuild the existing 138/12.5 kV Substation by replacing the existing 12.5 kV distribution switchgear with outdoor air insulated distribution circuit breakers at Stations 1 and 2. | 2019-06-03 | 2019-12-15 |  |  | 5421782 |  |  | 60 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37436 | Jacksonville Switch : Upgrade and reconfigure the existing station in a 5-breaker 69 kV single-bus arrangement | City of Jacksonville/Cherokee County | Upgrade and reconfigure the existing station by installing five, 69 kV circuit breakers in single-bus arrangement. Remove the Single Phase Auto Transformers. | 2019-06-25 | 2019-11-15 |  |  | 5034419 |  |  | 30 | 69/138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37311 | Kemp Ranch Switch (Venus Switch) : Install two 138 kV point of interconnections by constructing a 138 kV switching station in a breaker-and-a-half bus arrangement. | City of Midlothian/ Ellis County | Install two 138 kV POD for customer owned stations by constructing a 138 kV Kemp Ranch Switching station in a breaker-and-a-half bus arrangement. | 2019-02-18 | 2019-10-30 |  |  | 11506348 |  |  | 95 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38411 | Killeen Park Street Sub : Install three sectionalizing switches to loop line | City of Killeen/ Tarrant County | Install three sectionalizing switches and loop line into station to as a part of establishing a 138 kV point of interconnection (POI). | 2019-11-16 | 2019-12-14 |  |  | 191, 851 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38360 | Lake Hall Switch : Establish 345 kV Switching Station to Provide POI | City of Waco/McLennan County | Establish 345 kV switching station by installing two 345 kV transmission line exits and provide one interconnection point from a 345 kV three breaker ring bus arrangement. | 2019-09-16 | 2019-12-15 |  |  | 7196857 |  |  | 15 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04107 | Lake Wichita Switch: 69 kV Line Terminal Upgrade to 138 kV | City of Wichita Falls/ Tarrant County | Install one 138 kV circuit breaker on the 138 kV bus. Remove 69 kV bus and associated equipment. | 2019-07-22 | 2019-12-20 |  |  | 1140802 |  |  | 75 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T65010 | Las Colinas Sub: Upgrade 138 kV line terminals | City of Dallas, Dallas County | Upgrade all terminal and associated equipment to meet or exceed 2000 A as a part of upgrading the NW Carrollton- Norwood Switch 138 kV Double-circuit line. | 2020-01-15 | 2020-02-01 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38367 | Latigo (McPherson (BEC)) POI : Install a new 138 kV point of interconnection for the McPherson (BEC) 138 kV Substation | City of Fort Worth, Tarrant County | Establish a new 138 kV point of interconnection for the McPherson (BEC) 138 kV Substation located in the Roanoke Sw. Euless Sw. 138 kV Line. | 2019-08-19 | 2019-12-15 |  |  | 860751 |  |  | 15 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
17T65009 | Liggett Switch: 138 kV Cedar Hill Terminal upgrade, 345 kV protective relay upgrades and replace the Norwood switch transfer trip panel | City of Irving/Dallas County | Upgrade all terminal and associated equipment as a part of upgrading the Cedar Hill Sw. Sta. Liggett 138 kV line. | 2018-01-10 | 2020-02-28 |  |  | 1630734 |  |  | 50 | 138/345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04389 | Mankin Switch: Establish Station for POI | City of Trinidad City/Henderson County | Establish a 138 kV Point of Interconnection located in the Trinidad Sw. Sta. Kaufman Northwest 138 kV line by constructing the Mankin 138 kV POI with a 3-breaker 138 kV ring bus arrangement. | 2019-04-01 | 2019-11-15 |  |  | 533268 |  |  | 5 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
16T64009 | Mary Avenue Substation: Install one transformer and two feeder breakers | City of Waco/McLennan County | Establish station with one transformer and two feeder breakers | 2020-01-06 | 2021-06-01 | [5 empty] | 0 | 138/12.5 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38220 | Montfort Switch: Replace 138 kV circuit breaker | City of Corsicana/ Navarro County | Replace three 138 kV circuit breakers | 2019-11-01 | 2019-11-27 |  |  | 699414 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38134 | McDonald Road Switch : Establish line terminal | City of Big Springs/Howard County | Install one 3200 A, 138 kV circuit breaker in a ring bus arrangement as a part of converting the McDonald Road Switch - Garden City Substation 69 kV Line Section to 138 kV operation. | 2019-07-15 | 2019-10-16 |  |  | 1097713.5 |  |  | 99 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38218 | Navarro Sub : Replace two 138 kV circuit breakers | City of Corsicana/ Navarro County | Replace two 138 kV circuit breakers | 2019-09-16 | 2019-09-28 | 2019-09-28 |  | 310041 |  |  | 100 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37587 | Nelson Switch : Install a 138 kV POI | City of Odessa/ Andrews County | Install a 138 kV POI on the Andrews County South Sw. Sta. Fullerton Sw. Sta. 138 kV Line by installing three 138 kV circuit breakers in a ring bus configuration. | 2019-08-16 | 2019-11-15 |  |  | 4329713 |  |  | 10 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
16T62037 | North Main Switch: Install two 138 kV, 2000 A circuit breakers with provisions for an additional 138 kV circuit. | City of Fort Worth/ Tarrant County | Install two 138 kV, 2000 A circuit breakers with provisions for an additional 138 kV circuit. | 2019-11-25 | 2020-03-14 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT01788 | Norwood Substation: Upgrade 138 kV NW Carrollton Line Terminals | City of Irving/Dallas County | Upgrade all terminal and associated equipment as a part of upgrading the NW Carrollton Norwood Sw. Sta. 138 kV double-circuit line. | 2019-02-04 | 2020-05-15 |  |  | 286343 |  |  | 90 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T65027 | Norwood Substation: 345 KV Bus Auto #1 & 138 kV yard relay upgrade | City of Irving/Dallas County | Upgrade protective relaying within the 345 kV and 138 kV switchyards at Norwood Substation | 2019-02-25 | 2019-11-30 |  |  | 2500000 |  |  | 75 | 345/138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T65039 | Norwood Switch: Modify 345/138 auto #1 relay protection | City of Irving/Dallas County | Modify 345/138 auto #1 relay protection | 2019-03-07 | 2019-03-22 | 2019-03-25 |  | 295008 |  |  | 100 | 345 /138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37340 | Odessa EHV Switch : Install security measures | City of Odessa/Midland County | Install security measures at switching station. | 2019-11-01 | 2019-12-15 |  |  | 2102168 |  |  | 0 | 345/138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38518 | Odessa EHV: 345 kV Line Terminal Addition | City of Odessa, Ector County | Install two, 345 kV circuit breakers to establish line terminal to create the new Odessa EHV Switch - Wolf Switch 345 kV Line as a part of adding a second circuit to the existing Moss Switch - Odessa EHV Switch. | 2019-09-03 | 2020-05-15 |  |  | 3640838 |  |  | 25 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04005 | Odessa North Switch: Remove 69 kV terminal and re-terminate the new Cowden North - Odessa North 138 kV Line | City of Odessa, Ector County | Remove 69 kV terminal and re-terminate the new Cowden North - Odessa North 138 kV Line. | 2019-08-05 | 2019-10-16 |  |  | 518029 |  |  | 98 | 69 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04138 | Owl Hills Sub: Establish Substation with two Transformers and four Feeder Breakers | City of Odessa/Ector County | Establish Substation with two Transformers and four Feeder Breakers | 2019-05-13 | 2019-10-16 |  |  | 5235119 |  |  | 99 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39370 | Palestine Sub : Modify relaying for the new Blackburn Switch terminal. | City of Palestine/Anderson County | Modify relaying for the new Blackburn Switch terminal by adding a transfer trip receiver | 2019-10-16 | 2019-10-21 |  |  | 116126 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
16T62052 | Panther Island Sub | City of Fort Worth/Tarrant County | Remove and rebuild the North Main Substation to the south of Heritage Sub and North Main Switch as Panther Island Sub consisting of two transformers and eight feeder breakers | 2019-11-02 | 2019-12-31 |  |  | 6029913 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T65075 | Parkdale Switch: Replace two 138 kV bus differentials and replace 138 kV | City of Dallas/Dallas County | Upgrade 138 kV bus protection to provide redundancy for three phase faults and replace 138 kV circuit breaker. | 2019-11-11 | 2019-12-01 |  |  | 678303 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T65175 | Prolina (Redbud) 138 kV POI | City of Prosper/ Collin County | Install three motor operated SCADA control 138 kV line sectionalizing switches. | 2019-06-24 | 2019-11-15 |  |  | 1226517.76 |  |  | 70 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04087 | Quarry Field Switch ( formerly Kyle Ranch Sw. Sta.) | City of Mentone/Loving County | Establish the switching station by installing eight 138 kV circuit breakers in a breaker-and-a-half bus arrangement in the Riverton - Wink 138 kV Double Circuit Line. This project will also include the installation of terminal equipment for two 138 kV PODs for customer owned stations. | 2019-06-03 | 2019-10-16 |  |  | 12580046 |  |  | 99 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38606 | Railside Switch : Establish POD by installing four 138 kV circuit breakers in a ring-bus arrangement | City of Odessa/Wink County | Provide two 138 kV PODs for customer owned stations on the Wink Switch No Trees Switch 138 kV Line by establishing four 138 kV circuit breakers in a ring-bus arrangement. | 2019-07-22 | 2019-12-13 |  |  | 716285 |  |  | 45 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04062 | Ranger Sub: 69 kV emergency capacitors | City of Ranger, Eastland County | Install one bank of 69 kV transmission capacitors and associated terminal equipment. | 2019-02-28 | 2019-10-31 |  |  | 2077310 |  |  | 85 | 69/138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38072 | Red Lakes Switch : Establish station a 3-breaker 138 kV ring bus arrangement | City of Odessa/Ector County | Establish station with a 3-breaker 138 kV ring bus arrangement for interconnection generation interconnection. | 2019-08-15 | 2019-11-08 |  |  | 4213265 |  |  | 50 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39224 | Richardson Spring Creek-Install 4th Transformer and Two Feeder Breakers | City of Dallas/Dallas County | Install 4th Transformer and Two Feeder Breakers | 2019-11-18 | 2020-02-29 | [5 empty] | 0 | 138/12.5 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04008 | Riverton Switch: Install 138 kV Line Terminal for 138 kV Sand Lake Switch Line | City of Wink/ Winkler County | Install one 138 kV circuit breaker and associated switches, CVTs, arresters, relaying in Rung #3 as a part of constructing the new Riverton Sw. Sta. Sand Lake Sw. Sta. 138 kV Line. | 2019-05-06 | 2019-09-30 | 2019-09-30 |  | 2000000 |  |  | 100 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37647 | Rondo STATCOM | Odessa County | Install one +250/-250 Mvar Dynamic Reactive Device and one 138 kV circuit breaker at Quarry Field 138 kV Sw. Station | 2019-05-15 | 2019-12-20 |  |  | 33058594 |  |  | 60 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04026 | Rough Creek Sub: Establish 138-12.5 kV Station | Scurry County | Convert the station to operate at 138 kV by replace the existing substation with a two transformer station. | 2020-01-02 | 2020-04-18 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT01720 | Royse Switch: 138 kV Forney line terminal upgrade | City of Royce City/Rockwall County | Upgrade all terminal and associated equipment as a part of upgrading the Forney Switching Station Royse Switching Station 138 kV Line. | 2019-02-25 | 2019-12-15 |  |  | 527217 |  |  | 89 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT01664 | Sand Lake (Previously Mentone) 138 kV Switching Station | City of Odessa, Ector County | Establish the Sw Sta. by installing eight 3200 A, and 138 kV circuit breakers in a breaker-and-a-half bus arrangement. | 2019-02-11 | 2019-07-29 | 2019-07-29 |  | 8468049 |  |  | 100 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04308 | Screwbean Sub: Install Second Transformer and Two Feeders | City of Salt Flat/ Hudspeth County | Install Screwbean Substation Transformer #2, one transformer and two feeder breakers | 2019-05-06 | 2019-11-15 |  |  | 3504267 |  |  | 99 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T65019 | Seagoville Switch: Replace Seagoville Switch: Replace 345 kV bus and 138 kV bus protective relaying | City of Seagoville/ Dallas County | Upgrade protective relaying at 345 kV and 138 kV Switching Stations. Replace failed Reactor on Reactor Bank #1 | 2019-04-08 | 2019-12-15 |  |  | 1600000 |  |  | 65 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38854 | Shin Oak 138 kV POD : Establish Point of Delivery | City of Wink/ Winkler County | Establish a 138 kV POD for customer owned station on the Yucca Switch Moss Switch 138 kV Line. | 2019-10-21 | 2019-12-20 |  |  | 614379 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04142 | Shipwreck Sub : Establish Substation with two Transformers and five Feeder Breakers | City of Odessa/Ector County | Establish Substation with two Transformers and five Feeder Breakers. Connect the Shipwreck 138 kV Substation to the McDonald Road Switch - Shipwreck Substation 138 kV Line, approximately 14 miles southwest of Garden City 69 kV Substation, and install three 138 kV sectionalizing switches | 2019-04-08 | 2019-10-06 | 2019-10-06 |  | 4600000 |  |  | 100 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T62062 | Springdale Sub - Upgrade bus and switches to 2000 A | City of Fort Worth/ Tarrant County | Upgrade all line terminal and associated equipment. | 2019-01-07 | 2019-07-19 | 2019-07-19 |  | 412200 |  |  | 100 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04398 | Thorntonville Sub: Install one transformer and two Feeder | City of Monahans/ Ward County | Establish substation by installing Transformer #1,one transformer, and two feeder breakers | 2019-07-15 | 2019-10-16 |  |  | 4083202 |  |  | 97 | 138/69 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T65002 | TI Dallas Sub: Terminal upgrade for Coit Road line, (West Circuit) | City of Dallas, Dallas County | Upgrade all terminal and associated equipment as a part of upgrading the TI Dallas - Schroeder Road 138 kV double-circuit underground line section by replacing the existing HPFF underground conductor with two new XLPE underground conductors. | 2019-09-23 | 2019-11-15 |  |  | 946042 |  |  | 10 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT37764 | TI Dallas Sub : Terminal upgrade for Kirkland park line, (East Circuit) | City of Dallas/Dallas County | Upgrade all terminal and associated equipment as a part of upgrading the TI Dallas – Schroeder Road 138 kV double-circuit underground line section by adding two additional HPFF underground conductors. | 2020-01-01 | 2020-04-15 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04051 | Tri Corner Switch: 345 kV rung 4 addition | City of Seagoville/ Dallas County | Install three 345 kV, 3200 A circuit breakers to create the Watermill Sw. Sta. to Trinidad 345 kv Line Terminal as a part of the reconductor of Tri Corner Switching Station. Watermill Switching Station. 345 KV line | 2019-01-30 | 2020-01-31 |  |  | 2186397.78 |  |  | 47 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04054 | Trinidad Switch: Terminal upgrade | City of Trindad/ Henderson County | Upgrade line terminal as a part of the Tri Corner Switching Station. Watermill Switching Station. 345 KV line upgrade to 3200 A. and modify relaying for the new Tri Corner Sw Line terminal. | 2019-02-11 | 2019-12-14 |  |  | 367680.82 |  |  | 99 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38928 | Turnbaugh Corner Switch: Establish 138 kV switching station | Odessa County | Establish a switching station with a 3-breaker 138 kV ring bus arrangement for a 138 kV POI for customers generator. | 2019-12-02 | 2020-03-13 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT03971 | Tyler Substation: Rebuild to 138 kV | City of Tyler/ Smith County | Convert Tyler Sub to 138kV by replacing two transformers with two transformers and install one feeder breaker. | 2019-10-28 | 2020-06-30 |  |  | 7116396 |  |  | 0 | 69/12.5 | 138/12.5 | na | na | na | na | na | na | na | 25.83(a)(3)
18T65023 | Venus Switch: Bus and auto relay upgrades | City of Venus/Ellis County | Upgrade North and South 345 kV bus protection and add three 345 kV circuit breakers. | 2019-08-19 | 2019-12-15 |  |  | 2808705 |  |  | 20 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04099 | Vineyard (formerly Grapevine) Switch: Establish 138 kV Station | City of Grapevine, Tarrant County | Establish the Vineyard 138 kV Switch approximately 0.2 miles south of McKamy Tap by installing twelve 3200 A, 138 kV circuit breakers in a breaker-and-a-half arrangement. | 2019-06-21 | 2019-12-31 |  |  | 10349114 |  |  | 30 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04053 | Watermill Switch: Line Terminal Upgrade and Replace 138 kV circuit breaker | City of Lancaster/Dallas County | Upgrade line terminal as a part of the reconductor of Tri Corner Switching Station -Watermill Switching Station 345 KV. Replace 138 kV circuit breaker. | 2019-02-11 | 2020-01-31 |  |  | 720044 |  |  | 67 | 345/138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39201 | West Network Sub-Rebuild station adjacent to existing station | City of Dallas/Dallas County | Rebuilding of West Network Substation includes replacing swtichgear containing twelve feeder breakers and three transformers | 2020-06-01 | 2020-09-01 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04289 | Weston Substation: Establish one substation transformer and two feeder breakers | City of McKinney/Dallas County | Establish one substation transformer and two feeder breakers | 2019-11-01 | 2020-04-15 |  |  | 4667449 |  |  | 0 | 138/24.9 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39591 | Willow Wells Sub: Install one transformer and two feeder breakers | Odessa County | Install one transformer and two feeder breakers | 2020-01-06 | 2020-02-06 | [5 empty] | 0 | 138/21.6 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38773 | Wolf Switch: Establish 345 kV three rung breaker and a half | City of Monahans, Ward County | Establish switching station by installing nine 345 kV circuit breakers in a three rung breaker and a half arrangement with two autotransformers and three 138 kV circuit breakers. | 2019-10-16 | 2020-05-02 |  |  | 20150000 |  |  | 0 | 138 | 345/138 | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38646 | Ray Roberts Switch : Establish Station for POI | City of Gainesville, Cooke County | Install a 138 kV (POI) Connect the Ray Roberts 138 kV Switch to the Gainesville Switch – Spring Switch (BEC) and install three circuit breakers | 2019-12-18 | 2020-02-15 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39579 | Hill Crest: Rebuild station to replace existing station with one transformer & three feeder breakers | City of Big Springs, Howard County | Rebuild station to replace the existing station with one transformer and three feeder breakers | 2019-12-19 | 2020-02-29 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39819 | Dog House Switch : Establish 345kV Switching Station | City of Andrews, Andrews County | Establish the Dog House Switch that will provide a POI in Andrews County and the existing Clear Fork 345 kV Switch. | 2019-11-22 | 2020-02-15 | [5 empty] | 0 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38704 | Handley Switch : Bus Protection Upgrade | City of Fort Worth, Tarrant County | Replace 138 kV bus protection and install new 138 kV breaker and associated switches/CCVT's. | 2019-10-31 | 2019-11-23 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38948 | Ntusu Clearfork Switch : Establish 345 Kv Line Terminal To Dog House | City of Andrews, Andrews County | Establish one 345 kV, 3000A circuit breaker at Clearfork Switch and all terminal and associated equipment. | 2019-10-31 | 2020-04-01 |  |  | 2721164 |  |  | 0 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39269 | China Lake Sub : Establish Substation With oneTransformer and two feeder breakers | City of Pyote, Ward County | Establish substation with one transformer and two feeder breakers | 2019-11-20 | 2020-02-29 | [5 empty] | 0 | 138/22 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39945 | Decatur Switch : Demo 69 Kv Station | City of Decatur, Wise County | Demolition of the 69kV yard at Decatur. | 2019-09-16 | 2019-11-30 |  |  | 449459 |  |  | 10 | 138/69 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38585 | Howden POD : Provide A 138 Kv (POD) | City of Big Springs, Howard County | Install motor operate Scada control on three 138 kV 3200 A line sectionalizing switches and provide customer revenue metering as a part of installing a 138 kV (POD) on the Buzzard Draw – Gunsight 138 kV Line. | 2019-10-31 | 2019-11-30 |  |  | 563897 |  |  | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39746 | Allen Switch : Security Updates | City of Plano, Denton County | Security Updates | 2019-12-01 | 2020-01-20 | [5 empty] | 0 | na | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39900 | Camp Pasture POD | City of Odessa, Ector County | Provide a 138 kV (POD) on the south circuit of the Spraberry Switch – Midessa South Switch/Odessa EHV Switch 138 kV Double-Circuit Line. Install motor operated SCADA control on three 138 kV 3200 A line sectionalizing switches, provide customer revenue metering. | 2019-12-01 | 2020-04-15 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39273 | Cedar Hill Sub: Install one transformer | City of Cedar Hill, Dallas County | Add second transformer, transformer #4, convert the distribution load and move away from transformer #1 and #2. | 2019-12-01 | 2020-01-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04046 | Centerville I45 Sub: 138 kV Line Terminal Upgrade | City of Buffalo, Leon County | Upgrade all line terminal and associated equipment to meet or exceed 2000 A as a part of the rebuild of the Crockett Switching Station - Jewett Switching Station 138 kV Line. | 2020-01-10 | 2020-05-15 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39416 | Cloverdale POD: Provide a (POD) | City of Midland, Midland County | Install motor operate Scada control on three 138 kV 2000 A line sectionalizing switches, and provide customer revenue metering as a part of installing a as a part of installing a 138 kV (POD) on the Midland East Spraberry Switch 138 kV Line. | 2019-12-01 | 2020-01-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
17T65011 | Dalworth Substation 138 kV line terminal upgrade | City of Arlington, Tarrant County | Upgrade all terminal and as a part of upgrading the Cedar Hill Sw. Sta. Liggett 138 kV line. Includes replacing high side switches on both transformers and adding FIDs to both transformers. | 2019-12-01 | 2020-01-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39275 | Dooley Sub : Replace one transformer | City of Monahans, Ward County | Rebuild existing Northward Sub with one transformer and establish new Dooley Sub with one transformer | 2019-12-01 | 2020-05-15 | [5 empty] | 0 | 69 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38449 | East Network Sub : Relay work to support the new terminal at Sargent Rd | City of Dallas, Dallas County | Add dual SEL-421 relays and communications in the underground switchgear for the low voltage totaling breakers. | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | na | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39272 | Edgecliff Sub : Install Second Transformer #4 with Two Feeder Breakers | City of Fort Worth, Tarrant County | Install Transformer #4 with two feeder breakers, rebuild the bus, upgrade station #3 bus to standard and relaying to Suburban IV. | 2020-09-14 | 2020-12-15 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39911 0PT40872 | Elbow Sub : Replace Transformer #1 with one transformer | City of Big Springs, Howard County | Replace Transformer #1 with one transformer | 2019-12-01 | 2020-01-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39466 | Gober Switch: Establish a switching station for a 138 kV POI | City of Gober, Fannin County | Install three 138 kV, 3200 A circuit breakers in a ring bus arrangement to establish a 138 kV (POI). Connect this switching station to the Bonham Wolf City 138 kV line section of the Valley Switch. | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39759 | Hutto Switch : 345/138kV autotransformer #2 | City of Hutto, Williamson County | Install a new autotransformer, one 345 kV, 3200 A circuit breaker and two 138 kV, 3200 A circuit breakers at Hutto Switch. Install two 37.5 MVAR reactors on the tertiary of the new autotransformer. | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138/345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
17T65187 | Industrial Blvd Switching Station: 138 kV Cedar Crest Line Terminal Upgrade | City of Dallas, Dallas County | Upgrade all line terminal and associated equipment to meet or exceed 2000 A. | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39278 | Jack Rabbit Sub : Establish Substation with one Transformer, and three feeder Breakers | City of Odessa, Ector County | Establish Substation with one Transformer, and three feeder Breakers | 2019-12-01 | 2020-04-08 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39895 | Kelton Windmill POD: Establish POD | City of Odessa, Ector County | Provide a 138 kV (POD) on the east circuit of the McKenzie Draw Switch – Midland County Northwest/Midland East Switch 138 kV Double-Circuit Line. Install motor operated SCADA control on three 138 kV 3200 A line sectionalizing switches, provide customer revenue metering. | 2019-12-01 | 2020-04-15 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39748 | Kennedale Sub : Establish substation with two transformers | City of Kennedale, Tarrant County | Establish substation by installing Bank #3 and Bank #4 with two transformers and four feeder breakers. This will be done by looping the Everman – Cleburne 138 kV Line into station. | 2019-12-01 | 2020-01-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04144 | Kyle Ranch: Establish Substation with two Transformers and four Feeder Breakers | City of Odessa, Ector County | Establish Substation with two transformer and four Feeder Breakers | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
18T650111 | Lake Hubbard Switch: Protective Relay Upgrade | City of Forney/Kaufman County | Upgrade East and West 138 kV bus protection to provide redundancy for three phase faults. | 2019-12-01 | 2020-12-31 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39486 | Lakecrest Sub (Fish Creek) : Establish Substation with one Transformer and Three Feeder Breaker | City of Grand Prairie, Dallas County | Establish Substation with one transformer and three feeder breakers | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT40696 | Lakewood Sub : Replace transformer #1 and #2 | City of Fort Worth, Tarrant County | Replace transformer #1 and #2 with Delta-Wye transformers due to transformer #2 failing and requiring replacement. | 2019-12-01 | 2020-01-24 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39742 | Long Pasture POD | Not in City Limits, Ward County | Install motor operate Scada control on three 138 kV 3200A line sectionalizing switches, a 138kV circuit breaker for UVLS, and provide customer revenue metering as a part of installing a as a part of installing a 138 kV (POD) on the north circuit of the Wink Switch - Riverton Switch 138 kV Double-Circuit Line. | 2020-01-06 | 2020-02-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT40652 | Loring POI : Establish 138 KV POI | Clay County, TX | Install motor operated Scada control on three 138 kV 2000 A line sectionalizing switches as a part of installing a 138 kV POI located in the Commerce Sw. - Bonham Sw. 138kV line. | 2020-04-16 | 2020-05-06 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38517 | Moss Switch: 345 kV Line Terminal Addition | City of Odessa, Ector County | Install two 3200 A, 345 kV circuit breakers to establish line terminal to create the new Odessa EHV Switch - Wolf Switch 345 kV Line and 138 kV breaker replacement | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138/345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04282 | Pauline Substation: Install oneTransf. #2 and one 25kV Feeder | City of Mabank/Henderson County | Install one transformer #2 and One Feeder Breaker | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT01087 | Salado South Substation: Establish Salado South Substation with one transformer and two feeder breakers | City of Salado, Bell County | Establish Salado South Substation with one transformer and two feeder breakers | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38427 | Sand Lake Switch: Establish 345kV Switch Station | City of Odessa, Ward County | Establish the 345kV Switch Station at Sand Lake Switch. The initial build out will consist of four 345kV circuit breakers to accommodate termination of AEP Solstice lines 1 and 2, installation of Auto #2 and associated tertiary equipment, installation of Auto #1 tertiary reactors and associated equipment. | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT04021 | Sargent Road Switch: 138 kV terminal upgrade | City of Dallas, Dallas County | Add line terminal as a part of the new line from Sargent Rd- to Oakland Ave. Upgrade all line terminal and associated equipment to meet or exceed 1200 A. | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT01906 | Scatter Branch Substation: Establish New Substation with One Transformer and Two 25 kV Feeder Breakers | City of Greenville, Hunt County | Establish New Substation with one transformer and Two 25 kV Feeder Breakers | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT40274 | Slager Lake POD : Provide a 138 kV (POD) | Reagan County | Install motor operate Scada control on three 138 kV 2000 A line sectionalizing switches as a part of installing a 138 kV POD on the Pemkiff-Ringo 138 kV Line. | 2020-03-16 | 2020-04-11 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT39694 | Vealmoor Switching Station: Install second autotransformer | City of Big Springs, Howard County | Upgrade the switch by installing a second auto transformer and re-configuring the switching station. Install a 4-breaker ring bus arrangement with four 345 kV, 3200 A circuit breakers. | 2019-12-01 | 2019-12-28 | [5 empty] | 0 | 345/138 | na | na | na | na | na | na | na | na | 25.83(a)(3) | NTSU project
0PT40162 | Wink Switch : Install 138 kV circuit breaker | City of Wink, Winkler County | Install one 3200 A, 138 kV circuit breaker and reterminate the Wink Switch – Yucca Drive Switch 138 kV Line onto the fifth rung and terminate the new Wink Switch – Andrews County South Switch 138 kV Line on the fourth rung. | 2019-12-01 | 2020-03-20 | [5 empty] | 0 | 138 | na | na | na | na | na | na | na | na | 25.83(a)(3)
0PT38701 | Woodard Switch : Establish Station for (POI) | City of Deport, Lamar County | Install a 345 kV (POI) at Woodard 345 kV Switch. Connect the Woodard 345 kV Switch to the Monticello Switch Paris Switch 345 kV line section. Install three 345 kV, 3200 A circuit breakers at Woodard 345 kV Switch. | 2019-12-01 | 2020-02-20 | [5 empty] | 0 | 345 | na | na | na | na | na | na | na | na | 25.83(a)(3)
CCN APPLICATIONS - APPROVED
17T80065/ 18T63096 BP/BC | Riverton Sw. - Tunstill POD 138 kV Line | City of Orla, Reeves County | This project is to construct the new double-circuit 138 kV line connecting the planned Riverton Switching Station to the Tunstill POD to serve Stateline Processing's oil and gas facilities. One circuit will be installed initially. | 2018-08-01 | 2018-12-15 | 2018-12-15 | 7755000 | 7755000 |  |  | 100 | na | 138 | 5.4 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 70 | 5.4 | 47595 | Application Filed on 10/12/2017. Administrative approval received on 12/28/2017.
13T80013 BP 16T80061 TB | New Bethel 345 kV Loop Line | Anderson, Freestone, Navarro and Henderson Counties | This project is to construct the new double-circuit New Bethel 345 kV Line connecting the proposed New Bethel Switching station to a connection along one of four existing 345 kV transmission line segments in the region. | 2020-12-31 | 2022-12-31 |  | 26499000 |  |  |  | 0 | na | 345 | 27 | 1926.9 kcmil ACSS/TW | Lattice Steel Towers | na | na | 160 | 13.5 | 44672 | Application Filed 7/10/2015. Administrative Approval received on 09/25/2015.
16T80071 BP 18T63018 CH/IA | Littman - Phillips Andrews Tap 138 kV Line | Andrews County | This project is to construct the new double-circuit Littman - Phillips Andrews Tap 138 kV Line connecting the existing Littman Substation to the existing Phillips Andrews Tap. One circuit will be installed initially. | 2018-06-13 | 2018-10-20 | 2018-10-20 | 9714000 | 9947814 |  |  | 100 | na | 138 | 11.1 | 959.6 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 70 | 11.1 | 46987 | Application Filed 4/10/2017. Administrative Approval received on 6/26/2017.
16T80079 BP 0PT38665 AB 0PT04007 AB | Riverton - Sand Lake 345 kV Line (Operating at 138 kV) | Reeves, Ward, and Loving Counties | Construct the new double-circuit capable Riverton - Sand Lake 345 kV Line connecting the proposed Riverton Switching Station to the proposed Sand Lake Switching Station. Initially, one circuit will be installed and operated at 138 kV. | 2018-01-09 | 2019-12-31 |  | 47483000 | 62908903 |  |  | 50 | na | 138 | 37 | 1926.9 kcmil ACSS/TW | Lattice Steel Towers | na | na | 160 | 37 | 47368 | Application Filed 7/21/2017. Final Order issued on 5/11/2018.
18T80016 18T63124 BP/AB | Dune Switch Loop 138 kV Line | Winkler County | This project is to construct the new double-circuit 138 kV line connecting the existing Oncor Wink-Yukon 138 kV Line to the proposed Dune Switch station. | 2019-01-25 | 2019-03-01 | 2019-03-01 | 2850000 | 4038607 |  |  | 100 | na | 138 | 4 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 70 | 2 | 48310 | Application Filed 5/11/2018. Administrative Approval received 7/30/2018.
17T80077 BP 0PT38182, 0PT38179 KD/KF | Odessa EHV - Riverton and Moss - Riverton 345 kV Line | Crane, Ector, Loving, Reeves, Ward, and Winkler Counties | This project is to construct the new double-circuit 345 kV line connecting the Odessa EHV Switching Station and the Moss Switching Station to the Riverton Switching Station. | 2020-01-31 | 2020-12-31 |  | 199729000 |  |  |  | 0 | 345 | 345 | 216.7 | 1926.9 kcmil ACSS/TW | Lattice Steel Towers | 150 | 15.9 | 160 | 100.4 | 48095 | Application Filed 3/16/2018. Final Order issued on 9/17/2018.
18T80036 BP 0PT04001 0PT38840 0PT37565 OER/JC | Horseshoe Springs - Owl Hills 138 kV Line | Culberson County | Construct the new single-circuit 138 kV line connecting the Horseshoe Springs Switching Station to Owl Hills Subsation. | 2019-06-24 | 2019-11-13 |  | 34033000 | 41619112 |  |  | 50 | na | 138 | 29.9 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 70 | 29.9 | 48544 | Application Filed 8/31/2018. Administrative Approval received on 11/20/2018.
0PT37302 BP; 0PT38601 OER/JC | Owl Hills - Tunstill POD 138 kV Line | Culberson and Reeves Counties | Construct the new single-circuit 138 kV line connecting the proposed Owl Hills Substation to the Tunstill POD. | 2020-01-30 | 2020-05-30 |  | 20628000 | 26705050 |  |  | 0 | na | 138 | 18.7 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 70 | 18.7 | 48582 | Application Filed 8/31/2018. Administrative Approval received on 11/20/2018.
17T80032 BP | Cogdell - Clairemont 138 kV Line | Kent and Scurry Counties | This project is to construct the new double-circuit 138 kV line connecting the Oncor existing Cogdell Substation to the Brazos Electric existing Clairemont Substation. One circuit will be installed initially. | 2020-01-30 | 2020-06-30 |  | 13,170,500 (Oncor Portion) |  |  |  | 0 | na | 138 | 11.9 (Oncor Portion) | 959.6 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 70 | 11.9 (Oncor Portion) | 47808 | This is a joint project with Brazos Electric Power - only Oncor associated project costs are being reported. Application Filed 12/11/2017. Final Order issued on 1/18/2019.
0PT39679 KC/CL | Clearfork - Dog House 345 kV Line | Andrews County | Construct the new 345 kV transmission line connecting the existing Clearfork Switchyard to the proposed Dog House Switchyard. | 2019-10-01 | 2020-03-02 |  | 14304695 | 13832636 |  |  | 0 | na | 345 | 10.3 | 959.6 kcmil ACSS/TW | Steel Poles | na | na | 175 | 10.3 | 48861 | Application Filed 11/28/2018. Administrative Approval received 2/6/2019. This is a NTU project.
S4T15775 CL | Tall City - Glass 138 kV Line | Martin and Midland Counties | Construct the new 138 kV transmission line connecting the existing Tall City station to the existing Glass station. | 2018-07-16 | 2019-04-10 |  | 13027901 | 13027901 |  |  | 100 | na | 138 | 13.06 | 959.6 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 100 | 13.06 | 45308 | Application Filed 11/13/2015. Final Order issued on 9/15/2016. This is a NTU project.
S4T15844 CL | Sale Ranch - Natural Dam 138 kV Line | Howard and Martin Counties | Construct the new 138 kV transmission line connecting the existing Sale Ranch station to the existing Natural Dam station. | 2018-07-23 | 2019-06-05 |  | 17425000 | 17425000 |  |  | 100 | na | 138 | 16.98 | 959.6 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 100 | 16.98 | 45397 | Application Filed 12/4/2015. Final Order issued on 9/16/2016. This is a NTU project.
NA | Stiles - Coates 138 kV Line | Reagan County | Construct the new 138 kV transmission line connecting the existing Stiles station to the proposed Coates station. | 2020-12-31 |  |  | 9682000 |  |  |  | 0 | na | 138 | 8 | 959.6 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 100 | 8 | 46726 | Application Filed 1/17/2017. Final Order issued on 9/29/2017. This is a NTU project. No project number has been assigned yet.
0PT37182 BP | Sand Lake - Solstice 345 kV Line | Pecos, Reeves, and Ward Counties | This project is to construct the new double-circuit 345 kV line connecting the Oncor Salt Lake Switch to the AEP Texas Solstice Switch. | 2020-04-30 | 2020-12-31 |  | 49,110,000 (Oncor Portion) |  |  |  | 0 | na | 345 | 89 | 1926.9 kcmil ACSS/TW | Lattice Steel Towers | na | na | 160 | 44.5 | 48785 | This is a joint project with AEP Texas - only Oncor associated project costs are being reported. Application Filed 11/7/2018. Final Order issued on 6/26/2019.
0PT38174 BP | Riverton - Kyle Ranch 138 kV Line | Loving and Reeves Counties | Construct the new single-circuit 138 kV line connecting the Riverton Switch station to the Kyle Ranch Substation. | 2020-03-30 | 2020-09-30 |  | 19207000 |  |  |  | 0 | na | 138 | 15.2 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 70 | 15.2 | 49304 | Application Filed 3/28/2019. Administrative Approval received on 7/17/2019.
0PT39835 BP | Ogallala - Abernathy 345 kV Line | Castro, Hale and Swisher Counties | Construct the new single-circuit 345 kV line connecting the existing Ogallala station to the existing Abernathy station. This project is part of the LP&L integration into the ERCOT system. | 2020-03-30 | 2021-06-30 |  | 87876048 |  |  |  | 0 | na | 345 | 57.9 | 1926.9 kcmil ACSR/TW | Steel Poles or Lattice Steel Towers | na | na | 175 | 57.9 | 48625 | Application Filed 9/6/2018. Final Order issued on 9/26/2019. This is a NTU project.
0PT38573 BP | Riverton - Sand Lake 345 kV Line Circuit Addition (Phase 2) | Reeves and Ward Counties | Add the second circuit on the vacant circuit position of the Riverton - Sand Lake 345 kV Line that will be operated at 345 kV. | 2020-01-01 | 2020-12-31 |  | 29,200,000 (t-line) 1,185,000 (station) |  |  |  | 0 | 138 | 345 | 39.9 | 1926.9 kcmil ACSS/TW | Lattice Steel Towers | 160 | 39.9 | na | na | 49723 | Application Filed 7/19/2019. Administrative Approval received on 10/7/2019.
| CCN APPLICATIONS - PENDING | [19 empty] | .
0PT38176 BP | Kyle Ranch - Quarry Field 138 kV Line | Loving County | Construct the new single-circuit 138 kV line connecting the Kyle Ranch Substation to the Quarry Field Switch station. | 2020-03-30 | 2020-09-30 |  | 16832000 |  |  |  | 0 | na | 138 | 12.4 | 1926.9 kcmil ACSS/TW | Steel or Concrete Poles | na | na | 70 | 12.4 | 49302 | Application Filed 3/28/2019.
0PT39896 BP | Abernathy - Wadsworth 345 kV Line | Hale and Lubbock Counties | Construct the new single-circuit 345 kV line connecting the existing Abernathy station to the existing Wadsworth station. This project is part of the LP&L integration into the ERCOT system. | 2020-03-30 | 2021-06-30 |  | 56736759 |  |  |  | 0 | na | 345 | 32.9 | 1926.9 kcmil ACSR/TW | Steel Poles or Lattice Steel Towers | na | na | 175 | 32.9 | 48668 | Application Filed 9/20/2018.
0PT39845 BP | Wadsworth - New Oliver - Farmland 345 kV Line (WNF) | Lubbock and Lynn Counties | Construct the new single-circuit 345 kV line connecting the existing Wadsworth station to the existing Farmland station, routed through one of two options for the proposed New Oliver station. This project is part of the LP&L integration into the ERCOT system. | 2020-03-30 | 2021-06-30 |  | 67769000 |  |  |  | 0 | na | 345 | 41.9 | 1926.9 kcmil ACSR/TW | Steel Poles or Lattice Steel Towers | na | na | 175 | 41.9 | 48909 | Application Filed 12/19/2018.
| Southeast - New Oliver - Oliver 115 kV Line (SNO) | Lubbock County | Construct the new single-circuit 115 kV line connecting the existing Southeast station to the existing Oliver station, routed through one of two options for the proposed New Oliver station. This project is part of the LP&L integration into the ERCOT system. |  |  |  | 20688000 |  |  |  | 0 | na | 115 | 17.8 | 959.6 kcmil ACSS/TW | Steel Poles | na | na | 60 | 17.8
0PT39846 BP | Abernathy - North - North Loop 345/115 kV Line | Hale and Lubbock Counties | Construct the new transmission line connecting the existing Abernathy station to the northern portion of LP&L's planned 115 kV loop line, routed through one of three options for the proposed North station. Depending on which North station is used, this line will be either a single-circuit 345 kV line or a combination of single-circuit 345 kV and double-circuit 115 kV line. This project is part of the LP&L integration into the ERCOT system. | 2020-07-31 | 2021-06-30 |  | 39782000 |  |  |  | 0 | na | 345/115 | 34.3 | 1926.9 kcmil ACSR/TW (345 kV) 959.6 kcmil ACSS/TW (115 kV) | Steel Poles or Lattice Steel Towers (345 kV) Steel Poles (115 kV) | na | na | 175 (345 kV) 60 (115 kV) | 24.6 | 49151 | Application Filed 2/19/2019.

## EntryInstructions
General Instructions for Entering Information
1. Please use "na" whenever appropriate to reduce ambiguity, except in the "Costs," "Percent Complete," and "Percent Variance" columns. 2. Any new or revised entry must be entered using a red font. In the month following the red font entry, change the previous month's red entries back to black and make any new entries for the new month in red. This aids PUCT staff in quickly identifying any changes from the previous month's report. 3. On the final monthly report on an existing line in which one of the attributes as listed in the attribute spreadsheets below has changed, enter that data in a bolded green font.
Utility's Project Number | Enter the Utility's Project Number. No duplicate numbers are allowed in this column.
Project Name | Enter the name of the project. If possible, use the same name as was reported to ERCOT in any reports.
Location (City/County) | Enter the names of the counties where the project is located. Also enter the names of cities, if appropriate. Please delineate all county and city names with commas only. (e.g., Liberty, Chambers, Anahuac, etc.)
Description | Describe the project in enough detail to allow the Commission to ensure that the work does not require a CCN, if the utility does not intend to apply for a CCN. Include any significant or relevant detail not being reported in other columns.
Estimated (or Actual) Start Date | Enter the estimated project starting date. When construction begins, please replace the estimated date with the actual date of the start of construction
Finish Date (Construction Complete) | Enter the date (mm/dd/yy) when the construction related to the project has been completed.
Date Energized (If Applicable) | Enter the date (mm/dd/yy) the project was energized or restored to service (if applicable).
Initial Estimated Project Cost | CCN Projects Only: Enter the estimated cost from the CCN application. When reporting both T-Line and Substation Costs, enter them separately in the same cell. (e.g., "$3,946,000 T-Line; $1,768,000 Substation") This number shall not be changed in future months unless the Application is amended. Please DO NOT use links to other sheets within the workbook. Non-CCN Projects Only: No entry is needed; Enter the estimated cost in the
Final Estimated Project Cost | CCN Projects: Enter the latest available estimated cost for the month that construction starts. This number shall not be changed after construction begins. and a cost variance explanation is not required unless requested by PUC Staff For Non-CCN Projects: Enter the initial estimated cost. Estimate revisions are not necessary
Final Actual Project Cost | Enter the actual, final project cost after the project has been energized and all costs have been recorded. Omit the project from all following reports.
% Variance | The cells contain a formula for calculating the percent variance of the final actual cost with respect to the final estimated cost. This is essentially a calculation of the percent of the cost over-run or under-run. Please do not change these cells.
Percent Complete | State the construction progress of the project as a percent. Please use only an integer and do not write"%." Do not report the percent of money spent.
Existing Voltage | Enter the nominal system existing voltage, if any. In the event of a voltage upgrade, this will be the "before" voltage. If the project is for a new line, enter "na." For projects involving multiple voltages, please delineate the voltages by a comma, (e.g., "69,138"). Please do not write "volts."
Upgraded or New Voltage | Enter the nominal system voltage after upgrading or if new line construction is involved. Please use the same practices described in the "Existing Voltage" column. Please do not write "volts."
Circuit Length (Miles) | Enter the total circuit length. Example: For a new double-circuit line using 10 miles of new ROW, the circuit length would be 20 miles. Please enter only a number, if possible. Please do not write "miles."
Conductor Type & Size & Bundling | Describe the conductor characteristics, including whether double or single circuit or mixed. Lengthy explanations shall be made in the Project Description column.
Structure Type(s) | Describe structure types and materials used.
Existing ROW Width (Feet) | Enter width of existing ROW. The entry type is unrestricted. If the project is only for new line and no old ROW exists, enter "na." Entries such as "60,80,100" or "60 - 100" or "centerline" are permissible. Make detailed explanations, if needed, elsewhere. Please do not write "feet."
Existing ROW Length (Miles) | Enter length of existing ROW. The entry type is unrestricted. If the project is only for new line and no old ROW exists, enter "na." Make detailed explanations, if needed, elsewhere. Please do not write "miles."
New ROW Width (Feet) | Enter width of new ROW. The entry type is unrestricted. Entries such as "60,80,100" or "60 - 100" or "centerline" or "railroad" or "street" are permissible. Make detailed explanations, if needed, elsewhere. Please do not write "feet."
New ROW Length (Miles) | Enter new (additional) ROW length, in miles. Please do not write "miles."
Rule Section or PUC Control Number | Enter the PUC Substantive Rule 25.101 section(s) which are applicable. For multiple section applicability, please delineate by commas, e.g., "25.101(c)(5)(A), 25.101(c)(5)(B)" for a project incorporating a line extension (A) and a voltage upgrade on the existing line which is being extended (B). If the project involves a CCN Application, enter ONLY the .5-digit control number. Please do not write "docket," "CCN" or other text, except when needed in citing Rule 25.101. Should the project include work done under both CCN and 25.101(c)(5), follow the same practices and delineate with commas.
Comments | Enter information not included elsewhere, including reimbursed costs. A cost variance explanation is no longer required for non-CCN projects. However, utilities will be required to submit a Cost Analysis only for CCN Projects. See Note below.

## 16T80061 & 16T64136
Project No. 16T80061 & 16T64136 - New Bethel 345 kV Loop Line - Transmission Line Project
| Estimated cost included in CCN Application (Route 1963) | Estimated cost once a route is approved and CCN granted (Route 1963) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 2952000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 601000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 2959000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 8324000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 11663000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 26499000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total |  | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | N/A | N/A
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 499000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 3341000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 338000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 2467000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 6645000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 587000 | Costs not yet available | Costs not yet available
Estimated Project Total | 7232000 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 26499000

## 16T80071 & 18T63018
Project No. 16T80071 & 18T63018 - Littman - Phillips Andrews Tap 138 kV Line - Transmission Line Project
| Estimated cost included in CCN Application | Estimated cost approved route and CCN Granted. | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 799000 | 799000 | Costs not yet available
Engineering and Design (Utility) | 476000 | 476000 | Costs not yet available
Engineering and Design (Contract) | 898000 | 618925 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 2877000 | 3200000 | Costs not yet available
Construction of Facilities (Utility) | 0 | 100000 | Costs not yet available
Construction of Facilities (Contract) | 4664000 | 4753889 | Costs not yet available
Estimated Total Cost | 9714000 | 9947814 | Costs not yet available
Other (all costs not included in the above categories) | 0 | 0 | Costs not yet available
Estimated Project Total | 9714000 | 9947814 | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | 0 | N/A
Engineering and Design (Utility) | 45500 | 45500 | Costs not yet available
Engineering and Design (Contract) | 0 | 0 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 195000 | 195000 | Costs not yet available
Construction of Facilities (Utility) | 21500 | 21500 | Costs not yet available
Construction of Facilities (Contract) | 190000 | 190000 | Costs not yet available
Estimated Total Cost | 452000 | 452000 | Costs not yet available
Other (all costs not included in the above categories) | 0 | 0 | Costs not yet available
Estimated Project Total | 452000 | 452000 | Costs not yet available
Reported on Monthly Construction Report | 9714000 | 9947814

## 16T80079 & 0PT04007
Project No. 16T80079 & 0PT04007 & 0PT38665- Riverton - Sand Lake 345 kV Line - Transmission Line Project (Operating at 138 kV)
| Estimated cost included in CCN Application (Route 56) | Estimated cost once a route is approved and CCN granted (Route 54) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 4781000 | 8230416 | Costs not yet available
Engineering and Design (Utility) | 1773000 | 976563 | Costs not yet available
Engineering and Design (Contract) | 1987000 | 1621845 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 14486000 | 20013049 | Costs not yet available
Construction of Facilities (Utility) | 0 | 0 | Costs not yet available
Construction of Facilities (Contract) | 24456000 | 32067030 | Costs not yet available
Estimated Total Cost | 47483000 | 62908903 | Costs not yet available
Other (all costs not included in the above categories) | 0 | 0 | Costs not yet available
Estimated Project Total | 47483000 | 62908903 | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | 0 | N/A
Engineering and Design (Utility) | 0 | 540000 | Costs not yet available
Engineering and Design (Contract) | 500000 | 45000 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 4000000 | 4315185 | Costs not yet available
Construction of Facilities (Utility) | 100000 | 100000 | Costs not yet available
Construction of Facilities (Contract) | 4150000 | 4548467 | Costs not yet available
Estimated Total Cost |  | 9548652 | Costs not yet available
Other (all costs not included in the above categories) | 0 |  | Costs not yet available
Estimated Project Total | 8750000 | 9548652 | Costs not yet available
Reported on Monthly Construction Report | 47483000 | 62908903

## 17T80065 & 18T63096
Project No. 17T80065 & 18T63096 - Tunstill POD 138 kV Line - Transmission Line Project
| Estimated cost included in CCN Application (Route 2) | Estimated cost once a route is approved and CCN granted (Route 2) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 465000 | 465000 | Costs not yet available
Engineering and Design (Utility) | 182000 | 182000 | Costs not yet available
Engineering and Design (Contract) | 619000 | 619000 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 2319000 | 2319000 | Costs not yet available
Construction of Facilities (Utility) | 0 | 0 | Costs not yet available
Construction of Facilities (Contract) | 4170000 | 4170000 | Costs not yet available
Estimated Total Cost | 7755000 | 7755000 | Costs not yet available
Other (all costs not included in the above categories) | 0 | 0 | Costs not yet available
Estimated Project Total | 7755000 | 7755000 | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | N/A | N/A
Engineering and Design (Utility) | 0 | 0 | Costs not yet available
Engineering and Design (Contract) | 242035 | 242035 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 846095 | 846095 | Costs not yet available
Construction of Facilities (Utility) | 93355 | 93355 | Costs not yet available
Construction of Facilities (Contract) | 611505 | 611505 | Costs not yet available
Estimated Total Cost | 1792990 | 1792990 | Costs not yet available
Other (all costs not included in the above categories) | 0 | 0 | Costs not yet available
Estimated Project Total | 1792990 | 1792990 | Costs not yet available
Reported on Monthly Construction Report | 7755000 | 7755000

## 17T80077
Project No. 17T80077 - Odessa EHV - Riverton and Moss - Riverton 345 kV Line - Transmission Line Project
| Estimated cost included in CCN Application (Route 1180) | Estimated cost once a route is approved and CCN granted (Route 1180) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 21540000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 5322000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 2269000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 74495000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 96103000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 199729000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 199729000 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | N/A | N/A
Engineering and Design (Utility) | 245000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 922857 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 15969607 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 2270494 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 4424042 | Costs not yet available | Costs not yet available
Estimated Total Cost | 23832000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 23832000 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 199729000

## 18T80036
Project No. 18T80036, 0PT04001, 0PT38840, 0PT3765 - Horseshoe Springs - Owl Hills 138 kV Line - Transmission Line Project
| Estimated cost included in CCN Application (Route 508) | Estimated cost once a route is approved and CCN granted (Route 508) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 2827000 | 4554323 | Costs not yet available
Engineering and Design (Utility) | 970000 | 0 | Costs not yet available
Engineering and Design (Contract) | 1402000 | 6171328 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 9019000 | 13983403 | Costs not yet available
Construction of Facilities (Utility) | 0 | 0 | Costs not yet available
Construction of Facilities (Contract) | 19815000 | 16910058 | Costs not yet available
Estimated Total Cost | 34033000 | 41619112 | Costs not yet available
Other (all costs not included in the above categories) | 0 |  | Costs not yet available
Estimated Project Total | 34033000 | 41619112 | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | N/A | N/A
Engineering and Design (Utility) | 90000 | 0 | Costs not yet available
Engineering and Design (Contract) | 80000 | 4641321 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 1752000 | 7207631 | Costs not yet available
Construction of Facilities (Utility) | 226500 | 562250 | Costs not yet available
Construction of Facilities (Contract) | 602000 | 4343654 | Costs not yet available
Estimated Total Cost | 2750500 | 16754856 | Costs not yet available
Other (all costs not included in the above categories) | 117500 | 0 | Costs not yet available
Estimated Project Total | 2868000 | 16754856 | Costs not yet available
Reported on Monthly Construction Report | 34033000 | 41619112

## 18T80016 & 18T63124
Project No. 18T80016 & 18T63124 - Dune Switch Loop 138 kV Line - Transmission Line Project
| Estimated cost included in CCN Application | Estimated cost once a route is approved and CCN granted | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 350000 | 135000 | Costs not yet available
Engineering and Design (Utility) | 200000 | 53000 | Costs not yet available
Engineering and Design (Contract) | 150000 | 107618 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 850000 | 916717 | Costs not yet available
Construction of Facilities (Utility) | 0 | 0 | Costs not yet available
Construction of Facilities (Contract) | 1300000 | 2826272 | Costs not yet available
Estimated Total Cost | 2850000 | 4038607 | Costs not yet available
Other (all costs not included in the above categories) | 0 |  | Costs not yet available
Estimated Project Total | 2850000 | 4038607 | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | 10000 | N/A
Engineering and Design (Utility) | 0 | 250000 | Costs not yet available
Engineering and Design (Contract) | 275000 | 65000 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 1750000 | 1934091 | Costs not yet available
Construction of Facilities (Utility) | 0 | 0 | Costs not yet available
Construction of Facilities (Contract) | 2000000 | 1765205 | Costs not yet available
Estimated Total Cost | 4025000 | 4024296 | Costs not yet available
Other (all costs not included in the above categories) | 0 | 0 | Costs not yet available
Estimated Project Total | 4025000 | 4024296 | Costs not yet available
Reported on Monthly Construction Report | 2850000 | 4038607

## 17T80032
Project No. 17T80032 - Cogdell - Clairemont 138 kV Line - Transmission Line Project
*THIS IS A JOINT PROJECT WITH BRAZOS ELECTRIC POWER - ALL COSTS SHOWN IN TABLE BELOW ARE ONCOR'S PORTION OF THE PROJECT
| Estimated cost included in CCN Application (Route 125) | Estimated cost once a route is approved and CCN granted (Route 39) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 1226000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 378500 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 438000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 2930000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 5225000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 10197500 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 10197500 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | N/A | N/A | N/A
Engineering and Design (Utility) | N/A | N/A | N/A
Engineering and Design (Contract) | N/A | N/A | N/A
Procurement of Material & Equipment (including Stores) | N/A | N/A | N/A
Construction of Facilities (Utility) | N/A | N/A | N/A
Construction of Facilities (Contract) | N/A | N/A | N/A
Estimated Total Cost | N/A | N/A | N/A
Other (all costs not included in the above categories) | N/A | N/A | N/A
Estimated Project Total | N/A | N/A | N/A
Reported on Monthly Construction Report | 10197500

## 0PT37302
Project No. OPT37302, 0PT38601 - Owl Hills - Tunstill POD 138 kV Line - Transmission Line Project
| Estimated cost included in CCN Application (Route 15) | Estimated cost once a route is approved and CCN granted (Route 15) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 1769000 | 3498658 | Costs not yet available
Engineering and Design (Utility) | 607000 | 0 | Costs not yet available
Engineering and Design (Contract) | 830000 | 3505474 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 5734000 | 8210994 | Costs not yet available
Construction of Facilities (Utility) | 0 | 0 | Costs not yet available
Construction of Facilities (Contract) | 11688000 | 11489924 | Costs not yet available
Estimated Total Cost | 20628000 | 26705050 | Costs not yet available
Other (all costs not included in the above categories) | 0 |  | Costs not yet available
Estimated Project Total | 20628000 | 26705050 | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | N/A | N/A
Engineering and Design (Utility) | 90000 | 0 | Costs not yet available
Engineering and Design (Contract) | 0 | 328471 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 1250000 | 1533127 | Costs not yet available
Construction of Facilities (Utility) | 155000 | 64150 | Costs not yet available
Construction of Facilities (Contract) | 352000 | 477226 | Costs not yet available
Estimated Total Cost | 1847000 | 2402974 | Costs not yet available
Other (all costs not included in the above categories) | 0 | 0 | Costs not yet available
Estimated Project Total | 1847000 | 2402974 | Costs not yet available
Reported on Monthly Construction Report | 20628000 | 26705050

## 0PT37182
Project No. 0PT37182 - Sand Lake - Solstice 345 kV Line - Transmission Line Project
*THIS IS A JOINT PROJECT WITH AEP TEXAS - ALL COSTS SHOWN IN TABLE BELOW ARE ONCOR'S PORTION OF THE PROJECT
| Estimated cost included in CCN Application (Route 320) | Estimated cost once a route is approved and CCN granted (Route XX) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 4561500 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 1058500 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 1348000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 16793500 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 500 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 25348000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 49110000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 49110000 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | N/A | N/A
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 400000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 13200000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 1210000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 2026000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 16836000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 764000 | Costs not yet available | Costs not yet available
Estimated Project Total | 17600000 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 49110000

## 0PT38174
Project No. 0PT38174 - Riverton - Kyle Ranch 138 kV Line - Transmission Line Project
| Estimated cost included in CCN Application (Route 7) | Estimated cost once a route is approved and CCN granted (Route X) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 1694000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 517000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 876000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 4866000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 11254000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 19207000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 19207000 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 70000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 200000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 1900000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 120000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 750000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 3040000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 3040000 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 19207000 | Costs not yet available

## 0PT38176
Project No. 0PT38176 - Kyle Ranch - Quarry Field 138 kV Line - Transmission Line Project
| Estimated cost included in CCN Application (Route 11) | Estimated cost once a route is approved and CCN granted (Route X) | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 1382000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 422000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 834000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 4424000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 9770000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 16832000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 16832000 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 2270000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 500000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 7700000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 585000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 4800000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 15855000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 15855000 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 16832000 | Costs not yet available

## 0PT39679
Project No. 0PT39679 - Clear Fork - Dog House Line - NTU Transmission Line Project
| Estimated cost included in CCN Application | Estimated cost once a route is approved and CCN granted | Approximately 12 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 1051381 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 32509 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 632401 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 7237942 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 97793 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 5169697 | Costs not yet available | Costs not yet available
Estimated Total Cost | 14221723 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 82972 | Costs not yet available | Costs not yet available
Estimated Project Total | 14304695 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 10400 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 724600 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 3217100 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 3043300 | Costs not yet available | Costs not yet available
Estimated Total Cost | 6995400 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 6995400 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 14304695 | Costs not yet available

## S4T15775
Project No. S4T15775 - Tall City - Glass 138 kV Line - NTU Transmission Line Project
| Estimated cost included in CCN Application (Route D) | Estimated cost once a route is approved and CCN granted (Route X) | Approximately 12 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 3512346 | 3512346 | Costs not yet available
Engineering and Design (Utility) | 195795 | 195795 | Costs not yet available
Engineering and Design (Contract) | 884484 | 884484 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 3548984 | 3548984 | Costs not yet available
Construction of Facilities (Utility) | 164887 | 164887 | Costs not yet available
Construction of Facilities (Contract) | 4621319 | 4621319 | Costs not yet available
Estimated Total Cost | 12927815 | 12927815 | Costs not yet available
Other (all costs not included in the above categories) | 100086 | 100086 | Costs not yet available
Estimated Project Total | 13027901 | 13027901 | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 |  | Costs not yet available
Engineering and Design (Utility) | 0 |  | Costs not yet available
Engineering and Design (Contract) | 0 |  | Costs not yet available
Procurement of Material & Equipment (including Stores) | 0 |  | Costs not yet available
Construction of Facilities (Utility) | 0 |  | Costs not yet available
Construction of Facilities (Contract) | 0 |  | Costs not yet available
Estimated Total Cost | 0 |  | Costs not yet available
Other (all costs not included in the above categories) | 0 |  | Costs not yet available
Estimated Project Total | 0 |  | Costs not yet available
Reported on Monthly Construction Report | 13027901 | 13027901

## S4T15844
Project No. S4T15844 - Sale Ranch - Natural Dam 138 kV Line - NTU Transmission Line Project
| Estimated cost included in CCN Application (Route C) | Estimated cost once a route is approved and CCN granted (Route X) | Approximately 12 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 4395000 | 4395000 | Costs not yet available
Engineering and Design (Utility) | 252000 | 252000 | Costs not yet available
Engineering and Design (Contract) | 1131000 | 1131000 | Costs not yet available
Procurement of Material & Equipment (including Stores) | 5044000 | 5044000 | Costs not yet available
Construction of Facilities (Utility) | 165000 | 165000 | Costs not yet available
Construction of Facilities (Contract) | 6338000 | 6338000 | Costs not yet available
Estimated Total Cost | 17325000 | 17325000 | Costs not yet available
Other (all costs not included in the above categories) | 100000 | 100000 | Costs not yet available
Estimated Project Total | 17425000 | 17425000 | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 0 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 0 | Costs not yet available | Costs not yet available
Estimated Total Cost | 0 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 0 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 17425000 | 17425000

## NA
Project No. NA - Stiles - Coates 138 kV Line - NTU Transmission Line Project
| Estimated cost included in CCN Application (Route B4) | Estimated cost once a route is approved and CCN granted (Route X) | Approximately 12 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 3347000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 249000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 733000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 2070000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 222000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 2915000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 9536000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 146000 | Costs not yet available | Costs not yet available
Estimated Project Total | 9682000 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 161000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 84000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 893000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 4376000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 432000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 2780000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 8726000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 8726000 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 9682000 | Costs not yet available

## 0PT39835
Project No. 0PT39835 - Ogallala - Abernathy 345 kV Line - NTU Transmission Line Project (Dkt. 48625)
| Estimated cost included in CCN Application (Route 4) | Estimated cost once a route is approved and CCN granted (Route 4a) | Approximately 12 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 13575702 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 165760 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 3430680 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 35371142 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 356601 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 34795274 | Costs not yet available | Costs not yet available
Estimated Total Cost | 87695159 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 180889 | Costs not yet available | Costs not yet available
Estimated Project Total | 87876048 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 507200 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 4883800 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 2913600 | Costs not yet available | Costs not yet available
Estimated Total Cost | 8304600 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 8304600 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 87876048 | Costs not yet available

## 0PT39896
Project No. 0PT39896 - Abernathy - Wadsworth 345 kV Line - NTU Transmission Line Project (Dkt. 48668)
| Estimated cost included in CCN Application (Route 1) | Estimated cost once a route is approved and CCN granted (Route X) | Approximately 12 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 7979470 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 110471 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 1917538 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 21275928 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 202943 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 25127504 | Costs not yet available | Costs not yet available
Estimated Total Cost | 56613854 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 122905 | Costs not yet available | Costs not yet available
Estimated Project Total | 56736759 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 605500 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 5266900 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 3531300 | Costs not yet available | Costs not yet available
Estimated Total Cost | 9403700 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 9403700 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 56736759 | Costs not yet available

## 0PT39845
Project No. 0PT39845 - Wadsworth - New Oliver - Farmland 345 kV Line (WNF) and Southeast - New Oliver - Oliver 115 kV Line (SNO) - NTU Transmission Line Projects (Dkt. 48909)
| Wadworth - New Oliver - Farmland 345 kV Line |  |  |  | Southeast - New Oliver - Oliver 115 kV Line
| Estimated cost included in CCN Application (Route 20) | Estimated cost once a route is approved and CCN granted (Route X) | Approximately 12 months after construction is complete |  | Estimated cost included in CCN Application (Route 9) | Estimated cost once a route is approved and CCN granted (Route X) | Approximately 12 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs: |  | Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 8257000 | Costs not yet available | Costs not yet available | Right-of-Way and Land Acquisition | 4471000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 117000 | Costs not yet available | Costs not yet available | Engineering and Design (Utility) | 120000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 2794000 | Costs not yet available | Costs not yet available | Engineering and Design (Contract) | 1530000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 27393000 | Costs not yet available | Costs not yet available | Procurement of Material & Equipment (including Stores) | 4298000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 314000 | Costs not yet available | Costs not yet available | Construction of Facilities (Utility) | 216000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 28726000 | Costs not yet available | Costs not yet available | Construction of Facilities (Contract) | 9921000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 67601000 | Costs not yet available | Costs not yet available | Estimated Total Cost | 20556000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 168000 | Costs not yet available | Costs not yet available | Other (all costs not included in the above categories) | 132000 | Costs not yet available | Costs not yet available
Estimated Project Total | 67769000 | Costs not yet available | Costs not yet available | Estimated Project Total | 20688000 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities |  | Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 564000 | Costs not yet available | Costs not yet available | Right-of-Way and Land Acquisition | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available | Engineering and Design (Utility) | 105000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 1617000 | Costs not yet available | Costs not yet available | Engineering and Design (Contract) | 1075000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 10517000 | Costs not yet available | Costs not yet available | Procurement of Material & Equipment (including Stores) | 25465000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available | Construction of Facilities (Utility) | 170000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 7940000 | Costs not yet available | Costs not yet available | Construction of Facilities (Contract) | 4433000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 20638000 | Costs not yet available | Costs not yet available | Estimated Total Cost | 31248000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available | Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 20638000 | Costs not yet available | Costs not yet available | Estimated Project Total | 31248000 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 67601000 | Costs not yet available | Costs not yet available | Reported on Monthly Construction Report | 20688000 | Costs not yet available | Costs not yet available

## 0PT39846
Project No. 0PT39846 - Abernathy - North - North Loop 345/115 kV Line - NTU Transmission Line Project (Dkt. 49151)
| Estimated cost included in CCN Application (Route 25) | Estimated cost once a route is approved and CCN granted (Route X) | Approximately 12 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 4871000 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 237000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 2720000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 13414000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 230000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 18124000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 39596000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 186000 | Costs not yet available | Costs not yet available
Estimated Project Total | 39782000 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 115000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 2141000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 21621000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 150000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 9340000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 33367000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 33367000 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 39782000 | Costs not yet available

## 0PT38573
Project No. 0PT38573 - Riverton - Sand Lake 345 kV Line Circuit Addition - Transmission Line Project (Phase 2)
| Estimated cost included in CCN Application | Estimated cost once a route is approved and CCN granted | Approximately 6 months after construction is complete
| Initial Estimated Project Costs: | Final Estimated Project Costs: | Final Actual Project Costs:
Right-of-Way and Land Acquisition | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Utility) | 1400000 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 1900000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 12500000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 0 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 13400000 | Costs not yet available | Costs not yet available
Estimated Total Cost | 29200000 | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 29200000 | Costs not yet available | Costs not yet available
| Substation Facilities | Substation Facilities | Substation Facilities
Right-of-Way and Land Acquisition | 0 | Costs not yet available | N/A
Engineering and Design (Utility) | 0 | Costs not yet available | Costs not yet available
Engineering and Design (Contract) | 155000 | Costs not yet available | Costs not yet available
Procurement of Material & Equipment (including Stores) | 665000 | Costs not yet available | Costs not yet available
Construction of Facilities (Utility) | 78000 | Costs not yet available | Costs not yet available
Construction of Facilities (Contract) | 287000 | Costs not yet available | Costs not yet available
Estimated Total Cost |  | Costs not yet available | Costs not yet available
Other (all costs not included in the above categories) | 0 | Costs not yet available | Costs not yet available
Estimated Project Total | 1185000 | Costs not yet available | Costs not yet available
Reported on Monthly Construction Report | 29200000 | Costs not yet available | Costs not yet available