## INTRO
Automated Water Loss Calculation
This calculation uses the Texas Water Development Board's Water Loss "Audit" Worksheet Format. It is recommended that you use "bottom-up"
methodologies whenever possible to gather the data in order to produce as precise a calculation as possible. Use of the TWDB's "Guidance Matrix for
Assigning Scores to Components of the Water Audit" is also recommended.
Begin by entering data into the Info Tracker spreadsheet in the yellow-highlighted cells in Column E.
Sources and Reports to gather the information from are shown in columns H & I, along with additional information in column J.
The amounts entered will show up in Column A of the spreadsheet.
Average Customer Meter Accuracy (cell A48) comes from the second spreadsheet named "Weighted Avg Customer Meter Accuracy Calculation".
That spreadsheet takes the amounts of water used by "billing type", once they are entered into the Info Tracker spreadsheet, and
calculates a weighted average accuracy figure once the meter accuracy ratings for each meter size (from testing reports) are entered.
The weighted average is automatically transferred into the data collection spreadsheet (cell A48).
Reliability Ratings are entered into the yellow-highlighted cells in Column L.
Use the Guidance Matrix for Assigning Scores to Components of the Water Audit provided by TWDB to determine the Reliability Ratings.
Information and Sources used to determine the ratings are shown in columns M & N for each item.
The Info Tracker spreadsheet prints out on three 11" x 17" sheets (Landscape Format)
The Report Format prints out on two 8-1/2" x 11" sheets (Portrait Format)
The information in the Report Format spreadsheet is automatically entered from the Info Tracker spreadsheet and includes a graph
to show the amounts of water by authorized consumption and water loss categories (the groupings on the graph are different than on
the TWDB report because they are intended to help management better understand where the water is being used.)
The Weighted Average Customer Meter Accuracy Calculation prints on one 8-1/2" x 11" sheet (Landscape Format)
The TWDB's Water Loss Calculation format was automated into a data collection spreadsheet
by Robert Elizondo and Robert Young, Office of the City Auditor, February 2009.
DO NOT USE WITHOUT PRIOR AUTHORIZATION BY OCA

## Info Tracker
January 1, 2017 to December 31, 2017
Assessment table
CALCULATED VALUES | TWDB Report Line Number | TWDB Water Loss Calculation Component Name | AWU Line Item Description | DATA INPUT COLUMN | Units | Source | Document(s) | Additional Information | Reliability Rating (Input into yellow highlighted cells) | Data used for Reliability Matrix judgment | Audit Year when Score Achieved | Source | 1 | 2 | 3 | 4 | 5
Austin Water | 1 | Water Utility Name | Same | Austin Water | N/A | Known | N/A
Dan Strub AW Pipeline Operations | 2 | Contact Name & Info | Same | Dan Strub AW Pipeline Operations | N/A | Known | N/A
January 1, 2017 to December 31, 2017 | 3 | Reporting Period | Same | January 1, 2017 to December 31, 2017 | N/A | Known | N/A
100% | 4 | Source Water Utilization | Same | 100% Surface Water |  | Known | N/A
975086 | 5a | Retail Population Served | Same | 975086 | POP | Marisa Flores-Gonzalez, Systems Planning | 2017_AW_Population_Estimate.xls spreadsheet | From AW Population Portal on SharePoint, July 1 population, with River Place subtracted
64055 | 5b | Wholesale Population Served | Same | 64055 | POP | Marisa Flores-Gonzalez, Systems Planning | 2017_AW_Population_Estimate.xls spreadsheet | From AW Population Portal on SharePoint, July 1 population, with River Place added
3847.81 | 6 | Utility's Length of Main Lines, miles |  | Column A summarizes the following 2 lines. |  |  |  |  | 5 | GIS system used to track system length along with components. | FY07 | Steve Hutton & Tracy Busby - AWU Systems Planning / GIS | Estimates only | Paper records in poor condition (no totals from year to year) | Good annual paper records | Electronic records and asset management system in good condition; includes system backup | GIS data and asset management database in agreement; random field checks validate database
|  |  | Transmission (16" or greater diameter) | 687.92 | Miles | Cara Cooke, GIS | GIS Water Statistics Report | Use # of miles of transmission lines for December of the reported fiscal year
|  |  | Distribution (less than 16" diameter) | 3159.89 | Miles | Cara Cooke, GIS | GIS Water Statistics Report | Use # of miles of distribution lines for December of the reported fiscal year
50 | 7 | Number of Wholesale Connections Served | Same | 50 | Conn. | Robert Rowan, Finance | email from Robert Rowan | Numbers of customers served kept on monthly basis, used fiscal year average
229071 | 8 | Number of Retail Connections Served | Same | 229071 | Conn. | Darrel Culberson, Finance | email from Robert Rowan or Darrel Culberson | Numbers of customers served kept on monthly basis, used calendar year average | 5 |  |  |  | Poor paper records of number of active and inactive service connections | Paper billing/connection information records in poor condition (no totals from year to year) | Good annual paper records, with reasonably accurate tracking of number of active and inactive connections, few or limited field verifications and audits | Electronic records in good condition and reviewed periodically; routine field verifications and audits allow more accurate active/inactive connection count | Well managed policies and procedures for active/inactive connection information in place; GIS data and asset management database in agreement; field verifications and audits prove database accuracy
59.5328 | 9 | Service Connection Density |  | Calculated (Line 8 div by Line 6)
77.3 | 10 | Average Yearly System Operating Pressure | Same | 77.3 | PSI | Joe Smith, Systems Planning | email from Joe Smith | GIS based algorithm within the AWU hydraulic model is used to calculate avg pressure throughout the system. | 5 | GIS based algorithm is used to calculate avg pressure throughout the system. Preliminary "district" testing done through SCADA system. | FY07 | Steve Hutton & Tracy Busby - AWU Systems Planning / GIS | Estimates only | Random pressure testing and averaging | Pressure testing through system standardized on annual basis | Combine pressure testing to calibrate hydraulic model to develop average system pressure | District testing and averaging matching data from hydraulic model
Gallons | 11 | Volume Units of Measure | Same | Gallons | N/A | Dan Strub, Pipeline Operations |  | All measurements converted to gallons by OCA
47592529787 | 12 | Water Volume from own Sources | Annual Usage from Distribution System | 47592529787 | Gals | Harrison Stokes, Pumping and Distribution | Annual pumping and usage data spreadsheet emailed |  | 4.5 | Fully metered; annual testing or electronic calibration - however, 17 of 27 meters are over 15 years old. | FY07 | Pumping and Distribution (Rick Coronado) | No meters; volume quantified by estimates only | Partially metered; several supply sources metered but not all | Fully metered; no regular testing or calibration of meters | Fully metered; partial testing or electronic calibration; no meters greater than 15 years old | Fully metered; annual electronic calibration and flow testing; no meters greater than 15 years old
0.98424 | 13 | Production Meter Accuracy (enter percentage) | Calculated Production Meter Accuracy | 0.98424 | Percent | Harrison Stokes - AWU Pumping and Distribution |  | Actual venturi meters are not tested. Using 98% for Ulrich and Davis, 100% for WTP4, and weighting those for the total amounts each plant produced. | 4.5 | Systematic testing of all meters on an annual basis; all meters over standards replaced or repaired and retested. | FY07 | Pumping and Distribution (Rick Coronado) | No testing of production meters; estimated adjustment used only as needed | Testing of production meters only where problems suspected | Systematic testing of meters; underperforming meters not always replaced | Systematic testing of all meters within at least a five-year cycle; all meters over standards replaced or repaired and retested | Testing of all production meters conducted in year of audit; replacement of all meters outside standard accuracy range
48354666261.4429 | 14 | Corrected Input Volume |  | Calculated (Line 12 div by Line 13)
689000 | 15 | Wholesale Water Imported | Same | 689000 | N/A | Teri Hawkins, Finance | copies of bills from Loop 360 Water Supply | Water purchased from Loop 360 WSC for Austin Country Club restrooms. | 4.5 | As per TWDB instructions | FY12 | Mark Mathis, TWDB | No meters; volume quantified by estimates only | Partially metered; several interconnections metered but not all | Fully metered; no regular testing or calibration | Fully metered; partial testing or electronic calibration; no meters greater than 15 years old | Fully metered; annual electronic calibration and flow testing; no meters greater than 15 years old
100 |  | Treated Purchased Water Meter Accuracy |  | 100 |  |  |  | Three meters measuring consumption from Loop 360 WSC not regularly tested. 100% accuracy assumed. | 2 |  | 2015 |  | No testing of production meters; estimated adjustment used only as needed | Testing of production meters only where problems suspected | Systematic testing of meters; underperforming meters not always replaced | Systematic testing of all meters within at least a five-year cycle; all meters over standards replaced or repaired and retested | Testing of all production meters conducted in year of audit; replacement of all meters outside standard accuracy range
2829946400 | 16 | Wholesale Water Exported | Same | 2829946400 | Gals | Financial Management (Darrel Culberson), with adjustments for water exported to River Place (does not show as wholesale water sold) | spreadsheet and emails from Judy Musgrove | Wholesale Water Exported is metered and billed. See Metered Consumption Report from CIS. | 2 |  | 2016 |  | No meters; volume quantified by estimates only | Partially metered; several supply sources metered but not all | Fully metered; no regular testing or calibration of meters | Fully metered; partial testing or electronic calibration; no meters greater than 15 years old | Fully metered; annual electronic calibration and flow testing; no meters greater than 15 years old
100 |  | Wholesale sales meter accuracy |  | 100 |  |  |  | Each meter tested at least annually, some every 6 months. 100% accuracy assumed. | 5 |  | 2015 |  | No testing of production meters; estimated adjustment used only as needed | Testing of production meters only where problems suspected | Systematic testing of meters; underperforming meters not always replaced | Systematic testing of all meters within at least a five-year cycle; all meters over standards replaced or repaired and retested | Testing of all production meters conducted in year of audit; replacement of all meters outside standard accuracy range
45525408861.4429 | 17 | System Input Volume |  | Calculated (Line 14 + Line 15 - Line 16)
37909491100 | 18 | Billed Metered |  | Column A summarizes the following 6 lines.
|  |  | Billed Consumption - Large Volume | 3753954300 | Gals | " | " | Large Volume Consumption History | 3.5 | Manual meter reads with edit checks of data; automated billing but no automated meter reading | FY07 | Austin Energy - Jerry Roberts, CIS Manager | No consumption data gathered; flat or fixed rate in use only | Manual meter reads and billings; no regular audits of customer billing data | Automated billing system; no annual checks of data | Automated meter reading and billing system; internally checked or checked by third party on less than annual basis | Automated meter reading and billing system audited by third party on annual basis
|  |  | Billed Consumption - Commercial | 9968717500 | Gals | " | " | Used the Inside City - Retail Commercial and the Outside City - Retail Commercial amounts from the report. |  | " |  | "
|  |  | Billed Consumption - Multifamily | 9590329100 | Gals | " | " | Inside City - Retail MultiFamily +Outside City - Retail MultiFamily |  | " |  | "
|  |  | Billed Consumption - Residential | 13964121100 | Gals | " | " | Inside City - Retail Residential + Outside City - Retail Residential |  | " |  | "
|  |  | Billed Consumption - Municipal | 616248900
|  |  | Billed Consumption - Other | 16120200 | Gals | Dan Pedersen, Water Conservation | email from Dan Pedersen | Customers paying reuse water rate for potable water until reuse water is available. There were 14 such customers in 2017. |  | " |  | "
4595913 | 19 | Billed Unmetered |  | Column A summarizes the following 4 lines.
|  |  | Billing Adjustments | 0 | Gals | Customer Services (Lora Schneider) | N/A | Backbilled charges for Damaged Meter, Slow/Stop Mtr, Stop Meter Report, Sys. Not Billing Codes. Is not data handling error, were recorded here, but are imputed with usage estimates and are currently included in billed metered totals. Customer Service will be working on recapturing these totals when the BASS tracking system is reinstated. | 4 | Entire system input measured by production meters; most consumption is metered, and all unmetered consumption is estimated and recorded at time of use. One district metered area in operation in Glenlake, with 3 others projected for FY15. | FY07 |  | Estimates of consumption used | Production meters used to determine consumption; all areas not monitored | Production meters used to determine consumption; all areas monitored | District meters (each 3,000 or fewer connections) used to determine consumption; no total coverage; rest use production meters | District meters (each covers 3,000 connections or less) throughout system used to determine consumption
|  |  | Special Billings | 324012 |  | Rosemary Ybarra | emailed spreadsheet | Special billings occur when a third party causes water to escape the distribution system, When the third party responsible is identified and billed for the water, this total moves from unbilled/unmeterd to billed unmetered.
|  |  | AFD - Fire Training | 123975 | Gals | Austin Fire Department (Frank Alvarez) | 2017 AFD unmetered water report | Hydrants at training academy are metered so amount used is captured in Billed Consumption Report - Commercial line. Additional training session usage away from training facilities provided from reports submitted by 94 stations. |  | Training academy has meters for whole complex. | FY07 | Bat. Chief Smith e-mail
|  |  | ARR - Unmetered | 2691160 | Gals | Leticia Molina | ARR 2017 Water Billing spreadsheet | Based on reported estimates from SWS per Fall 09 MOU. |  | See above.
|  |  | WPDR - Unmetered | 722861 | Gals | WPDR Field Operations Pete Reyes, Israel Benavides / Tammie Hagerud | WPD 2017 Water Use spreadsheet | Estimate based on number of fill-ups of 1,000 gallon trucks (Vactors) from various fire-hydrants (no truck meters) in accord with March 2010 MOU. |  | See above.
|  |  | PWD - Street Bridge Unmetered | 733905 | Gals | Tyler Steinbarger / Tammie Hagerud | Public Works 2017 Usage Estimate spreadsheets | Estimates based on number of times equipment tanks are refilled in accord with July 2011 MOU. |  | See above.
54684090 | 20 | Unbilled Metered |  | Column A summarizes the following 3 lines.
|  |  | Water used at inactive accounts | 0 | Gals | Customer Services (Lora Schneider) | emails from Lora Schneider | Some inactive accounts still have installed meters. Occasionally, water gets used at these addresses. Although it is theft, it is measured and may be recouped in some instances. AE is not collecting this data. | 2 |  | FY11 | Lora Schneider | No testing; estimates only | Testing only where problems suspected | Systematic testing of all meters; underperforming meters not always replaced | Systematic testing of all meters within at least a five-year cycle; all meters over standards replaced or repaired and replaced | Testing of all production meters conducted in year of audit; replacement of all meters outside standard accuracy range
|  |  | Downtown Austin Alliance | 67390 | Gals | Pipeline Operations (Dan Strub) | emails from David Thomas, DAA | Self reported totals from hydrant meter; water used for sidewalk cleaning downtown
|  |  | Metered Consumption - Utility | 54616700 | Gals | Financial Management (Darrel Culberson) | email from Darrel Culberson | This is the "Utility" line from consumption report (what AWU uses that is metered but not billed to it) - See note above to split out other City Dept usage similar to this. |  | Manual meter reads with edit checks of data; automated billing but no automated meter reading | FY07 | Austin Energy - Jerry Roberts, CIS Manager
92728311 | 21 | Unbilled / Unmetered |  | Column A summarizes the following 12 lines
|  |  | AWU - Pumping Maintenance | 453696 | Gals | Production Losses -Pumping and Distribution (Gregory Sundahl) | Reservoir overflows and maintenance spreadsheet | Includes only water used or drained for reservoir maintenance, not overflows. | 4 | Based on measured reservoir drawdowns. | FY11 | Rick Coronado Interview | Overall estimates throughout system | Partial estimates for some of variables; basic estimates for others | Estimates using formulae (for example, time x gallons per flush) for known events | Partial estimates using test data; other estimates using formulae for known number of events | Estimates using previous metered testing to determine overall estimated values
|  |  | AWU - Distrib System Maintenance |  | Gals | David Shannon - Water Loss Report (Maintenance) | Water Loss Crystal Report from Hansen | Used the totals for "intentional" use - meaning that water was NOT lost from breaks or leaks, but rather from intentional maintenance of distribution system. |  | Estimates using formulae for known events - no estimates using test data. | FY07 | Donn Lorbieski
|  |  | Intentional - SRs | 51785534 |  | David Shannon | Hansen
|  |  | Intentional - WOs | 30784838 |  | David Shannon | Hansen | Includes flushing WOs.
|  |  | Line Flushing | 1871841 |  | Dan Strub | 2017 Flushing Totals spreadsheet | Line flushing from newly constructed lines. Currently no automatic flushing devices are in use.
|  |  | AWU - Private Hydrant Testing | 698680 | Gals | Trebor Brown/Philip Fletcher - Water Protection | Query of WEIRS by Adam Smith | Work is underway to complete WEIRS database to identify owners of private hydrants, remind them of annual inspection/maintenance requirement, and track amount of water used for each inspection. |  | Estimates using formulae for known events - no estimates using test data. | FY07 | A.J. Hamilton, AWU
|  |  | AFD - Fire Suppression | 802316 | Gals | Austin Fire Department (Frank Alvarez) | 2017 AFD unmetered water report | AFD Water Usage is tracked from reports into database. |  | Estimates using formulae for known events combined with some test data. | FY11 | Bat. Chief Smith Interview
|  |  | AFD - City Hydrant Maint | 1502040 | Gals | " | 2017 AFD unmetered water report | New estimate in 2012 of 60 gals per hydrant, based on field observations and codified in an MOU with AFD. |  | Estimates using formulae for known events - no estimates using test data. | FY07 | Bat. Chief Smith Interview
|  |  | AFD - Hydrant Flow Tests | 687008 | Gals | " | 2017 AFD unmetered water report | New estimate in 2015 of 941 gallons per test, based on field observations and codified in an MOU with AFD. |  | Estimates using formulae for known events - no estimates using test data. | FY07 | Bat. Chief Smith Interview
|  |  | AFD - Standpipe Flow Test | 1245150 | Gals | " | 2017 AFD unmetered water report | Estimates based on flow measurements taken during tests
|  |  | Distribution system capacity expansion | 2897208 | Gals | Cara Cooke, GIS | Spreadsheet from Cara Cooke | As the distribution system grows, water is required to fill the expanded volume. The spreadsheet allows the calculation of the expanded capacity. |  | Not included in reliability matrix
38061499414 | 22 | Total Authorized Consumption |  | Calculated (Line 18 + Line 19 + Line 20 + Line 21)
7463909447.4429 | 23 | Water Losses |  | Calculated (Line 17 - Line 22)
0.97948 | 24 | Average Customer Meter Accuracy | Calculated Average Customer Meter Accuracy | Input into Column A (Cell A48) comes from Weighted Average Customer Meter Accuracy calculation spreadsheet. | Percent | Dan Strub, Pipeline Operations, and Darrel Culberson, Finance, | 2012 meter accuracy study | Updated accuracies resulting from meter accuracy study for 5/8", 3/4", 1", 1 1/2", and 2" meters. | 3 | Meter testing program exists thru 3" meters, but no current meter replacement program in place for small meters. Analysis of data in place except for small meters, but meter shop is keeping data in Hansen W/Os about age to calculate actual replacement age. | FY07 | Nowell Mojica interview | No testing or replacement; estimates only | Testing or replacement of 1 to 5% of meters in year or audit | Analysis of test data finds meters meeting specs, or testing and replacement of 5 to 10% of meters per year | Previous test data analyzed and all meters in specifications, or testing or replacement of 10 to 50% of all meters in year of audit | Previous test data analyzed and all meters in specifications, or testing or replacement of over 50% of all meters in year of audit
795185857.0174 | 25 | Customer Meter Accuracy Loss |  | Calculated ((Line 18 + Line 20 div by Line 24) - (Line 18 + Line 20))
0 | 26 | Systematic Data Handling Discrepancy | Billing System Data Handling Errors | 0 | Gals | Customer Services (Lora Schneider) | email from Lora Schneider | Data handling corrections are tanslated into water usage totals and included in billed meter usage under CC&B. | 4 | Automated system; internally checked on at least an annual basis (meter read edit reports) | FY07 | Lora Schneider | No review of billing system. | Automated system but no checks of data validity. | Automated system; less than annual checks of data. | Automated system; internally checked on at least annual basis. | Assessment of data handling errors conducted internally audited by third party on annual basis.
113813522.1536 | 27 | Unauthorized Consumption |  | Column A summarizes the following 2 lines.
|  | Unauthorized Consumption was figured as the estimate of water loss due to theft (incl hydrants and at customer connections incl tampering with meters, illegal taps, etc.) PLUS actual theft thru meter tampering, etc. | Estimated Theft | 113813522.1536 | Gals | Customer Services (Lora Schneider) | See Note | Theft from hydrants is not calculable due to lack of data - using the default of 0.25% of input volume from plants as allowed by TWDB in addition to theft contained in Admin Water category of billing adjustments spreadsheet. NOT using system input volume from raw water uptake, using calculated system input from plants. | 4 | Water theft study completed and monitoring and enforcement program begun. Using default value of 0.25% of input volume. | FY11 | Lora Schneider | Arbitrary volume estimates | Default of 0.25% of input volume | Number of events of each type evaluated; multiply by estimated gallons lost per event | Number of occurrences evaluated; monitoring and enforcement program started | Monitoring and enforcement program well established with analyzed losses less than 0.25% and declining from previous years
|  |  | Billing Adjustments for Open Meter Bypass & Direct Hookups | 0 | Gals | Customer Services (Lora Schneider) | email from Lora Schneider | Imputed totals for these categories of theft are now included in billed metered water usage. (Open Bypass, Direct Hook-Up, Tampering Codes) |  | Testing is done only where problems suspected. There is no systematic testing of all meters at present. | FY11 | Lora Schneider
908999379.171 | 28 | Total Apparent Losses |  | Calculated (Line 25 + Line 26 + Line 27)
77863939 | 29 | Reported Breaks and Leaks |  | Column A summarizes the following 3 lines.
|  |  | Water Loss from Hansen SRs | 390437 | Gals | Donn Lorbieski | Water Loss Report from Hansen | Totals for "non-intentional" use - meaning that water was lost from breaks or leaks, rather than from intentional maintenance of distribution system. | 5 | Visual leaks and breaks reported by customers and city staff; call-to-repair times known (greater than one week average); good records (based on the fact that w/o & s/r calcs are entered using the reported date in calc of amt of water lost) | 2015 | Donn Lorbieski interview | Arbitrary estimates; repairs of reported leaks and breaks not documented | Only visual leaks and breaks from customer calls fixed; no known duration before fixing cursory records | Visual leaks and breaks reported by customers and city staff; call-to-repair times known (greater than one week average); good records | Visual leaks and breaks reported by customers and city staff; call-to-repair times less than one week; computerized maintenance management system used to document leak repair trends | Visual leaks and breaks reported by customers and city staff; call-to-repair times less than two days; outstanding computer maintenance records track system deficiencies and repair crew performance
|  |  | Water Loss from Hansen WOs | 74729724 | Gals | Donn Lorbieski | See above. | See above.
|  |  | Reservoir System Overflows | 2743778 | Gals | Production Losses -Pumping and Distribution (Gregory Sundahl) | reservoir overflows and maintenance spreadsheet |  |  | Estimates using formulae for known events - no estimates using tests data. |  | Rick Coronado Interview
6477046129.2719 | 30 | Unreported Loss |  | Column A "back calculates" this value by deducting Reported Breaks & Leaks (Line 29) and Total Apparent Losses (Line 28) from Water Losses (Line 23) |  |  |  |  | 3 | Limited leak detection using basic sounding performed for a portion of the distribution system; some detailed records/database (Hansen W/Os) | 2014 | Various | If no active leakage control activities exist, unreported leaks are undetected and quantity is zero | Limited leak detection using basic sounding performed for a portion of the distribution system; no detailed records/database | Proactive leak detection using basic sounding, correlation and detailed leak detection records; one or more District Metered Areas in use | Proactive leak detection using basic sounding, correlation and detailed leak detection and asset condition records; detailed component analysis results | Fully integrated flow monitoring and leak detection program with continuous reporting and analysis of system leakage; integration with asset management, GIS and economic level of leakage
6554910068.2719 | 31 | Total Real Losses |  | Calculated (Line 29 + Line 30)
7463909447.4429 | 32 | Water Losses (Apparent + Real) |  | Calculated (Line 28 + Line 31) = Line 23
7611321848.4429 | 33 | Non-revenue Water (Water Losses + Unbilled Authorized Consumption |  | Calculated (Line 32 + Line 20 + Line 21)
10.8718 | 34 | Apparent Losses Normalized (Apparent Loss Volume / # of Retail Service Connections / 365) |  | Calculated (Line 28 / Line 8 / 365)
6554910068.2719 | 35 | Real Loss Volume |  | Same as Line 31 | Gals
4265785.2023 | 36 | Unavoidable Annual Real Losses (UARL) |  | Calculated from Table 3-2 | GPD
4.2099 | 37 | Infrastructure Leakage Index |  | Calculated (Line 35 / Line 36)
78.3807 | 38 | Real Losses Normalized (Real Loss Volume / # of Service Connections / 365) |  | IF LINE 9 > 32, then Calculated (Line 35 / (Line 7 + Line 8) / 365) |  |  |  | Equal to [(5.41 x length of main lines in miles) + (0.15 x number of service connections)] x average pressure in system
4667.2413 | 39 | Real Losses Normalized (Real Loss Volume / Miles of Main Lines / 365) |  | THIS DOES NOT APPLY TO AUSTIN IF LINE 9 < 32, then Calculated (Line 35 / Line 6 / 365)
908999379.171 | 40 | Total Apparent Losses |  | Same as Line 28
5.84 | 41 | Retail Price of Water | Calculated Average Retail Price | 5.84 | Per 1000 Gals | Darrel Culberson, Finance | email from Darrel, based on COS model | From Volume & Revenue worksheet in FY 2011 COS Model, System wide Volumetric Rate | 5 | Weighted average residential rate using volumes in each rate block | 2014 | Darrel Culberson - AWU Finance | Estimates only | Residential rate only | Weighted average residential rate using volumes in each rate block | Weighted average combination usage rate (includes residential commercial and industrial) | Third-party reviewed; weighted average combination usage rate (includes residential, commercial and industrial)
5308556.3744 | 42 | Cost of Apparent Losses |  | 59103
6554910068.2719 | 43 | Total Real Losses |  | Same as Line 31
0.373 | 44 | Variable Production Cost of Water | Calculated Production Costs | 0.373 | Per 1000 Gals | Li Yang and Songli Floyd, Budget and Accounting | Variable cost of water 2017 spreadsheet | Compiled along guidelines set by AW audit team | 4 | Internally audited wholesale, electric, and chemical costs | 2016 | Li Yang - AWU Finance | Estimates only | Extrapolated from evaluation of partial system electric and chemicals costs | Non-audited evaluation of total system electric and chemical costs | Internally audited wholesale, electric and chemical costs | Third-party audited wholesale, electric, chemical and detailed support costs annually
2444981.4555 | 45 | Cost of Real Losses |  | Calculated (Line 43 x Line 44)
79 | 46 | Total Assessment Score |  | Calculated (Adds Assessment Scale Scores at right)
7753537.8298 | 47 | Total Cost Impact of Apparent and Real Losses |  | Calculated (Line 42 + Line 45)
[9 empty] | 79 | TOTAL POINTS
TOTALS BELOW COME FROM THE CALCULATION ABOVE AND FEED THE GRAPH SHOWN AT THE BOTTOM OF THE REPORT FORMAT (on last spreadsheet)
45525408861.4429 |  | Total Pumpage
Broken down as follows
37914087013 | 83.28% | Total Billed
54684090 | 0.1201% | Utility Use - Buildings
84895909 | 0.1865% | Utility Use - Maintenance | 38061499414 | Authorized Usage
802316 | 0.001762% | Fire Suppression
4132878 | 0.009078% | Fire Hydrant/System Testing & Maint
2897208 | 0.007642% | System Expansion
2743778 | 0.006027% | Loss - Overflows
795185857.0174 | 1.747% | Loss - Customer Meter Inaccuracy
0 | 0% | Loss - Data Handling Errors | 7463909447.4429 | Water Loss
113813522.1536 | 0.25% | Loss - Theft
75120161 | 0.165% | Loss - Reported Breaks & Leaks
6477046129.2719 | 14.23% | Loss - Unreported Breaks & Leaks
45525408861.4429 | 100% | Total | 45525408861.4429 | Total
|  |  | 0 | Diff from Column A Totals
0

## Wghtd Avg Cust Mtr Accrcy Calc
WEIGHTED AVERAGE CUSTOMER METER ACCURACY CALCULATION | [6 empty] | For: | January 1, 2017 to December 31, 2017
(Input from Tests)
|  | Totals from Info Tracker |  | % of total | Meter Sizes | Meter Accuracy |  | Weighted Avg Meter Accuracy
| Wholesale | 2829946400 | Gals | 6.417% | 10" - 8" | 98% |  | 6.288%
| Industrial | 3753954300 | Gals | 8.512% | 8" - 6" | 98% |  | 8.342%
| Commercial | 9590329100 | Gals | 21.75% | 6" - 3" | 98% |  | 21.31%
| Multifamily | 13964121100 | Gals | 31.66% | 3" - 1" | 98% |  | 31.03%
| Residential | 13964121100 | Gals | 31.66% | 1" - 5/8" | 97.7% | ** | 30.93%
|  | 44102472000 | TOTAL |  |  |  |  | 97.91% | Average Customer
Meter Accuracy
[5 empty] | ** | This rate estimated
based on best info
| Meter size | gallons |  | % of total |  | meter accuracy |  | Weighted Avg Meter Accuracy
| 5/8" | 13536501500 |  | 33.15% |  | 97.66% |  | 32.38%
| 3/4" | 2962080000 |  | 7.255% |  | 98.9% |  | 7.175%
| 1" | 1858870100 |  | 4.553% |  | 97.37% |  | 4.433%
| 1 1/4" | 0 |  | 0% |  | 98% |  | 0%
| 1 1/2" | 2126086300 |  | 5.207% |  | 98.27% |  | 5.117%
| 2" | 5260180700 |  | 12.88% |  | 98.09% |  | 12.64%
| 3" | 2147216200 |  | 5.259% |  | 98% |  | 5.154%
| 4" | 2951224600 |  | 7.228% |  | 98% |  | 7.084%
| 6" | 3896539900 |  | 9.543% |  | 98% |  | 9.352%
| 8" | 2230425300 |  | 5.463% |  | 98% |  | 5.353%
| 10" | 3052377300 |  | 7.476% |  | 98% |  | 7.326%
| 12" | 808492000 |  | 1.98% |  | 98% |  | 1.941%
|  | 40829993900 |  | 100% |  |  |  | 97.95% | Average Customer
Meter Accuracy
There is a difference between total gallons by meter size and total gallons by customer class because customer class has had billing adjustments subtracted from it.
-2396769094.5
38147326129

## Report Format
AW Water Loss Calculation
for: | January 1, 2017 to December 31, 2017 | [5 empty] | Assessment Values
| Line # |  | Field Description (from TWDB Water Audit Reporting Form) | Value |  |  | Score | Contact | Notes | Max Points
A. | WATER UTILITY GENERAL INFORMATION
| 1 |  | Water Utility Name: | Austin Water
| 2 |  | Contact:
|  |  | Name | Dan Strub AW Pipeline Operations
|  |  | Telephone # | (512) 972-0349
|  |  | Email Address | dan.strub@austintexas.gov
| 3 |  | Reporting Period: | January 1, 2017 to December 31, 2017
| 4 |  | Source Water Utilization, percentage:
|  |  | Surface Water % | 100%
|  |  | Groundwater % | 0%
| 5 |  | Population Served:
|  |  | a. Retail Population Served | 975086 |  |  |  | Randy Alexis | via Teresa Lutes Randy provided a spreadsheet
|  |  | b. Wholesale Population Served | 64055 |  |  |  | Randy Alexis | via Teresa Lutes Randy provided a spreadsheet | System Data Points
| 6 |  | Utility’s Length of Main Lines, miles | 3847.81 |  |  | 5 | Tracy Busby | based on Sept 08 numbers reported | 5
| 7 |  | Number of Wholesale Connections Served | 50 |  |  |  | Denise McDonald | via Darrel Culberson / as of September 08
| 8 |  | Number of Retail Service Connections Served | 229071 |  |  | 5 | Denise McDonald | via Darrel Culberson / as of September 08 | 5
| 9 |  | Service Connection Density (Number of retail service connections/Miles of main lines) | 59.5328 | conn/mile
| 10 |  | Average Yearly System Operating Pressure (psi) | 77.3 | psi |  | 5 |  |  | 5
| 11 |  | Volume Units of Measure (check one): acre-ft million gallons thousand gallons gallons | Gallons
B. | SYSTEM INPUT VOLUME | [8 empty] | Water Supplied Points
| 12 |  | Water Volume from own Sources | 47592529787 | gals |  | 4.5 | Rick Coronado | Email sent 4/16 | 5
| 13 |  | Production Meter Accuracy (%) | 98.42% | pct. |  | 4.5 |  |  | 5
| 14 |  | Corrected Input Volume | 48354666261.4429 | gals
| 15 |  | Wholesale Water Imported | 689000 | gals |  | 4.5 |  |  | 5
|  |  | Wholesale Water Purchased Meter Accuracy |  |  |  | 2 |  |  | 5
| 16 |  | Wholesale Water Exported | 2829946400 | gals | 5.852% | 2 | Drema Gross | "keep # 0" | 5
|  |  | Wholesale Water Exported Meter Accuracy |  |  |  | 5 |  |  | 5
| 17 |  | System Input Volume | 45525408861.4429 | gals | 100%
C. | AUTHORIZED CONSUMPTION | [8 empty] | Authorized Consumption Points
| 18 |  | Billed Metered | 37909491100 | gals | 83.27% | 3.5 | Drema Gross | Consumption per Capita Spreadsheet | 5
| 19 |  | Billed Unmetered | 4595913 | gals | 0.0101% | 4 |  |  | 5
| 20 |  | Unbilled Metered (amount used at AWU buildings/facilities) | 54684090 | gals | 0.1201% | 2 |  |  | 5
| 21 |  | Unbilled Unmetered (amount used by other city Departments) ** | 92728311 | gals | 0.2037% | 4 |  |  | 5
| 22 |  | Total Authorized Consumption | 38061499414 | gals | 83.6%
NOTES:
|  | ** | Most of the water used by other City Departments is included in line 18.
D. | WATER LOSSES
| 23 |  | Water Losses (Line 17 minus Line 22) | 7463909447.4429 | gals | 16.4%
E. | APPARENT LOSSES | [8 empty] | Apparent Losses Points
| 24 |  | Average Customer Meter Accuracy % | 97.95% | pct. |  | 3 |  |  | 5
| 25 |  | Customer Meter Accuracy Loss | 795185857.0174 | gals | 1.747%
| 26 |  | Systematic Data Handling Discrepancy | 0 | gals | 0% | 4 |  |  | 5
| 27 |  | Unauthorized Consumption | 113813522.1536 | gals | 0.25% | 4 |  |  | 5
| 28 |  | Total Apparent Losses | 908999379.171 | gals | 1.997%
F. | REAL LOSSES | [8 empty] | Real Losses Points
| 29 |  | Reported Breaks and Leaks (Estimated volume of leaks and breaks repaired during the audit period) | 77863939 | gals | 0.171% | 5 |  |  | 5
| 30 |  | Unreported Loss (Includes all unknown water loss) (Calculated as Water Losses - Total Apparent Losses - Reported Breaks & Leaks) | 6477046129.2719 | gals | 14.23% | 3 | (calculated) |  | 5
| 31 |  | Total Real Losses (Line 29, plus Line 30) | 6554910068.2719 | gals | 14.4%
| 32 |  | Water Losses (Apparent + Real) (Line 28 plus Line 31) should = Line 23 | 7463909447.4429 | gals | 16.4%
| 33 |  | Non-revenue Water (Water Losses + Unbilled Authorized Consumption) (Line 32, plus Line 20, plus Line 21) | 7611321848.4429 | gals | 16.72%
G. | TECHNICAL PERFORMANCE INDICATOR FOR APPARENT LOSS
| 34 |  | Apparent Losses Normalized (Apparent Loss Volume/# of Retail Service Connections/365) | 10.8718 | gals/conn/day
H. | TECHNICAL PERFORMANCE INDICATORS FOR REAL LOSS
| 35 |  | Real Loss Volume (Line 31) (shown as total gallons/year) | 6554910068.2719 | gals | 14.4%
| 36 |  | Unavoidable Annual Real Losses, volume (calculated) in MGD | 4265785.2023 | MGD | 3.42%
| 37 |  | Infrastructure Leakage Index (calculated) (Equals real loss volume (div by 365) divided by unavoidable annual real losses) | 4.2099
| 38 |  | Real Losses Normalized (Real Loss Volume/# of Service Connections/365) (This indicator applies if service connection density is greater than 32/mile) | 78.3807 | gals/conn/day |  |  |  |  | Austin's Serv Conn Density > 32/mile so this calc is used
| 39 |  | Real Losses Normalized (Real Loss Volume/Miles of Main Lines/365) (This indicator applies if service connection density is less than 32/mile) | 4667.2413 | gals/mile/day |  |  |  |  | This one not used
I. | FINANCIAL PERFORMANCE INDICATORS
| 40 |  | Total Apparent Losses (Line 28) | 908999379.171 | gals |  |  |  |  | Cost Data Points
| 41 |  | Retail Price of Water | 5.84 | Per 1,000 Gals |  | 5 |  |  | 5
| 42 |  | Cost of Apparent Losses (Apparent loss volume multiplied by retail cost of water - Line 40/1000 x Line 41) | 5308556.3744
| 43 |  | Total Real Losses (Line 31) | 6554910068.2719 | gals
| 44 |  | Variable Production Cost of Water* (*Note: In case of water shortage, real losses might be valued at the retail price of water instead of the variable production cost.) | 0.373 | Per 1,000 Gals |  | 4 |  |  | 5
| 45 |  | Cost of Real Losses (Real loss multiplied by variable production cost of water - Line 43/1000 x Line 44) | 2444981.4555
| 46 |  | Total Assessment Score |  |  |  | 79 |  |  | 100
| 47 |  | Total Cost Impact of Apparent and Real Losses | 7753537.8298
79%
|  | LEGEND: | [7 empty] | Percentage of points
|  |  | = calculated item | [6 empty] | available
= reliability assessment required
= Update Needed
Legend:
* Category
* Total Gallons This Year
* % of Corrected System Input Value