## Slide 1: Water Loss Primer
Dan Strub
Water Loss Control Program Manager

## Slide 2: Some Water Loss Basics
Real Losses = water lost from the distribution system through leakage
  Includes water recorded as lost in WOs and SRs for leaks
Apparent Losses = water produced and not measured, but is still used
Includes meter inaccuracies, theft, billing errors

## Slide 3: Annual Water Loss Audit
Submitted to TWDB by May 1
Calendar year timeframe
Format created by TWDB, based on AWWA audit
Enhanced by Austin Water refinements
Data from 27 sources
Undergoes QA/QC, reviewed for changes, anomalies, trends
Each data line has a validity score to encourage rigorous data collection and use of BMPs

## Slide 4: What Do We Measure?
System Input Volume
Imports and Exports
Billed Metered
Unbilled Metered
Unbilled Metered
Unbilled Unmetered
Meter accuracy
Flushing and maintenance
Overflows
Theft and billing errors
Notes: If water leaves the distribution system, we want numbers

## Slide 5: Audit Outputs
Total gallons lost
Infrastructure Leakage Index
Losses per connection per day
Cost of Real Losses
Cost of Apparent Losses
Total cost of losses

## Slide 6: What Is the ILI?
Infrastructure Leakage Index is the best measure of distribution system efficiency
real losses
unavoidable real losses
Unavoidable Real Losses = How much water is going to be lost in a perfect system, calculated by a formula

## Slide 7: What Does the Score Mean?
>5.0: Low costs to increase supplies, enough system capacity to meet long-term needs
3.0-5.0: Moderate costs to increase supplies, enough system capacity to meet short-term needs
1.0-3.0: A water utility that has limited water supplies, little ability to increase revenues, or high costs to increase supply

## Slide 8: How Are We Doing?
Year | ILI
2013 | 2.72
2014 | 3.17
2015 | 3.88
2016 | 3.31
2017 | 4.21
2018 preliminary | 4.00

## Slide 9
Chart: Water Loss Trend
| FY 12 | FY13 | 2014 | 2015 | 2016 | 2017 | 2018
Infrastructure Leakage Index | 2.0552 | 2.7184 | 3.1692 | 3.883 | 3.309 | 4.21 | 4
Goal | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7

## Slide 10: Early Efforts
Second shift of operations crews to fix leaks faster
All leaks classified as Priority 1
Leak Detection
MOUs with other City Departments that use unmetered water
Improvements in data collection and QA/QC

## Slide 11: What Are We Doing Now?
Leak detection
Renewing Austin
District Metered Areas (DMAs)
AMI
Meter accuracy study
Production meter accuracy testing
Changing new meter specs