# ADDENDUM OF ONCOR ELECTRIC DELIVERY COMPANY TO ITS

# SERVICE QUALITY REPORT FOR THE 2019 REPORTING YEAR

The Public Utility Commission of Texas (Commission), in Ordering Paragraph No. 5 in its April 18, 2019 Order in Docket No. 48841, Agreed Notice of Violation and Settlement Agreement Relating to Oncor Electric Delivery Company’s Violation of PURA § 38.005 and 16 TAC 25.52, Concerning Reliability and Continuity of Service, requires Oncor Electric Delivery Company LLC (Oncor) to “file a report regarding actions to bring feeders that are found to be in violation of any of its system-wide service quality standards for two or more consecutive years into compliance with the Commission's service quality standards, and this report must be filed as an addendum to Oncor's required annual service quality reports, as prescribed by 16 TAC § 25.81.”  This Addendum is filed to comply with that requirement.

Oncor would stress that its capital and maintenance projects remain fluid over the course of a calendar year, and the projects set out below that are designated as “planned” or “scheduled” are subject to change and may not take place in  the stated year  due to changes in customer loading on the feeder, the impact of storms and storm repairs locally and across the Oncor system, load growth elsewhere on the Oncor system, equipment repairs/replacement elsewhere on the Oncor system, and other factors.

Eight Consecutive Years (Seven Year Violation)

  - DHIDE-2821

    - This feeder is 71.9 miles long and currently serves 105 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 10% vegetation density.

    - The feeder violation is due to SAIDI. In 2019, multiple lightning caused events during local storms were the primary reason.

    - In 2019, a system improvement project installed voltage regulators to provide voltage support on the feeder.  Two distribution automation projects were started to replace single operation line fuses at a key locations on the feeder with vacuum reclosing fuses.  One of these projects was completed in the fourth quarter and the other is nearing completion in 2020.

  - BARNW-4521

    - This feeder is 51.9 miles long and currently serves 89 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 10% vegetation density.

    - The feeder violation is due to SAIDI.  An underground primary cable fault, multiple lightning and unknown caused events during local storms were the primary reasons.

    - A substation improvement project completed in late 2018 added a new 28MVA Bank #2 with two new feeder breakers.  After these new feeders were placed in service in early 2019, some of the load from this feeder (BARNW-4521) was transferred to one of the new feeders (BARNW-4522).  Another substation improvement project was started in 2019 and is in progress that is adding a new 47MVA Bank #3 substation transformer with two new feeder breakers to handle the increasing load growth in the area.  The addition of the two new banks and four new feeders will allow each feeder to have less overhead exposure to lightning and wind by decreasing the miles and the number of customers served per feeder.  To date, the length of this feeder has been reduced from 64.7 miles in 2018 to 51.9 miles in December-2019.  In 2020, system improvement projects to reconductor about 48,000 feet (about 9.1 miles) of the existing feeder by replacing the existing small wire with new larger wire, new stronger poles where needed, and new fiberglass crossarms is scheduled.  Also, in 2020 a distribution automation project to upgrade an existing oil-filled recloser at a key location on the feeder with an electronic vacuum recloser equipped with SCADA (Supervisory Control and Data Acquisition) for remote monitoring and control is planned.

  - RYLTY-1411

- This feeder is 91.6 miles long and currently serves 110 customers in rural West Texas.  The customers are almost exclusively oil and gas field-related.  The terrain is low scrub brush and desert sands with limited paved road access and 25% vegetation density.

- The feeder violation is due to SAIDI.  In 2019, multiple lightning caused events during local storms were the primary reason.

- In 2019, reactive maintenance projects replaced damaged poles, crossarms, and conductor after patrols of the feeder during and after adverse weather events. A planned maintenance project replaced deteriorated poles, crossarms, conductor, and ground wires that were identified by patrols of the feeder in the previous year.  A distribution automation project replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses.  A system improvement project at the substation is planned for 2021 that will upgrade the existing substation transformer and associated facilities.

Seven Consecutive Years (Six Year Violation)

  - SBEAN-6011

    - This feeder is 24.3 miles long and currently serves 56 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% tree density.

    - The feeder violations are due to SAIDI (Six Year) and SAIFI (One Year).  In 2019, there were multiple unknown, swinging conductor, and lightning caused events during adverse weather.

    - In 2019, system improvement projects installed capacitor banks at multiple locations on the feeder to improve voltage support.  Two distribution automation projects replaced single operation line fuses at key locations on the feeder with vacuum reclosing fuses.  A system improvement project to reconductor about 13,000 feet (about 2.5 miles) of the existing feeder by replacing the existing small wire with new larger wire, new stronger poles where needed, and new fiberglass crossarms is in progress and is near completion in the first quarter of 2020.  Also, a system improvement project at the substation was started in 2019 that is installing a new 46.7MVA Bank #2 transformer with two new feeder breakers.  The existing Bank #1 only has two feeders (6011 and 6021).  These additional feeders should allow more load diversity among the four feeders and provide an alternate source capability to this and the other existing feeder.  This project is scheduled to be completed in 2020.

  - BRNSY-1211

    - This feeder is 64.8 miles long and currently serves 111 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violation is due to SAIDI. In 2019, lightning caused events mostly on one day in May were the primary reason.

    - In 2019, reactive maintenance projects replaced damaged and deteriorated poles, crossarms and other facilities after patrols of the feeder mostly after adverse weather events.  A system improvement project at the substation was completed that upgraded the existing substation transformer Bank #1 to an increased load capacity of 28.0 MVA with three feeder breakers instead of only two, and a new control center configured for the newest Suburban IV substation design.  The added feeder breaker will allow the existing two feeders to be reconfigured in 2020.  Two distribution automation projects replaced single operation line fuses at key locations on the feeder with vacuum reclosing fuses and corrected recloser to fuse timing coordination.  A detailed analysis of the locations and causes of outage events on the feeder in 2018 and in previous years resulted in a project to closely inspect a targeted 8.7 mile section of the feeder.  The poles and other facilities in this section were inspected by the OSMOSE pole inspection contractor to identify deteriorated facilities for repair or replacement.  Thirty-three (33) poles that were identified for restoration by installing pole trusses was completed in 2019.  A planned maintenance project is scheduled to be worked in 2020 that will replace the deteriorated poles that could not be trussed as well as deteriorated crossarms that were identified by these inspections in 2019.

Six Consecutive Years (Five Year Violation)

  - GSMTH-1732

    - This feeder is 38.4 miles long and currently serves 29 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violation was due to SAIDI.  In 2019, multiple lightning caused events during adverse weather were the primary reason.

    - In 2019, a reactive maintenance project replaced two spans of damaged wire.  A distribution automation project replaced single operation line fuses at key locations on the feeder with vacuum reclosing fuses.  A system improvement project built a new substation (Pumper) about eight miles from GSMTH with a new 28.0MVA transformer and three new feeder breakers.  This project was designed in the previous year and construction was completed at the new substation in the second quarter of 2019.  The purpose of this project was to provide distribution grade service to a large customer in the area and also to establish feeder ties with adjacent feeders and transfer some load from these feeders to one of the new feeders out of the new substation.  An associated project has been designed, materials ordered, and construction scheduled to establish these feeder ties in 2020.  When this later project is completed about 3.0 MW of load on GSMTH-1732 will be transferred to the new feeder out of the new substation.  When the transfer is completed the primary miles of exposure on the feeder will be reduced about 30 percent from thirty-eight (38) miles to about twenty-seven (27) miles.  Also, the feeder tie with the new feeder will provide an alternate source capability when there is an outage and temporary load transfer between the feeders is possible.  A distribution automation project is planned for 2021 that will replace an existing oil-filled recloser at a key location on the feeder with an electronic vacuum recloser equipped with SCADA for remote monitoring and control single operation line fuses.

Five Consecutive Years (Four Year Violation)

  - BLKRV-8311

    - This feeder is 58.4 miles long and currently serves 56 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The violation was due to SAIDI (Four Year) and SAIFI (One Year).  In 2019, outage events were caused by downed overhead conductor and lightning during adverse weather.  Also, several unknown cause and one public vehicle caused event occurred.  This substation is about 100 miles from the nearest service center so the outage durations are naturally of longer duration due to required drive time and the time to locate the cause of the outage and then restore power to the customers.

    - A detailed analysis of the locations and causes of outage events on the feeder in 2018 and in previous years resulted in a project to closely inspect a targeted 7.7 mile section of the feeder.  The poles and other facilities in this section were inspected by the OSMOSE pole inspection contractor to identify deteriorated facilities for repair or replacement.  Six poles were identified for restoration by installing pole trusses and this work was completed in the first quarter of 2019.  The other maintenance work identified on this section was completed in the third quarter.  An analysis of where swinging conductor events were occurring was made and a project to install mid-span spacers on several long spans of overhead primary was completed in the third quarter.  Multiple system improvement projects to install new capacitor banks for better voltage support on the feeder were completed during the year.  Seven additional system improvement projects were started during the year to rebuild about 68,600 feet (about 13.0 miles) of the existing feeder by installing new larger wire, removing one-hundred ninety-four (194) older poles and crossarms and installing three-hundred twenty-seven (327) new stronger poles with new fiberglass crossarms.  Two projects were completed in 2019 (about 19,000 feet), two were completed in early 2020 (about 17,000 feet), and three are in progress and scheduled for completion in 2020 (about 32,000 feet).  A system improvement project is planned for 2020 to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.

  - ELMAR-3222

    - This feeder is 40.5 miles long and currently serves 60 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violations were due to SAIDI (Four Year) and SAIFI (Two Year).  In 2019, multiple unknown and lightning caused events - mostly during adverse weather - were the primary reason. This substation is about 60 miles from the nearest service center so the outage durations are naturally of longer duration due to required drive time and the time required locating the cause of the outage and then restoring power to the customers.

    - In 2019, a system improvement project rebuilt about 14,100 feet (about 2.7 miles) of the existing feeder with new poles, crossarms, and larger wire.  About forty-five (45) older and deteriorated poles were removed and replaced with about eight-two (82) new taller and stronger poles with new fiberglass crossarms.  Another system improvement project replaced an older oil-filled hydraulic recloser with an electronic vacuum recloser equipped with SCADA for remote monitoring and control and installed new voltage regulators to improve voltage support on the feeder.  Two more projects during the year installed new capacitor banks for added voltage support on other sections of the feeder.  A system improvement project is planned for 2020 to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.

Three Consecutive Years (Two Year Violation)

  - COYAN-6311

    - This feeder is 26.0 miles long and currently serves 47 customers in West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violation is due to SAIDI.  In 2019, multiple lightning and unknown caused events - mostly during adverse weather - were the primary reason.

    - In 2019, reactive maintenance projects replaced damaged crossarms and overhead conductor identified during feeder patrols mostly during and after adverse weather events.  A distribution automation project replaced an older oil-filled hydraulic recloser with an electronic vacuum recloser equipped with SCADA for remote monitoring and control.  Another system improvement project installed voltage regulators to improve voltage support on the feeder.  A system improvement project is planned for 2021 to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.

  - KYSTN-1021

    - This feeder is 36.7 miles long and currently serves 37 customers in West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violation is due to SAIDI. In 2019, three poles that went down during adverse weather on one day in September were the primary reason. The soil in the area was water saturated and required the use of a dozer to move equipment to and from their locations in order to install the new poles.

    - In 2019, reactive maintenance projects replaced damaged poles and other damaged facilities identified during feeder patrols mostly after adverse weather events.  A system improvement project installed two new capacitor banks for added voltage support on sections of the feeder.  Two system improvement projects were started to rebuild about 19,200 feet (about 3.6 miles) of the existing feeder by removing the older deteriorated poles, wood crossarms, and small wire and installing new taller and stronger poles with new fiberglass crossarms and new larger wire. Both of these projects are scheduled to be completed in 2020.  A system improvement project at the substation is planned for 2022 that will add a new Bank #2 and additional feeder breakers which will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.

  - COYNW-8151

    - This feeder is 45.8 miles long and currently serves 62 customers in West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violations were due to SAIDI (Two Year) and SAIFI (Two Year).  In 2019, there were multiple lightning, swinging conductor, downed overhead conductor, metering, and unknown caused outage events.  Also, an electronic vacuum recloser control failure and a short duration high load condition both locked out the feeder breaker causing the high SAIFI.

    - In 2019, a system improvement project at the substation was completed that installed a new 28MVA Bank #2 with two new feeder breakers.  The increased load capacity and two additional feeder breakers will allow for the load on the two existing feeders to be split-up among four feeders and will also make backstand options possible.  Reactive maintenance projects replaced a damaged pole, two spans of damaged overhead wire and other damaged facilities identified during feeder patrols mostly after adverse weather events.  A system improvement project installed a new capacitor bank for improved voltage support on the feeder.  A system improvement project rebuilt about 13,500 feet (about 2.6 miles) of the feeder by removing the older deteriorated poles, wood crossarms, and small wire and installing new taller and stronger poles with new fiberglass crossarms and new larger wire.  Three other system improvement projects will convert about 10,000 feet (about 1.9 miles) of the existing feeder from 12.5KV to 22KV and install a larger 22/12KV auto transformer and replace various transformers and other facilities due to the operating voltage change. These projects are scheduled to be completed in 2020.  A system improvement project is planned for 2021 to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.  In addition, a distribution automation project is planned for 2021 that will replace an existing oil-filled recloser at a key location on the feeder with an electronic vacuum recloser equipped with SCADA for remote monitoring and control.

  - VESTS-3111

    - This feeder is 18.4 miles long and currently serves 47 customers in West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 10% vegetation density.

    - The feeder violations were due to SAIDI (Two Year) and SAIFI (Two Year).  In 2019, multiple outage events - mostly in the month of January - caused by downed overhead conductor and swinging conductor during adverse weather were the primary reasons.

    - System improvement projects started in the previous year were completed in early 2019.  These projects rebuilt about 21,700 feet (about 4.1 miles) of the existing feeder by removing the older deteriorated poles, wood crossarms, and smaller wire and installing new taller and stronger poles with new fiberglass crossarms and new larger wire.  Two system improvement projects are scheduled for 2020 that will rebuild about 1,000 feet of the existing feeder by installing new larger wire, new stronger poles where needed, and new fiberglass crossarms.  A system improvement project at the substation is in progress that is replacing the existing substation transformer Bank #1 with a 28.0 MVA transformer and adding a third feeder breaker.  The addition of the new feeder will allow this feeder to be reconfigured to minimize exposure and the new feeder can provide an alternate source during future outage events.

  - RSKMN-3057

    - This feeder is 65.9 miles long and currently serves 1,128 customers in East Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 100% vegetation density.

    - The feeder violation is due to SAIDI.  In 2019, a public vehicle hit and damaged a pole in January, a large tree top fell across overhead primary conductor in October, and a logging truck knocked three spans of overhead primary conductor off their insulators in November.  These were the primary reasons for this feeder to have a high SAIDI.

    - In 2019, reactive maintenance projects replaced damaged poles and conductor identified during patrols of the feeder mostly after adverse weather events.  Reactive tree trimming was done by vegetation management during the year after adverse weather events.  A system improvement project replaced a section of overloaded conductor and improved voltage support on the feeder.  A distribution automation project replaced single operation line fuses at key locations on the feeder with vacuum reclosing fuses.  A system improvement project was started in 2019 to convert sections of the feeder serving the city of Alto from the older 2,400 Delta voltage to the newer 24.9 kV distribution voltage.  This project replaced about thirty-nine (39) older deteriorated poles and crossarms, forty-two (42) older transformers and installed three new step-down transformers and upgraded several voltage regulators.  This project is nearing completion in 2020.  Another distribution automation project is planned for 2020 to replace single operation line fuses at key locations on the feeder with vacuum reclosing fuses.  A distribution automation project is planned for 2021 to upgrade an existing older oil-filled hydraulic recloser with a new electronic vacuum recloser equipped with SCADA for remote monitoring and control.  Another system improvement project planned for 2021 will establish a feeder tie with an adjacent feeder that can provide an alternate source during future outage events.

Two Consecutive Years (One Year Violation)

  - WELCH-4911

    - This feeder is 13.0 miles long and currently serves 22 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 50% vegetation density.

    - The feeder violations were due to both SAIDI (One Year) and SAIFI (One Year).  In 2019, swinging conductor during adverse weather on one day in July downed four poles and broke several crossarms.  In October, on the same day downed overhead primary conductor and unknown caused events occurred.  Lightning caused events during adverse weather also were another reason.

    - In 2019, reactive maintenance projects replaced four poles, several crossarms and downed primary conductor damaged during adverse weather events.

  - GASLD-4211

    - This feeder is 71.6miles long and currently serves 90 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violation is due to SAIDI.  In 2019, an unknown caused event in May and an overhead primary conductor down in December were the primary reasons.

    - In 2019, reactive maintenance projects replaced several deteriorated poles identified during feeder patrols and overhead primary conductor damaged during adverse weather.  A distribution automation project to replace single operation line fuses at key locations on the feeder with vacuum reclosing fuses is scheduled for 2020.

  - MKNGB-5321

    - This feeder has 25.1 overhead miles, 9.0 underground miles, and currently serves 444 customers in West Texas.

    - The feeder violation is due to SAIDI.  In 2019, a lightning caused event in July and several unknown caused events during the year were the primary reasons.

    - In 2019, a reactive maintenance project replaced deteriorated overhead primary conductor identified during a patrol of the feeder.  A system improvement project established a new substation (HISKY) with two feeders northwest of the MKNGB substation.  A feeder tie was installed between the new feeder HISKY-8821 and MKNGB-5321.  This new feeder tie will provide backstand capability for both feeders and in the event that one feeder has an outage and the other doesn’t, it is possible to close-in this tie and pick up some of the load from the feeder that is out of service.  A planned vegetation management project to trim the trees on the mainline sections of the feeder is scheduled for 2020.

  - CRNES-2721

    - This feeder is 35.7 miles long and currently serves 77 customers in West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 25% vegetation density.

    - The feeder violations are due to SAIDI (One Year) and SAIFI (One Year). In 2019, an overhead conductor off insulator-caused event in March and multiple unknown-caused events in June and July were the primary reasons.

    - In 2019, a distribution automation project replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses. A system improvement project at the substation installed a new Bank #2 28.0MVA transformer with a new feeder breaker to relieve overload conditions on the existing Bank #1 and its two feeders.  Two system improvement projects rebuilt about 32,000 feet (about 6.0 miles) of the existing feeder by installing new larger wire, new stronger poles where needed, and new fiberglass crossarms.  These projects were completed in the third quarter of 2019.

  - SBEAN-6021

    - This feeder is 76.5 miles long and currently serves 175 customers in West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 25% vegetation density.

    - The feeder violation is due to SAIDI. In 2019, a swinging conductor caused event and pole down event both in April, and an overhead conductor down event in September were the primary reasons

    - In 2019, a system improvement project at the substation installed a new Bank #2 46.7MVA transformer with two new feeder breakers.  The existing Bank #1 only has two feeders (6011 and 6021).  These additional feeders should allow more load diversity among the four feeders and provide some needed backstand capability to this and the other existing feeder.  Several reactive maintenance projects replaced damaged poles and conductor after patrols of the feeder during and after adverse weather events.  Seven system improvement projects were in progress that are rebuilding about 58,000 feet (about 11.0 miles) of the existing feeder by installing new larger wire, new stronger poles where needed, and new fiberglass crossarms.  Two projects were completed in 2019, one project was completed in early 2020, and the other four projects are nearing completion.  A system improvement project is in progress in 2020 to establish a new substation in the area with new feeder breakers and to build a feeder tie with one of the new feeders and transfer load from SBEAN-6021. This will reconfigure the feeder to minimize exposure and provide an alternate source during future outage events.

  - MASON-3413

    - This feeder is 43.6 miles long and currently serves 57 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violations are due to SAIDI (One Year) and SAIFI (One Year). In 2019, lightning, downed overhead conductor, and unknown caused events were the primary reasons.  Most of these events occurred during or after adverse weather.

    - In 2019, reactive maintenance projects replaced damaged poles and conductor after patrols of the feeder during and after adverse weather events.  A system improvement project installed capacitor banks and upgraded voltage regulators to improve voltage support on sections of the feeder.  A distribution automation project replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses. A distribution automation project is planned for 2021 to replace an existing oil-filled recloser at a key location on the feeder with an electronic vacuum recloser equipped with SCADA for remote monitoring and control.  Another system improvement project planned for 2021 is to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.

  - MASON-3412

    - This feeder is 56.1 miles long and currently serves 97 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violation is due to SAIDI. In 2019, lightning, downed overhead conductor, and unknown caused events were the primary reasons.  Most of these events occurred during or after adverse weather.

    - In 2019, a reactive maintenance project replaced damaged crossarms and conductor after a patrol of the feeder following an adverse weather event.  System improvement projects installed multiple capacitor banks to improve voltage support on sections of the feeder.  A distribution automation project replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses.  Three system improvement projects were in progress in 2019 that reconductored about 10,400 feet (about 2.0 miles) of the existing feeder by installing new larger wire, new stronger poles where needed, and new fiberglass crossarms.  One project was completed in 2019 and the other two projects are nearing completion in 2020.  A system improvement project is planned for 2021 to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.

  - ELMAR-3231

    - This feeder is 33.7 miles long and currently serves 19 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 10% vegetation density.

    - The feeder violations were due to SAIDI (One Year) and SAIFI (One Year). In 2019, lightning, unknown, and one crossarm caused event in June were the primary reasons.

    - In 2019, reactive maintenance projects replaced a deteriorated pole after a patrol of the feeder and a damaged crossarm during an adverse weather event.  A system improvement project installed multiple capacitor banks to improve voltage support on sections of the feeder.  Another system improvement project reconductored about 4,000 feet of the existing feeder by installing new larger wire and new stronger poles where needed.  In 2020, a system improvement project is scheduled to reconductor about 1,000 feet of existing feeder by installing new larger wire, new stronger poles where needed, and new fiberglass crossarms.  Another system improvement project is planned for 2020 is to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during outage events.

  - DIALV-3911

    - This feeder is 110.1 miles long and currently serves 1,096 customers in rural East Texas.  The terrain is pine forests with trees greater than 100 feet tall in loose sandy soils with 100% vegetation density.

    - The feeder violations were due to SAIDI (One Year) and SAIFI (One Year).  In 2019, trees and lightning caused events were the primary reasons.  Most of the lightning caused events occurred during two adverse weather days in April.

    - In 2019, a vegetation management project trimmed the trees in the distribution right-of-way on the mainline and multi-phase sections of the feeder (about 26.0 miles) and was completed in the third quarter.  A distribution automation project is planned for 2021 to replace an existing oil-filled recloser at a key location on the feeder with an electronic vacuum recloser equipped with SCADA for remote monitoring and control.

  - HNTNG-1307

    - This feeder is 147.1 miles long and currently serves 1,503 customers in rural East Texas.  The terrain is pine forests with trees greater than 100 feet tall in loose sandy soils with 100% vegetation density.

    - The feeder violation is due to SAIDI.  In 2019, tree caused events in August and September, a lightning caused event on one day in April, and a disconnect switch caused event the next day in April were the primary reasons.

    - In 2019, targeted and reactive tree trimming was done by vegetation management during the year.  Some of the tree trimming was done during or after adverse weather events.

  - ANDRD-0921

    - This feeder is 55.7 miles long and currently serves 81 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violation is due to SAIDI.  In 2019, lightning and unknown caused events were the primary reasons.

    - In 2019, reactive maintenance projects replaced damaged crossarms and conductor after patrols of the feeder during and after adverse weather events.  A distribution automation project replaced single operation line fuses at a key location on the feeder with reclosing vacuum fuses.  In 2020, a distribution automation project is scheduled to replace single operation line fuses at key locations on the feeder with vacuum reclosing fuses.

  - SNDHL-3811

    - This feeder is 29.1 miles long and currently serves 53 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The violation was due to SAIDI.  In 2019, a pole down event on one day in September and unknown caused events during the year were the primary reasons.

    - In 2019, reactive maintenance projects replaced damaged and deteriorated poles identified after patrols of the feeder.  A planned vegetation management project to trim the trees on the mainline section of the feeder is scheduled for 2020.

  - WINKS-0521

    - This feeder is 24.6 miles long and currently serves 42 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violations were due to SAIDI (One Year) and SAIFI (One Year).  In 2019, a downed overhead conductor event in June, unknown cause, and swinging conductor caused events were the primary reasons.  Most of these events occurred during or after adverse weather.

    - In 2019, a distribution automation project replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses.  A reactive maintenance project replaced damaged facilities on the feeder identified by a feeder patrol after adverse weather.

  - FLRTN-3711

    - This feeder is 47.0 miles long and currently serves 101 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The violation was due to SAIDI.  In 2019, one pole down event during adverse weather in March and lightning caused events during the year were the primary reasons.

    - In 2019, reactive maintenance projects replaced poles and other damaged facilities identified during patrols of the feeder during and after adverse weather events.  A system improvement project reconductored about 14,500 feet (about 2.7 miles) of the existing feeder with new larger wire and new stronger poles and fiberglass crossarms where needed.  Targeted tree trimming was done by vegetation management during the year.  A distribution automation project is planned for 2020 to replace an existing oil-filled recloser at a key location on the feeder with an electronic vacuum recloser equipped with SCADA for remote monitoring and control.  Another system improvement project planned for 2020 is to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.

  - GLSCK-2411

    - This feeder is 120.0 miles long and currently serves 219 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% vegetation density.

    - The feeder violation was due to SAIDI.  In 2019, one public vehicle caused event in January and lightning caused events during the year were the primary reasons.

    - In 2019, reactive maintenance projects replaced storm and lightning damaged poles, damaged conductor, and other damaged facilities identified during patrols of the feeder after adverse weather events.  Targeted tree trimming was done by vegetation management during the year.  Two system improvement projects reconductored about 12,300 feet (about 2.3 miles) of the existing feeder with new larger wire and new stronger poles and fiberglass crossarms where needed.  These projects also installed voltage regulators to improve voltage support and replaced an older oil-filled hydraulic recloser with an electronic vacuum recloser equipped with SCADA for remote monitoring and control.  Three distribution automation projects replaced over twenty (20) single operation fuses at key location on the feeder with vacuum reclosing fuses.  Two projects were completed in the fourth quarter of 2019 and one was completed in early 2020.  A system improvement project started in 2019 is in progress in 2020 that will replace an older oil-filled hydraulic recloser with an electronic vacuum recloser equipped with SCADA for remote monitoring and control and install new voltage regulators to improve voltage support on the feeder.

  - ATHNW-1403

    - This feeder is 70.4 miles long and currently serves 1,893 customers in rural East Texas.  The terrain is sandy soils with mixed tree varieties and 95% vegetation density.

    - The feeder violation was due to SAIDI.  In 2019, a public vehicle knocked down a pole that locked out the breaker and caused a series of long duration outage events.  The events on this one day in February were the primary reason for the high SAIDI.

    - In 2019, a reactive maintenance project replaced the pole that was knocked down by the public vehicle mentioned above.  A planned maintenance project replaced twenty-three (23) deteriorated crossarms and other deteriorated facilities identified by a patrol of the feeder the previous year.  A distribution automation project replaced an older oil-filled recloser with an electronic vacuum recloser equipped with SCADA for remote monitoring and control.  A system improvement project to upgrade the feeder tie between ATHNW-1403 and ATHNW-1401 replaced about 3,700 feet of small wire with larger wire and installed two new air-break sectionalizing switches.  This project increased the maximum load that can be transferred to either feeder to improve backstand capacity in the event of an outage on one feeder so that load can be temporarily transferred to the other feeder.

  - ODESA-0242

    - This feeder is 13.3 overhead miles, 4.6 underground miles, and currently serves 370 customers in the town of Odessa in West Texas.

    - The feeder violation was due to SAIDI.  In 2019, several downed overhead primary conductor caused events were the primary reasons.

    - In 2019, reactive maintenance projects replaced a damaged pole, crossarms, two spans of conductor and a leaking transformer.  A planned vegetation management project to trim the trees on the mainline sections of the feeder is scheduled for 2020.  A distribution automation project is also scheduled that will replace three single operation line fuses at a key location on the feeder with a three-phase electronic vacuum recloser equipped with SCADA for remote monitoring and control.  Another system improvement project planned for 2020 is to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.

  - RSKMN-3046

    - This feeder is 36.5 miles long and currently serves 1,088 customers in rural East Texas.  The terrain is sandy soils with areas of tall trees and 100% vegetation density.

    - The feeder violation was due to SAIDI.  In 2019, swinging conductor caused events in October and November, unknown caused events in August and November, and an ice caused event in February were the primary reasons. Most of these events occurred during or after adverse weather.

    - In 2019, reactive maintenance projects replaced several damaged reclosers and a damaged voltage regulator.  A planned vegetation management project started the previous year was completed in 2019 that trimmed the trees in the distribution right-of-way of the mainline of the feeder (about 7.6 miles).  Also, reactive tree trimming was done by vegetation management during the year.  A planned vegetation management project to trim the trees on the multi-phase sections of the feeder is scheduled for 2020.  Another distribution automation project planned in 2020 will replace single operation line fuses at key locations on the feeder with vacuum reclosing fuses.  A distribution automation project is planned for 2021 to upgrade an existing older oil-filled hydraulic recloser with a new electronic vacuum recloser equipped with SCADA for remote monitoring and control.

  - CRNES-2711

    - This feeder is 35.0miles long and currently serves 127 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% tree density.

    - The feeder violation was due to SAIDI.  In 2019, an unknown caused event in January and a lightning caused event in May were the primary reasons. Both of these events occurred during adverse weather.

    - In 2019, reactive maintenance projects replaced damaged poles, crossarms, and conductor identified by feeder patrols that were damaged during adverse weather events.  A planned maintenance project replaced deteriorated poles and other facilities identified by a patrol of the feeder.  A distribution automation project replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses.  In 2020, another distribution automation project is in progress to replace single operation line fuses at several key locations on the feeder with vacuum reclosing fuses.

  - ELMAR-3232

    - This feeder is 87.9 miles long and currently serves 183 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 5% tree density.

    - The feeder violation was due to SAIDI.  In 2019, a tree caused event in June, a public vehicle caused event in February, lightning caused events during the year, and an underground primary cable caused event in December were the reasons.

    - In 2019, reactive maintenance projects replaced damaged poles, crossarms, and conductor identified by feeder patrols that were damaged during adverse weather events.  A system improvement project installed a new capacitor bank and another project replaced a damaged capacitor bank to improve voltage support on the feeder.  In 2020, a system improvement project is scheduled to reconductor about 10,400 feet (about 2.0 miles) of the existing feeder by installing new larger wire and new stronger poles and fiberglass crossarms where needed.  Another system improvement project planned for 2020 will establish a new substation nearby that will allow this feeder to be reconfigured and the new feeder(s) can provide an alternate source during future outage events.  Also, a distribution automation project is planned for 2021 to replace an existing oil-filled recloser at a key location on the feeder with an electronic vacuum recloser equipped with SCADA for remote monitoring and control.

  - LMESA-2813

    - This feeder is 72.7 miles long and currently serves 114 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 10% vegetation density.

    - The feeder violation was due to SAIDI.  In 2019, high winds in June took down transmission poles with distribution underbuilt on them which caused a long duration outage event to some customers while the transmission poles were replaced and primary conductor was re-installed.  A lightning caused event on that same day and other days during the year, a public vehicle caused event, and a damaged crossarm caused event were the reasons for the high SAIDI.

    - In 2019, reactive maintenance projects replaced damaged poles, crossarms, and conductor identified by feeder patrols that were damaged during adverse weather events.  Targeted tree trimming was done by vegetation management during the year.  A planned maintenance project replaced five deteriorated poles and other facilities.  A distribution automation project replaced single operation line fuses at key locations on the feeder with vacuum reclosing fuses.  In 2020, a distribution automation project is scheduled to replace an older oil-filled hydraulic recloser with an electronic vacuum recloser and also to install a new electronic vacuum recloser at a key location on the feeder to improve sectionalizing during future outage events.  Both of these new electronic reclosers will be equipped with SCADA for remote monitoring and control.

  - TRPMN-4094

    - This feeder is 51.2 miles long and currently serves 595 customers in rural East Texas. The terrain is sandy soils with areas of tall trees and 100% vegetation density.

    - The feeder violation was due to SAIDI.  In 2019, one tree caused event in June and several others during the year were the primary reasons.

    - In 2019, a planned vegetation management project started the previous year was completed that trimmed trees along the distribution right-of-way of feeder (about 17.5 miles).  Also reactive tree trimming was done by vegetation management during the year.  A distribution automation project installed three new IntelliRupter vacuum pulse-closing automated switches and 20 repeater communication units on two adjacent feeders in order to provide automatic service restoration between TRPMN-4094 and WHOUS-4122.  A distribution automation project is planned for 2020 to upgrade an existing older oil-filled hydraulic recloser with a new electronic vacuum recloser equipped with SCADA for remote monitoring and control.  Another distribution automation project is planned for 2020 to replace single operation line fuses at key locations on the feeder with vacuum reclosing fuses.

  - PMBRK-1821

    - This feeder is 42.7 miles long and currently serves 67 customers in rural West Texas.  The terrain is low scrub brush and desert sands with limited paved road access and 25% vegetation density.

    - The feeder violation was due to SAIDI.  In 2019, a downed pole event in June after several hours of high wind gusts and a broken pole caused event in September were the primary reasons.

    - In 2019, reactive maintenance projects replaced poles damaged during adverse weather events.  A planned maintenance project replaced deteriorated crossarms and other facilities identified by a patrol of the feeder in the previous year.  A system improvement project upgraded voltage regulators to improve voltage support on the feeder.  Two distribution automation projects replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses.  A system improvement project is in progress to reconductor about 5,500 feet (about 1.0 mile) of the existing feeder with new larger wire and new stronger poles and fiberglass crossarms where needed.  In 2020, a distribution automation project is in progress to replace single operation line fuses at several key locations on the feeder with vacuum reclosing fuses.  A system improvement project is planned for 2020 to decommission the PMBRK substation and transfer load to a larger capacity substation nearby with five feeder breakers.

  - OVRTN-4015

    - This feeder is 29.2 miles long and currently serves 621 customers in rural East Texas.  The terrain is sandy soils with areas of tall trees and 100% vegetation density.

    - The feeder violations were due to SAIDI (One Year) and SAIFI (One Year).  In 2019, tree caused events in February and September and a lightning caused event in March were the primary reasons.

    - In 2019, a distribution automation project replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses.  Reactive tree trimming was done by vegetation management during the year.  A distribution automation project is planned for 2020 to replace single operation line fuses at key locations on the feeder with vacuum reclosing fuses.

  - CRISP-1501

    - This feeder is 36.6 miles long and currently serves 257 customers in rural Central Texas.  The terrain is sandy soils with areas of tall trees and 100% vegetation density.

    - The feeder violation was due to SAIDI. In 2019, a downed overhead conductor event in April during adverse weather, a public contact of overhead primary conductor event in May, and a public vehicle event in June were the primary reasons.

    - A planned vegetation management project started the previous year was completed in early 2019 that trimmed the trees in the distribution row-of-way of the feeder (about 16.3 miles).  A distribution automation project is planned for 2020 to replace single operation line fuses at key locations on the feeder with vacuum reclosing fuses.

  - SHNRW-1609

    - This feeder is 22.0 overhead miles, 12.2 underground miles, and currently serves 1,806 customers in the town of Sherman in North Central Texas. There is a 75% vegetation density on this feeder.

    - The feeder violation was due to SAIFI.  In 2019, an overhead to underground termination caused event in August, an overhead insulator caused event in September, an unknown caused event and a lightning caused event both on the same day also in September were the primary reasons.

    - A planned vegetation management project started the previous year was completed in early 2019 that trimmed the trees in the distribution row-of-way of the feeder (about 12.7 miles).  Reactive tree trimming work was also done during the year.

  - CSHNG-1201

    - This feeder is 94.2 miles long and currently serves 922 customers in rural East Texas.  The terrain is pine forests with trees greater than 100 feet tall in loose sandy soils with 100% vegetation density.

    - The feeder violation was due to SAIFI.  In 2019, a swinging conductor caused event in April and lightning and unknown caused events in May were the primary reasons.

    - In 2019, a distribution automation project replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses.  Targeted and reactive tree trimming was done during the year.  A planned vegetation management project to trim the trees on the mainline sections of the feeder is scheduled for 2020.

  - DALLW-0003

    - This feeder is 11.3 overhead miles 0.6 underground miles, and currently serves 675 customers in a suburban area of DFW. There is a 50% vegetation density on this feeder.

    - The feeder violation was due to SAIFI.  In 2019, a swinging conductor caused event in February, a lightning arrester caused event in September, and an underground primary cable caused event also in September were the primary reasons.  Each of these three events caused the feeder breaker to lockout.

    - In 2019, reactive maintenance projects repaired a section of underground primary cable that failed and other facilities damaged during the year.  Targeted tree trimming was done by vegetation management during the year.  A distribution automation project is planned for 2020 to install automated vacuum switches to provide automatic service restoration between this feeder and an adjacent feeder.

  - CRSGL-1306

    - This feeder is 68.2 overhead miles, 3.2 underground miles, and currently serves 644 customers in rural Central Texas.  There is a 40% vegetation density on this feeder.

    - The feeder violation was due to SAIFI.  In 2019, an event caused by vines in May, a swinging conductor caused event in July, and an overhead to underground termination caused event in December were the primary reasons.

    - In 2019, a planned vegetation management project trimmed the trees in the distribution row-of-way of the feeder (about 9.7 miles).  Also, reactive tree trimming was done by vegetation management during the year.  Reactive maintenance projects replaced a span of deteriorated overhead conductor and other damaged facilities.  Three system improvement projects are in progress to replace older wood poles at multiple highway crossings on the feeder with either concrete or steel poles.  In 2020, a distribution automation project is scheduled to replace single operation line fuses at key locations on the feeder with vacuum reclosing fuses.  Also, a distribution automation project is planned for 2021 to replace an existing oil-filled recloser at a key location on the feeder with an electronic vacuum recloser equipped with SCADA for remote monitoring and control.

  - CKRHL-0008

    - This feeder is 14.9 overhead miles, 8.8 underground miles, and currently serves 1,668 customers in a suburban area of DFW.  There is a 40% vegetation density on this feeder.

    - The feeder violation was due to SAIFI.  In 2019, two swinging conductor caused events on the same day in April and a public vehicle caused event in June were the primary reasons. Each of the events caused the feeder breaker to lockout.

    - In 2019, the feeder was patrolled during outage events and repairs were made.  A system improvement project is planned for 2021 to establish a new substation nearby that will allow this feeder to be reconfigured to minimize exposure and the new feeder(s) can provide an alternate source during future outage events.