## Sheet1
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
A.0000646.004 A.0000646.010 A.0000646.011 | Ochiltree Substation to Lipscomb Substation | Ochiltree County, Lipscomb County | Construct approximately 19.5 miles of new 115 kV transmission line from Ochiltree Substation to the new Lipscomb Substation | 2014-01-01 | 2015-11-07 | 2016-07-15 | 13413951 | 13413951 | 10262195.38 | -23.5% | 100 | N/A | 115 | 19.53 | 397.5 kcMIL, ACSR, 26/7 stranded code name IBIS | Single-circuit, single-pole self supporting steel structures, drilled pier foundations for corners & angle structures with some H-frame steel structures | NA | NA | 70 | 19 - 27 | 41334 | Cost variance due to Final Estimated Project Cost including costs for RWIP work occuring on line Z66 whereas Final Actual Cost is the total Plant Addtion cost of the project for CWIP only.
A.0000673.023 A.0000673.024 | Yoakum to State Line | Yoakum, Gaines | 345-kilovolt (“kV”) electric transmission line between the existing Yoakum Substation, located in Yoakum County, Texas and the Texas State Line. This Project and the larger Proposed TYH Project were recommended by the High Priority Incremental Load Study (“HPILS”). | 2017-10-17 | 2018-08-21 | 2019-05-30 | 35715903 | 30030330 |  |  | 100 | NA | 345 | 27-28 | 795 kcMIL, ACSS, 26/7 stranded, code name DRAKE/ACSS | two-pole H-frame steel structures for tangents and light angles. Three-pole steel for high angle and dead-end structures. | NA | NA | 150 | 27-28 | 44726 | Construction is complete and the line was energized on 5/31/2019. ROW restoration is in progress and final costs will be reported once that work is complete.
A.0000296.005 A.0000296.013.001.002 A.0000296.013.001.003 | NE Hereford to LaPlata | Deaf Smith | A new single circuit, 115-kilovolt (“kV”) electric transmission line between the existing NE Hereford Substation and the new La Plata Substation, both located in Deaf Smith County, Texas | 2017-09-11 | 2018-03-25 | 2018-03-30 | 5126829 | 5126829 | 4972150.9 | -3.017% | 100 | NA | 115 | 7.5 | 477 kcMIL, aluminum conductor steel supported (ACSS), 26/7 stranded, code name HAWK. | single-circuit, self-supporting steel single pole structures within new ROW | NA | NA | 70 | 7.5 | 45158
A.0000979.001 A.0000979.004 A.0000979.002 A.0000979.011 A.0000979.003 | Mustang-Shell CO2 115kV Line | Denver City, TX | Construct New 9 Mile 115 Transmission Liine from Mustang to Shell CO2. Project will require both Mustang and Shell Substation to be expanded. | 2018-06-21 | 2019-12-15 | 2019-04-29 | 12362552 | 10663388 | 8756153.41 | -17.89% | 100 | 115 | 115 | 9 | 795 ACSR | SD-TO-190- Double Circuit, Tangent; SD-T60-1283-Single Circuit, Delta Tangent; SD-T60-1286-Single Circuit, In-line Deadend; SD-T60-1298- Single Circuit, Vertical Deadend | N/A | N/A | 70 | 9 | 47585
A.0000673.021 A.0000673.022 | TUCO to Yoakum | Hale, Yoakum, Terry, Hockley, Lubbock | Construct new 106.5 milke 345 kV line between Yoakum and the existing sub. | 2019-05-01 | N/A | N/A | 129541977 | 129541977 |  |  | 97 | N/A | 345 | 106.5 | 795 ACSS | Two-pole H-frame steel structures for tangents and light angles. Three-pole steel for high angle and dead-end structures. | N/A | 106.5 | 150 | 106.5 | 46042 | Construction is in progress.
C13-22574 | Hale Wind Interconnnection | Petersburg/ Hale | 230kV Generation-Tie Line | 2018-09-24 | 2019-01-20 | 2019-01-31 | 9,317,470 T-line 124,174 Sub | 11,609,138 T-Line 124,174 Sub |  |  | 100 | N/A | 230 | 14.59 | Bundled 1272 kcMIL, ACSR, 45/7 stranded, bittern | Self-supported Monopole | N/A | N/A | 150 | 14.59 | 48253 | Charges from transmission have not settled to the project yet. These were charges from the interconnection agreement to the tune of $162,851.76.
A.0001030.001 A.0001030.002 | Mustang-Seminole 115kV Line | Seminole, TX | Construct New 20 Mile 115 Transmission Line from Mustang to Seminole. Project will require both Mustang and Seminole Substation to be expanded. | 2020-04-01 | N/A | N/A | 13852000 | 13852000 |  |  | 0 | 115 | 115 | 20 | 397.5 MCM ASCR | SD-TO-190- Double Circuit, Tangent; SD-T60-1283-Single Circuit, Delta Tangent; SD-T60-1286-Single Circuit, In-line Deadend; SD-T60-1298- Single Circuit, Vertical Deadend | N/A | N/A | 70 | 19.3 | 48724 | Project is currently in the Engineering Phases for both Substation and Transmission Portions.
A.0000303.062 A.0000303.063 | V04 Structure Replacement | Amarillo, Randall | Pole failure to ground. Project is 1.25 mile reroute of line around existing golf course and remove existing structures. | 2020-03-09 | N/A | N/A | N/A | 1639496.5369 |  |  | 80 | 115 | 115 | 1.1 | 397.5 MCM ACSR | (Multiple) Single Steel Pole construction on concrete foundation | 75 | 0.75 | 75 | 1.1
A.0001402.002 A.0001402.005 A.0001402.006 A.0001402.007 A.0001402.008 A.0001402.009 A.0001402.011 A.0001402.015 A.0001402.016 | Sagamore Wind Network Upgrades | Multiple Texas Panhandle Counties | Upgrades to the existing SPS Transmission system to accommodate the Sagamore Wind Farm coming on line. These upgrades are located on existing transmission circuits and substations identified by the Southwest Power Pool | 2020-03-02 | N/A | N/A | N/A | 33596051 |  |  | 5 | N/A | 115 & 230 | TBD | 477 ACSS | (Multiple) Single Steel & Wood Pole construction on concrete foundation(Steel only) and direct embed(Wood Only) | TBD | TBD | TBD | TBD |  | Construction start date only represents civil construction which is why all length data is TBD until final design is complete.
A.0000795.010 | (SPS Sub Communication Network Group 1) Kirby Jericho T-52 115kV Line | Amarillo, Randall/Potter | Build out of the Fiber Communication Network in the Amarillo, Texas area. This Fiber buildout is on existing transmission circuits. | 2020-04-10 | N/A | N/A | N/A | 668565 |  |  | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | Communication project that does not change or modify voltage of exiting circuit.
A.0001022 | DCP - White Deer Sub | White Deer, Gray | New 115/13.2kV 28 MVA Substation to accommodate new load growth in the area. | 2020-07-31 | N/A | N/A | N/A | 1084567 |  |  | 0 | 115 | N/A | 0.75 | 477 ACSS | Single Pole Steel direct embed | N/A | N/A | 75 | 0.75 |  | NOTE: Distribution portion of the project has started, however the Transmission construction work is not starting until later.
Note on I10: Chris Buboltz: April 2020 CAA Tool
Note on I11: Chris Buboltz: April 2020 CAA Tool
Note on I12: Chris Buboltz: April 2020 CAA Tool