## WETT
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
Farmland | Long Draw Substation Farmland Expansion | Borden County | Expand Long Draw station footprint to add Bay 7 to allow connection of a 345 kV line coming from Sharyland's "Farmland" station | 2018-06-05 |  | 2018-10-26 | 3130000 | 3135000 |  |  | 99 | 345 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | Sub. Rule 25.83(a)(3) | Project already in service. Bus support needs to be installed for full completion.
LDSolar | Long Draw Solar Station to Long Draw Switching Station Transmission Line Project | Borden County | This project will consist of constructing 0.15 mile 345kV transmission line, 1.85 miles of 138kV transmission line, and new 138kV substation. This project will connect the Long Draw Solar collector station to WETT's existing Long Draw 345kV station. | 2019-10-31 | 2020-07-31 | 2020-10-22 | 14587478 |  |  |  | 99 | n/a | 345/138 | 0.15 miles at 345kV, 1.85 miles at 138kV | 959 kcmil ACSS/TW Suwannee | Steel Monopoles | n/a | n/a | 100 | 1.8 | 49238 | CCN application Notice of Approval filed on 06/18/19. Project energized on 10/22/20 but not yet fully complete.
Solar Nova (TSN1) | Solar Nova Project | Kent County | The project will consist of constructing a new 345kV switching station, a new 138kV substation, and 0.7 miles of 138kV transmission line. This project will be located on WETT's Cottonwood to Dermott 345kV line segment. | 2019-10-31 | 2021-10-15 |  | 23514208 |  |  |  | 0 | 345 | 345/138 | 0.7 miles at 138 kV | 959 kcmil ACSS/TW Suwannee | Steel Monopoles | n/a | n/a | 100 | 0.7 | Sub. Rule 25.83(a)(3)
Juno Solar | Juno Solar Station to Long Draw Switching Station Transmission Line Project | Borden County | The proposed project is a new single-circuit, 138 kV transmission line connecting the Juno Solar Collector Station to the Long Draw Switching Station | 2019-11-30 | 2020-12-31 |  | 7500000 |  |  |  | 85 | n/a | 138 | 6 | 959 kcmil ACSS/TW Suwannee | Steel Monopoles | n/a | n/a | 100 | 6 | 49973 | CCN application Notice of Approval filed on 01/02/20
Bearkat Area Transmission Improvements Project | Bearkat Switching Station to Oncor Switching Station Transmission Line Project | Howard and Glasscock Counties | The proposed project is a new single-circuit, 345 kV transmission line connecting WETT's Bearkat Switching Station to Oncor's Longshore Switching Station | 2021-01-14 | 2022-03-31 |  | $ 29,339,500 (t-line) $ 3,500,000 (station) (WETT Portion) |  |  |  | 0 | n/a | 345 | 30.8 | Twin Bundle 1590 kcmil 54/19 ACSR (WETT) | Steel Lattice Towers | n/a | n/a | 160 | 30.8 | 50410 | This is a joint project with Oncor Electric Delivery Company - only WETT associated project costs are being reported. Application filed 1/14/20.
Primary Control Center | Primary Control Center | Travis County | Construction associated with Primary Control Center move | 2019-03-30 | 2020-09-22 | n/a | 5900000 | n/a | 5950521.54 | 0.5% | 100 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | Sub. Rule 25.83(a)(3) | The initial estimated project cost has always been $5,900,000 from project inception