## MonthlyReportForm
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
TL282 | TxDOT SL375 Interchange Improvements | El Paso, El Paso | Adjust two 345kV transmission lines (Caliente to Amrad and Caliente to Picante) across State Highway Loop 375, south of Iron Medics Dr., to accommodate the new eastbound and westbound frontage roads to be constructed by TxDOT. EPE will replace several poles on either side of State Highway Loop 375 with taller steel poles for each line. | 2020-02-03 |  |  | 4292714 |  |  |  |  | 345 | n/a | 0.73 each | 954 ACSR corncrake double bundle conductor | Replace wood H-frame structures with 90'-125' steel H-frame or 3-pole structures. | 300 | 0.73 each | n/a | n/a | 25.101(c)(5)(F)
TL233 | Nuway Project | El Paso, El Paso | This is a 2-phase project to allow for the construction of a new substation, Nuway, underneath two transmission lines. Phase 1 temporarily reroute the 115kV Montoya to Anthony and permanently reroute the 69kV Rio Grande to Border Steel presently on a double circuit steel monopole. Phase 2 complete the installation of the 115kV transmission line Montoya to Anthony which will cut into the new Nuway Substation. | 2018-03-25 | 2018-03-31 | 2019-11-14 | 687000 | 1200000 | 1360665 | 13.39% | 100% | 115 and 69 | n/a | 115kV-8.58 and 69kV-13.09 | Both transmissions 795 ACSR single bundle | Temporarily install 2-95' steel structures to reroute the 115kV line to the east side of the substation. Permanently install an 85' steel double circuit monopole on the north and south side of the substation to continue with the 69kV and 115kV lines. Reroute the 69kV line to the west side of the substation on 2-85' single circuit monopoles. Once the substation is near completion, permanently install 2-85' single circuit monopoles for the 115kV line and tapping into Nuway Substation. | 50-100 | 115kV 8.58 and 69kV 13.09 | n/a | n/a | 25.101(c)(5)(A) | Line energized November 14, 2019
TL247 | TxDOT US 62/180 (Montana Ave) Expansion Accommodate Distribution Vista to Scotsdale | El Paso, El Paso | Install taller transmission structures on the Vista to Scotsdale 115kV line along Montana Ave to accommodate the distribution adjustments for the TxDOT highway expansion | 2019-04-01 | 2019-06-13 |  | 300185 |  |  |  | 100% | 115 | n/a | 5.18 | 556 ACSR | Replace existing monopole structures with monopole tangent steel structures; heights vary from 75'-105' | Highway right of way | 5.15 | n/a | n/a | 25.101(c)(5)(F)
TL247 | Vista to Caliente 115kV Transmission Line Adjustments | El Paso, El Paso | Due to the TxDOT US 62 (Montana) project, the removal of 2 existing span guy poles north of Montana that support the dead end structure holding the Vista-Caliente (VC) and Vista-Scotsdale (VS) 115 kV transmission lines affect the VC, VS, and Vista-Global Reach(VGR) 115kV line all the way back to Vista Substation. The VC line currently crossing under the VGR line, must be moved to the south side of the substation and repositioned to the east side of the corridor. The VGR will become a double circuit line and repositioned on the east side of the shifted VC line. | 2019-03-04 |  |  | 592758 |  |  |  | 90% | 115 | n/a | 1.5 | 795 ACSR single bundle | Install intermediate 95' monopoles | 100 | 6.64 | 30 | 0.06 | 25.101(c)(5)(F)
TL236 | Rio Grande to Sunset North 115kV transmission line tap into Executive Substation | El Paso, El Paso | Replace structures on the 15800 -115kV transmission line to tap into the new Executive Substation. Will create the Sunset North to Executive and Executive to Rio Grande 115kV lines | 2019-08-05 |  |  | 474590 |  |  |  | 20% | 115 | n/a | 0.1 | 556 ACSR double bundle; wire will not be replaced | Replace H-frame wood structures with 4-100' steel monopole tangents and install 2-85' deadend steel structures on drill pier foundations | 50 | 0.1 | n/a | n/a | 25.101(c)(5)(A)
TL283 | TxDOT SL375 Interchange Improvements | El Paso, El Paso | Adjust two 345kV transmission line (Caliente/Amrad and Caliente Picante) and two 115kV transmission lines (Global Reach/Picante and Liberty/Bliss Industrial) across State Highway Loop 375, north of Iron Medics Dr., to accommodate the new eastbound and westbound frontage roads to be constructed by TxDOT. EPE will replace several poles on either side of State Highway Loop 375 with taller steel poles for each line. | 2020-02-03 |  |  | 3372668 |  |  |  |  | 115 & 345 | n/a | 115kV-0.34 each & 345kV 0.37 each | 115kV-954 ACSR single bundle & 345kV 954 ACSR double bundle | 115kV each line install 100' tangent steel H-frame structures and 70'- 3 pole steel deadend structures. 345kV 90'-125' steel H-frame or 3-pole dead end structures | 115kV-100 & 345kV-300 | 115kV -0.34 each & 345kV 0.37 each | n/a | n/a | 25.101(c)(5)(F)
TL101 | Rio Grande to Sunset 69kV and Rio Grande to Sunset North 115kV transmission lines rebuild and reconductoring. | El Paso, El Paso | Rebuild two 69kV lines from Rio Grande to Sunset, and one 115kV line from Rio Grande to Sunset North, by upgrading the conductor and replacing existing wooden poles with one double-circuit and one single-circuit steel monopole line. One line will carry a 69kV line. The second line will carry a 69kV line and a 115kV double-bundle line. | 2019-07-31 |  |  | 22888944 |  |  |  | 17% | 69 & 115 | n/a | 5.24-115kV & 10.04 -69KV | 69kV lines replace 336 and 556 ACSR single bundle conductor with 954 ACSR single bundle and replace the 115kV - 556 ACSR double bundle conductor with 954 ASCR double bundle | All steel structures varying between 75' to 120' in height; single circuit tangent structures, double circuit tangent monopoles, and drill pier foundation dead end | 50'-100' | 4.32-115kV & 9.12-69kV | n/a | n/a | 25.101(c)(5)(B) | For the UTEP mountain portion of the project, all the conductor on the 69kV lines completed, continuing conductor pulling on the 115kV line.
TL253 | Lane to Mann | El Paso, El Paso | Replace wood poles that failed the integrity/strength test by OSMOSE | 2020-06-02 |  |  | 623038 |  |  |  |  | 69 | n/a | 0.63 | 556 ACSR single bundle | 85' steel monopoles | TxDOT ROW | 0.63 | n/a | n/a | 25.101(c)(5)(B)
TL106 | Wrangler to Sparks rebuild and reconductor | El Paso, El Paso | Rebuild a portion of the 115kV transmission line by replacing structures, upgrading the conductor, and adding optical ground wire. | 2020-03-02 |  |  | 1911367 |  |  |  |  | 115 | n/a |  | Replace 336 single bundle with 954 ACSR single bundle | 85' to 100' steel monopoles | TxDOT ROW | 2.66 | n/a | n/a | 25.101(c)(5)(B)
TS117 | Butterfield to Newman 115kV extend transmission service to a new Fort Bliss Military Reservation substation | El Paso, El Paso | 115kV in and out tap to service a new, North Bliss substation, inside the military reservation and install optical ground wire from Butterfield to North Bliss substations | 2020-04-20 |  |  | 450685 |  |  |  |  | 115 | n/a | 0.42 | Replace 556 ACSR singlebundle with 954 ACSR single bundle for the new portion into North sub | 75' steel monopoles and 100' steel double circuit monopoles | 25 | 0.47 | 60 | 0.21 | 25.101(c)(5)(F) & 25.101(c)(5)(A)
Note on H1: Author: Please enter only a single integer, if possible.
Note on I1: Author: Please enter only a single integer, if possible.
Note on M1: Author: If applicable.
Note on N1: Author: If applicable.