TO:		Taylor Denison, Attorney

Legal Division

FROM:	Heidi Graham, Lead Engineering Specialist

Infrastructure Division

DATE:  	November 5, 2020

SUBJECT:	Docket No. 50424 – Application of Monarch Utilities 1, L.P. and Goins Utility Service LLC for Sale, Transfer, or Merger of Facilities and Uncertificated Area in Polk County

- Application

Monarch Utilities 1, L.P. (Monarch) holds water Certificate of Convenience and Necessity (CCN) No. 12983 and sewer CCN No. 20899.  Monarch seeks approval to acquire facilities and to add to its CCNs all of the uncertificated water and sewer service areas of Goins Utility Service LLC (Goins).  In addition, Monarch requests to amend CCN No. 12983 to add a portion of the water service area of Lake Livingston Water Supply & Sewer Service Corporation (Lake Livingston), CCN No. 10147.  Lake Livingston has agreed to decertify that portion of its water service area.

The Goins water service area includes approximately 17 acres and 36 current customers.  The Goins sewer service area includes approximately 24 acres and 36 current customers.  The water service area of Lake Livingston to be decertified and simultaneously certified to Monarch is approximately 5 acres and has no customers.

- Notice

Monarch provided notice consistent with 16 Texas Administrative Code (TAC) §24.239(c).  The deadline for intervention stated in the notice was September 1, 2020, and no protests, intervention, or opt-out requests were received.

- Factors Considered

Texas Water Code (TWC) Chapter 13 and 16 TAC Chapter 24 require the Public Utility Commission (PUCT) to consider certain factors when granting or amending a water or sewer CCN, which are addressed below as subsections.

  - Consideration of the adequacy of service currently provided to the requested area (TWC § 13.246(c)(1) and 16 TAC § 24.227(e)(1))

The water service currently provided to the requested area by Goins is adequate.  Goins has a public water system (PWS) registered with the Texas Commission on Environmental Quality (TCEQ) under Beacon Bay Marina and RV Park, PWS No. 1870016.  Monarch submitted a TCEQ investigation report with the application that indicated Goins has an active violation with the TCEQ for record keeping for its well.

The sewer service currently provided to the requested area by Goins is adequate.  Goins has a sewer system registered with the TCEQ under Beacon Bay Marina Wastewater Treatment Facility, Wastewater Discharge Permit No. WQ0013637001.  According to the TCEQ investigation report submitted with the application, the previous violations Goins had with the TCEQ have been resolved.  The TCEQ investigator commented in the report that the wastewater treatment plant appeared to be well-maintained.

The PUCT’s Customer Protection Division has not received any complaints from Goins’ water or sewer customers.

  - Consideration of the need for additional service in the requested area (TWC § 13.246(c)(2) and 16 TAC § 24.227(e)(2))

Although Goins does not have a CCN, there are 36 customers currently receiving water service and sewer service from Goins’ water and sewer systems.  Therefore, there is a need for continuation of those services.  There is no information in the docket indicating a need for additional service in the Goins water and sewer service areas.

  - Consideration of the effect of granting an amendment on the recipient of the certificate or amendment, on the landowners in the area, and on any other retail public utility of the same kind already serving the proximate area (TWC § 13.246(c)(3) and 16 TAC § 24.227(e)(3))

The number of customers in the water and sewer service areas of Goins is small relative to the total number of customers served by Monarch, resulting in a negligible effect on Monarch.  The effect of application approval on landowners and other retail public utilities in the area would be the transfer of service areas from Goins and Lake Livingston to Monarch and Monarch’s planned construction projects, which I discuss below in subsection 3.10.

  - Consideration of the ability of the applicant to provide adequate service (TWC §§ 13.241(b), 13.246(c)(4), and 16 TAC § 24.227(e)(4))

It is unclear whether Monarch will provide adequate service in Goins’ water and sewer service areas if the appliction is granted.  Monarch is generally capable of providing adequate service given the large number of customers that it has served for a number of years.  However, Monarch’s provision of water service in compliance with the TCEQ’s rules in the general area of Goins water service area appears to be worse than Goins’ provision of water service.  Monarch has a public water system registered with the TCEQ under Oak Terrace Estates, PWS No. 1870055 that is adjacent to the Goins water service area.  According to the TCEQ’s online records, Monarch has active violations from 2019 for this public water system for failure to maintain all equipment in good working condition and failure to provide the required well production capacity of 0.6 gallons per minute per connection.  The violation for maintaining all equipment in good working condition is related to a bulging 5,000-gallon pressure tank that failed.  To date, Monarch has not requested construction approval from the TCEQ for a replacement pressure tank.

Monarch does not have a sewer CCN in the vicinity of the requested area.  In order to operate the Goins wastewater treatment plant after the CCN and facilities are transferred, Monarch would have to obtain approval for the transfer of the existing wastewater discharge permit from Goins by application to the TCEQ or apply to the TCEQ to obtain its own permit.  
Given that Monarch has held a number of wastewater discharge permits from the TCEQ, Monarch will likely be able to obtain such a permit to serve Goins’ sewer service area.

  - The applicants’ demonstration to the Commission that regionalization or consolidation with another retail public utility is not economically feasible when construction of a physically separate water or sewer system is required to provide service to the requested area. (TWC § 13.241(d) and 16 TAC § 24.227(b))

Monarch plans to replace major components of Goins’ existing water and wastewater systems, as discussed below in subsection 3.10.  As a result, regionalization or consolidation should be considered as alternatives.  Lake Livingston’s service area is adjacent to the Goins water service area.  David L. Sheffield d/b/a Texas Landing Utilities, sewer CCN No. 20569 is nearby to the north of the Goins sewer service area.  Aqua Texas, water CCN No. 13203, is nearby to the northwest of the Goins water service area.  However, the applicants did not address whether regionalization or consolidation with these systems is economically feasible.

Monarch plans to interconnect the Goins’ water system to Monarch’s neighboring Oak Terrace Estates water system.  However, the Oak Terrace Estates water system does not have the well production capacity to serve its existing customers.  As stated in subsection 3.4, the TCEQ has determined that Monarch is failing to provide the required well production capacity for its Oak Terrace Estates water system.

  - Consideration of the feasibility of obtaining service from an adjacent retail public utility (TWC § 13.246(c)(5) and 16 TAC § 24.227(e)(5))

As discussed above, there are retail public utilities in close proximity to Goins’ service areas.  Lake Livingston service area is adjacent to the Goins water service area.  David L. Sheffield d/b/a Texas Landing Utilities, sewer CCN No. 20569, is nearby to the north of the Goins sewer service area.  Aqua Texas, water CCN No. 13203, is nearby to the northwest of the Goins water service area.  However, the applicants did not address the feasibility of obtaining service from these retail public utilities.

  - Consideration of the financial ability of the applicant to pay for facilities necessary to provide continuous and adequate service (TWC § 13.246(c)(6) and 16 TAC § 24.227(e)(6))

Fred Bednarski from the Rate Regulation Division is addressing this factor.

  - Requirement of an applicant to provide a bond or other financial assurance in a form and amount specified by the Commission to ensure that continuous and adequate utility service is provided (TWC § 13.246(d) and 16 TAC § 24.227(f))

Fred Bednarski from the Rate Regulation Division is addressing this factor.

  - Consideration of environmental integrity and the effect on the land to be included in the certificated area (TWC §§ 13.246(c)(7) and (9) and 16 TAC § 24.227(e)(7) and (9))

Monarch’s plans for major construction to provide service in the Goins service areas may affect the environmental integrity of the land.  Monarch construction plans include replacement of the existing wastewater treatment plant.  This project would involve not only the construction of the new plant, but the dismantling of the existing plant and the disposal of sludge.  No information was provided by Monarch that addressed the environmental impact of any of its planned construction projects as required by this section of the PUCT’s rules.

  - Consideration of the probable improvement in service or lowering of cost to consumers (TWC § 13.246(c)(8) and 16 TAC § 24.227(e)(8))

The applicants did not demonstrate that there would be an improvement in service if the application is approved.  As explained above in subsection 3.4, Monarch’s provision of water service in the general area appears to be worse than Goins’ provision.  In addition, as explained in subsection 3.5, Monarch plans to interconnect the Goins’ water system to Monarch’s Oak Terrace Estates water system, despite the fact that the Oak Terrace Estates water system does not have the well production capacity to serve its existing customers.

Monarch plans to increase the rates of Goins’ customers.  On March 10, 2020, in its response to Staff’s deficiency memo, Monarch proposed to phase-in its consolidated rates, which are 79.54% higher for water service and 105.63% higher for sewer service than the existing Goins’ water and sewer rates.  In addition, Monarch has a pending base-rate application in which it proposes an overall increase of 9.80% in water revenues from its existing customers and an overall increase of 14.28% in wastewater revenues from its existing customers.  In Attachment HG-1, attached to this memorandum, Monarch’s current rates are compared to Goins’ rates and neighboring utilities’ rates.

In addition to interconnecting the Goins’ water system with its Oak Terrace Estates water system, Monarch plans construction of a replacement wastewater treatment plant; lift station rehabilitation; blower replacement; well and building rehabilitation; electrical work; meter replacement; and pressure tank replacement.  Monarch estimates that these projects will cost $268,000.  However, Monarch did not demonstrate that these projects are necessary or that the amount of $268,000 is justified.

Staff requested that the applicants provide the costs of Goins’ existing facilities so that I could calculate estimated rates for Goins using its existing facilities.  The applicants stated that records of the actual costs of Goins’ existing facilities do not exist.  As a result, Monarch prepared a trending study to estimate the costs of Goins’ facilities.  The trending study appears to have relied upon both insufficient and inaccurate inputs.  Monarch provided no documentation to support the estimated values of Goins’ facilities included in Monarch’s trending study.  In addition, according to the TCEQ’s online records, Beacon Bay Marina and RV Park water system records under PWS No. 1870016 date back to 1982.  For Beacon Bay Marina’s wastewater discharge permit No. WQ0013637001, the TCEQ’s online records date back to 1995.  Nevertheless, Monarch used an installation date of October 1, 2004, without explanation, for the majority of the water and sewer assets that it included in the trending study.  Therefore, without additional information showing otherwise, the trending study appears to be inaccurate.  As a result, I have not calculated estimated rates for Goins using its existing facilities.

  - Other factor considered – Nonfunctioning system or utility status of Goins

Goins is a very small utility, with only 36 water and sewer customers, and does not appear to be affiliated with other water and sewer utilities.  In addition, it is out of compliance with the requirement to have a Commission-approved tariff.  As a result, Goins is a nonfunctioning system or utility as that term is defined in 16 TAC § 24.3(23)(A).  As a class A utility, Monarch has the resources to bring Goins into compliance with the Commission’s regulatory requirements.

- Recommendation

Monarch has not yet demonstrated that its plans for major construction to provide service in the Goins service areas are reasonable and has not yet provided reasonable assurances that it will provide quality service to the customers of Goins. Therefore, I do not recommend approval of the transaction at this time, for the following reasons associated with the requirements of 16 TAC § 24.227 and TWC §§ 13.241 and 13.246:

- No information was provided about whether regionalization or consolidation with another retail public utility is economically feasible;

- Insufficient information was provided about the feasibility of obtaining service from a neighboring retail public utility;

- The potential exists for significant environmental impacts of construction projects that were not shown to be necessary;

- No information was provided detailing proposed improvements in service resulting from approval of the application; and

- A large rate increase that would result from the use of Monarch’s consolidated rates without a showing that those rates are comparable to rates based on the specific reasonable and necessary costs of serving Goins’ customers.

In the report, the TCEQ investigator required Goins to begin keeping well records and to submit those records to the regional office.  Staff notes that a violation related to lack of record keeping does not affect the adequacy of water service provided by Goins.

Application, page 9 of 20.

Application, TCEQ Compliance Correspondence Part F: Question 22.

Docket No. 50944, Application of Monarch Utilities I, L.P. for Authority to Change Rates.

Application, page 9 of 20 and Attachment Part C, Question 10 Capital Improvements Plan.