## Scenic Loop Area Load Growth
Data included in the original CCN Application:
SCENIC LOOP AREA SUBSTATION (kW)
LOCATION | 2014 | 2015 | 2016 | 2017 | 2018
La Sierra | 80056 | 95378 | 105197 | 104395 | 105524
Fair Oaks Ranch | 37140 | 39767 | 41193 | 41907 | 44428
Total in the Area | 117196 | 135145 | 146390 | 146302 | 149952
SCENIC LOOP AREA SUBSTATIONS FORECASTED LOAD GROWTH (kW)
LOCATION | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
La Sierra | 119005 | 122382 | 129481 | 136991 | 144936 | 153342 | 159476 | 165855 | 172489 | 177664 | 182994 | 188484 | 194138
Fair Oaks Ranch | 44806 | 47980 | 49228 | 50508 | 51821 | 53168 | 54550 | 55969 | 57088 | 58230 | 59394 | 60582 | 61794
Total in the Area | 163811 | 170362 | 178709 | 187499 | 196757 | 206510 | 214026 | 221824 | 229577 | 235894 | 242388 | 249066 | 255932
Recommended changes per the RFI to the CCN:
SCENIC LOOP AREA SUBSTATION (kW)
LOCATION | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
La Sierra | 80056 | 95378 | 105197 | 104395 | 105524 | 121040 | 102630 | 97440 |  | Covid Year - Not a typical year
Fair Oaks Ranch* | 37140 | 39767 | 41193 | 41907 | 44428 | 45780 | 57160 | 84040
Total in the Area | 117196 | 135145 | 146390 | 146302 | 149952 | 166820 | 159790 | 181480
Year over Year Growth % | - | 15.32% | 8.321% | -0.06011% | 2.495% | 11.25% | -4.214% | 13.57%
Normalised Growth % | - | 7.836% | 7.836% | 7.836% | 7.836% | 7.836% | 7.836% | 7.836%
Takeaways: Approximately 7.8% growth registered over 7 years between 2014 and 2021. Greater than 50% load growth in past 7 years, with large increases of 13 to 15% registered in some years. OSI PI data of feeder level peak loads, which are the basis for these calculations, are included in a separate document as a reference. * Fair Oaks Ranch Transformer #1 load is more than 80% of its normal rating since year 2017.
SCENIC LOOP AREA SUBSTATIONS FORECASTED LOAD GROWTH (kW)
LOCATION | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
La Sierra | 112525.6786 | 119051.7753 | 125956.5417 | 130995.0662 | 136234.836 | 141684.0652 | 145934.8582 | 150312.9696 | 154822.5066 | 159466.7547
Fair Oaks Ranch | 77880.6161 | 80756.0708 | 83755.531 | 86349.547 | 89028.6903 | 91452.6765 | 93616.8327 | 95833.4149 | 98105.4247 | 100433.6385
Total in the Area | 190406.2947 | 199807.8461 | 209712.0727 | 217344.6132 | 225263.5263 | 233136.7416 | 239551.6908 | 246146.3846 | 252927.9313 | 259900.3932
Year over Year Growth % | 4.919% | 4.938% | 4.957% | 3.64% | 3.643% | 3.495% | 2.752% | 2.753% | 2.755% | 2.757%
Normalised Growth % | 4.321% | 4.321% | 4.321% | 4.321% | 4.321% | 4.321% | 4.321% | 4.321% | 4.321% | 4.321%
Takeaways: Approximately 4.3% growth anticipated over next 10 years. The forecast is indicating 70 MW growth over next 10 years compared to a the growth over historical past 7 years. Growth of 5% for the near term 3 years, 4% for the mid term and 3% for the longer term within the 10 year plan. The % growth forecast is approximately 1/2 of the historical normalized growth. Based on CPS's planning experience, criteria and methodology - the forecast has no data to support any lower forecast than included in this submittal.

## Feeder Level Historical Peak
Takeaways: The data presented in this tab summarizes the peak loads reorded on the feeders served from La Sierra and FairOaks Ranch substations. Feeders that violate the loading criteria of CPS Energy are highlighted.
La Sierra Substation individual Historical annual peak loading (MW)
U111 | Normal Max | Date | U112 | Normal Max | Date | U113 | Normal Max | Date | U114 | Normal Max | Date | U132 | Normal Max | Date | U133 | Normal Max | Date | U134 | Normal Max | Date
2021 | 19.1 | 2021-09-21 | 2021 | 23.36 | 2021-02-15 | 2021 | 3.96 | 2021-06-25 | 2021 | 31.89 | 2021-02-15 | 2021 | 20.88 | 2021-02-15 | 2021 | 10.39 | 2021-07-02 | 2021 | 20.28 | 2021-09-06
2020 | 17.85 | 2020-07-10 | 2020 | 23.96 | 2020-07-13 | 2020 | 4.49 | 2020-01-05 | 2020 | 25.56 | 2020-05-19 | 2020 | 14.93 | 2020-07-13 | 2020 | 9.99 | 2020-07-20 | 2020 | 28.55 | 2020-05-19
2019 | 18.77 | 2019-07-12 | 2019 | 24.25 | 2019-08-13 | 2019 | 8.37 | 2019-06-29 | 2019 | 28.51 | 2019-08-13 | 2019 | 13.53 | 2019-08-12 | 2019 | 6.4 | 2019-08-05 | 2019 | 30.95 | 2019-08-13
2018 | 18.38 | 2018-09-19 | 2018 | 19.76 | 2018-07-23 | 2018 | 8.51 | 2018-07-04 | 2018 | 29 | 2018-07-23 | 2018 | 13.18 | 2018-07-23 | 2018 | 6.63 | 2018-07-24 | 2018 | 20.97 | 2018-02-12
2017 | 22.15 | 2017-06-23 | 2017 | 18.97 | 2017-07-29 | 2017 | 8.87 | 2017-06-17 | 2017 | 30.09 | 2017-07-29 | 2017 | 11.51 | 2017-09-20 | 2017 | 6.56 | 2017-07-20 | 2017 | 25.14 | 2017-07-30
2016 | 21.69 | 2016-08-12 | 2016 | 18.92 | 2016-08-12 | 2016 | 8.82 | 2016-07-01 | 2016 | 28.62 | 2016-08-12 | 2016 | - | - | 2016 | 6.75 | 2016-08-10 | 2016 | 28.3 | 2016-08-12
2015 | 23.13 | 2015-02-23 | 2015 | 29.49 | 2015-08-11 | 2015 | 8.64 | 2015-07-24 | 2015 | 27.08 | 2015-08-11 | 2015 | - | - | 2015 | 6.58 | 2015-07-17 | 2015 | 17.91 | 2015-02-23
2014 | 16.58 | 2014-10-02 | 2014 | 17.38 | 2014-08-11 | 2014 | 8.44 | 2014-07-26 | 2014 | 25.67 | 2014-01-07 | 2014 | - | - | 2014 | 6.32 | 2014-08-20 | 2014 | 21.47 | 2014-09-10
Fair Oaks Ranch Substation individual Historical annual peak loading (MW)
R011 | Normal Max | Date | R012 | Normal Max | Date | R013 | Normal Max | Date | R014 | Normal Max | Date | R033 | Normal Max | Date | R034 | Normal Max | Date
2021 | - | - | 2021 | - | - | 2021 | 12.55 | 2021-02-15 | 2021 | 26.92 | 2021-02-15 | 2021 | 22.57 | 2021-02-15 | 2021 | 23.66 | 2021-02-15
2020 | 13.31 | 2020-02-27 | 2020 | - | - | 2020 | 12.59 | 2020-07-13 | 2020 | 19.34 | 2020-07-13 | 2020 | 12.96 | 2020-12-17 | 2020 | 15.12 | 2020-07-13
2019 | 14.11 | 2019-12-19 | 2019 | 22.13 | 2019-03-04 | 2019 | 12.93 | 2019-08-13 | 2019 | - | - | 2019 | - | - | 2019 | 9.22 | 2019-08-12
2018 | 12.72 | 2018-01-03 | 2018 | 27.35 | 2018-01-03 | 2018 | 12.28 | 2018-07-23 | 2018 | - | - | 2018 | - | - | 2018 | - | -
2017 | 12.33 | 2017-01-08 | 2017 | 25.89 | 2017-01-07 | 2017 | 11.58 | 2017-07-30 | 2017 | - | - | 2017 | - | - | 2017 | - | -
2016 | 9.29 | 2016-02-05 | 2016 | 21.83 | 2016-08-12 | 2016 | 10.49 | 2016-12-19 | 2016 | - | - | 2016 | - | - | 2016 | - | -
2015 | 9.8 | 2015-03-05 | 2015 | 22.56 | 2015-03-05 | 2015 | 7.15 | 2015-03-05 | 2015 | - | - | 2015 | - | - | 2015 | - | -
2014 | 12.14 | 2014-01-07 | 2014 | 26.25 | 2014-01-07 | 2014 | 8.26 | 2014-01-07 | 2014 | - | - | 2014 | - | - | 2014 | - | -

## TR Level Historical Peak
La Sierra
TR#1 (U1T1) Peak | Date & Time | Load (MW) | TR#3 (U1T3) Peak | Date & Time | Load (MW) | Please note that the sum of peak values of all transformers is not equal to the substation peak. This is because not all transformers are peak at the same time and there is always a coincidence factor. In addition, there may be a load shift from one circuit to another circuit/station. This is also true for the sum of all peak circuit loads of the transformer and transformer peak itself. They are not equal.
2014 | 2014-08-08 16:44 | 61.55 | 2014 | 2014-09-10 18:20 | 24.19
2015 | 2015-07-26 | 76.89 | 2015 | 2015-08-11 | 23.34
2016 | 2016-08-12 | 75.85 | 2016 | 2016-08-12 | 34.14
2017 | 2017-07-29 | 74.13 | 2017 | 2017-07-30 | 30.4
2018 | 2018-07-24 | 69.12 | 2018 | 2018-07-23 | 39.61
2019 | 2019-09-22 | 83.12 | 2019 | 2019-08-12 | 46.66
2020 | 2020-07-10 | 63.3 | 2020 | 2020-05-19 | 44.3
2021 | 2021-02-15 09:41 | 63.72 | 2021 | 2021-06-13 17:54 | 40.74
Fair Oaks Ranch
TR#1 (R0T1) Peak | Date & Time | Load (MW) | TR#3 (R0T3) Peak | Date & Time | Load (MW)
2014 | 2014-01-07 07:46 | 46.05 | 2014 |  | 0
2015 | 2015-03-05 | 38.88 | 2015 |  | 0
2016 | 2016-12-19 | 44.6 | 2016 |  | 0
2017 | 2017-12-08 | 41.01 | 2017 |  | 0
2018 | 2018-01-17 | 50.24 | 2018 |  | 0
2019 | 2019-03-05 | 45.78 | 2019 | 2019-08-11 | 22.83
2020 | 2020-07-13 | 42.16 | 2020 | 2020-12-14 | 19.77
2021 | 2021-02-15 06:59 | 39.11 | 2021 | 2021-02-15 07:02 | 46.6