## MonthlyReportForm-AEPTX Central
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
41913060 | TPCO Dupont Station Relay Upgrades | San Patricio | Dupont Substation Relay/Protection | 2014-10-01 | 2019-10-21 |  |  | 879000 |  |  | 66 | [9 empty] | 16 TAC 25.83(a)(3)
42805106 | Shaffer Collector Station | Nueces | Install RTU, SDR and DME equipment in generator-owned station. | 2018-02-18 | 03/19/2019 |  |  | 639700 |  |  | 40 | 345 | [8 empty] | 16 TAC 25.83(a)(3)
42274263 | Tortuga | Nueces | New 138-kV Station | 2017-02-01 | 10/15/2019 |  |  | 4233000 |  |  | 80 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
42338741 | Tortuga | Nueces | Cut-in the AEP Upriver to Gila Line into New Tortuga Sub | 09/15/2017 | 10/15/2019 |  |  | 2593000 |  |  | 90 | 138 | 138 | [7 empty] | 16 TAC 25.101 (c)(5)(A) | Landowner consent
42502134 | Harlingen SS - Raymondville #2 69-kV Rebuild | Cameron Willacy | Rebuild 22.50 miles of 69-kV transmission line 138-kV capability & partial relocation pursuant to previous contractual obligations. | 2017-03-10 | 2017-11-01 | 2017-11-21 |  | 23646065 |  |  | 99 | 69 |  | 22.81 | 959.6 ACSS/TW | Steel Mono Pole | varies | 22.81 | 100 | 1.72 | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.101 (c)(5)(E) | Landowners Noticed. Consent and new easements & supplements were acquired as necessary.
42499311 | El Campo Station | Wharton | Replace relays (in conjunction w/ Project No. 42501676). | 03/15/2018 | 05/15/2018 |  |  | 6251145.51 |  |  | 75 | 138/69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42501676 | Lane City Station | Wharton | Replace EM Relays and assoc Panel on 138-kV CB 6485 and PVDs relays (in conjunction w/ Project No. 42499311). | 03/15/2018 | 05/15/2018 | 10/28/2018 |  | 1163678 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42633615 | Tuleta to Coleto Creek 138-kV Dbl Ckt Line | Goliad Bee | Construct new 48 mile 138-kV Double-Circuit capable transmission line from Tuleta to the New Euler Station to the Coleto Creek Substation. | 2017-11-06 | 12/31/2018 |  | 62625000 | 54546000 |  |  | 99 |  | 138 | 48 | 959 kcmil ACSR/TW | Steel Single Pole |  |  | 100 | 48 | 44837 | Construct a 11 mile 138-kV transmission line between Tuleta Station and the Proposed Euler Station, and a 37 mile 138-kV transmission line between the New Euler Station and Coleto Creek Station.
42612169 | Westside Substation | Corpus Christi/Nueces | Upgrade breaker and switches. | 2017-11-02 | 03/31/2019 |  |  | 2624458 |  |  | 80 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42623730 | West Oso Substation | Corpus Christi/Nueces | Upgrade breaker and switches. | 11/20/2017 | 02/28/2019 |  |  | 501084 |  |  | 15 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42595936 | Yosemite 69-kV Relocate | San Patricio | Gregory to Rincon: Two mile relocate per Landowner Request. | 2017-11-02 | 2018-01-31 | 2018-01-31 |  | 3470312 |  |  | 99 | 69 |  | 2.1 | 795 ACSR/AW | Steel Mono Pole | varies | 2.1 | 100 | 2.1 | 16 TAC 25.101 (c)(5)(D) | Written consent acquired from landowner with the right to construct. 100% CIAC
42606712 | Yosemite Dupont - Portland Relocate | San Patricio | Relocate section into ductbank for heavy haul road clearance. | 2018-09-24 | 2019-01-20 | 2019-01-21 |  | 3701410 |  |  | 99 | 138 |  | 0.11 | 2 - 795 ACSR/AW | Steel Mono Pole | 100 | 0.11 | 100 | 0.11 | 16 TAC 25.101 (c)(5)(D) | Written consent from landowner. 100% CIAC.
42606710 | Yosemite Whitepoint - Dupont #1 Relocate | San Patricio | Relocate section into ductbank for heavy haul road clearance. | 2018-09-24 | 2019-03-30 | 2019-04-15 |  | 6478523 |  |  | 99 | 138 |  | 0.13 | 795 ACSR/AW | Steel Mono Pole | 100 | 0.13 | 100 | 0.13 | 16 TAC 25.101 (c)(5)(D) | Written consent from landowner. 100% CIAC.
42726987 | Yosemite Whitepoint - Dupont #2 Relocate | San Patricio | Relocate section into curcuit #1's ductbank for heavy haul road clearance. | 2018-09-24 | 2019-04-30 | 2019-04-15 |  | 2943611 |  |  | 99 | 138 |  | 0.13 | 795 ACSR/AW | Steel Mono Pole | 100 | 0.13 | 100 | 0.13 | 16 TAC 25.101 (c)(5)(D) | Written consent from landowner. 100% CIAC.
42657137 | Pharr Station Expansion | Pharr/Hidalgo | Expand Station: Add (3) 138-kV breakers, (6) CCVT's, (6) 138-kV arrestors, bus work, deadends, and metering which will provide two independent 138-kV feeds to the ABB STATCOM. Install fourth ring to accommodate the SVC connections. | 2018-02-15 | 2018-12-31 |  |  | 3334240 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within acquired station property
42585400 | Pharr SVC Station | Pharr/Hidalgo | Construct SVC station on new land purchased adjacent to existing station. Install two +150/-75 MVAR SVCs for a total of +300/-150 MVAR. | 2018-01-01 | 2018-12-31 |  |  | 39572390 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
42652433 | Pharr SVC Bus Tie #1 | Pharr/Hidalgo | Construct bus tie #1 from existing 138-kV Pharr substation to SVC Yard. | 2018-02-15 | 2018-12-31 |  |  | 614918 |  |  | 99 |  | 138 | 0.15 | 959.6 ACSS/TW | Steel Mono Pole |  |  |  |  | 16 TAC 25.83(a)(3) | Within station property
42652435 | Pharr SVC Bus Tie #2 | Pharr/Hidalgo | Construct bus tie #2 from existing 138-kV Pharr substation to SVC Yard. | 2018-02-15 | 2018-12-31 |  |  | 573917 |  |  | 99 |  | 138 | 0.15 | 959.6 ACSS/TW | Steel Mono Pole |  |  |  |  | 16 TAC 25.83(a)(3) | Within station property
42652438 | Pharr - Polk Ave Transmission Line Relocate | Pharr/Hidalgo | Relocate the Pharr to Polk Ave 138-kV transmission line, one line position east between Breaks 1705 & 1715 at the Pharr Substation. | 2018-02-15 | 2018-12-31 |  |  | 217180 |  |  | 99 | 138 |  | 0.15 | 959.6 ACSS/TW | Steel Mono Pole |  |  |  |  | 16 TAC 25.83(a)(3) | Within station property
42654266 | Pharr - MVEC Transmission Line Relocate | Pharr/Hidalgo | Relocate the Pharr to MVEC 138-kv transmission line, one line position east of the newly installed fourth ring at the Pharr Substation. | 2018-02-15 | 2018-12-31 |  |  | 217180 |  |  | 99 | 138 |  | 0.15 | 959.6 ACSS/TW | Steel Mono Pole |  |  |  |  | 16 TAC 25.83(a)(3) | Within station property
42630431 | Victoria Dupont Breaker Changeout | Victoria | Replace CBs 9710, 9720, 9730, 9740, 9750, and 9760 (and associated switches). | 2018-03-12 | 2018-12-10 |  |  | 2952290 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42623024 | Rockport - Fulton 69-kV Rebuild | Rockport/Aransas | Rebuild and reconductor the Rockport to Fulton 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-03-15 | 2018-12-14 |  |  | 19237914 |  |  | 99 | 69 |  | 7.51 | 795 KCM ACCS "Drake" | Steel Mono Pole | Centerline | 7.51 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilize existing easements. Consent obtained where necessary. Landowners noticed.
42612156 | Refugio Substation: Install DICM | Refugio | Install new DICM at Refugio Substation, equipped with new line protection, and bus protection panels, RTU, DME. Purchase Property for Expansion. | 2018-04-15 | 2018-09-30 | 2018-12-21 |  | 2642609 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Property for Expansion Purchased
42629713 | Calallen (STEC) - Banquete 69-kV Rebuild | Corpus Christi/Nueces | Rebuild and reconductor the Calallen (STEC) to Banquete 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-05-28 | 2019-05-28 | 2019-05-28 |  | 8151812.58 |  |  | 99 | 69 |  | 12.7 | 795 KCM ACCS "Drake" | Concrete Mono Pole | Centerline | 12.7 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42630262 | Premont - Falfurrias 69-kV Rebuild | Jim Wells Falfurrias/Brooks | Rebuild and reconductor the Premont to Falufrrias 69-kV transmission line to 138-kv standards. Will continue to operate at 69 kV. | 2018-06-05 | 2020-06-07 | 2020-05-11 |  | 8000000 |  |  | 99 | 69 |  | 12.25 | 795 KCM ACCS "Drake" | Concrete Mono Pole | Centerline | 12.25 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42629781 | Three Rivers - Sunniland 69-kV Rebuild | Live Oak | Rebuild and reconductor the Three Rivers to Sunniland 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-07-13 | 2018-12-12 | 2018-12-20 |  | 5039296.6 |  |  | 99 | 69 |  | 7.2 | 795 KCM ACCS "Drake" | Steel Mono Pole | 50 | 7.2 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42629715 | Banquete - Stadium 69-kV Rebuild | Nueces Alice/Jim Wells | Rebuild and reconductor the Banquete to Stadium 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-07-25 | 2020-02-01 | 2020-02-25 |  | 15140894 |  |  | 99 | 69 |  | 16.96 | 795 KCM ACCS "Drake" | Concrete Mono Pole | Centerline | 16.96 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42736720 | Reading Substation: T-station Assets | Uvalde/Uvalde | Construct the 138-kV side of the Reading Substation including the installation of a 145 kV, 3000A, 40kA, 125VDC circuit switcher, in & out transmission bus work with two motor-operated switches, a manual bus tie switch, a switch on second bus terminal for future transformer, and a Wave Trap. | 2018-07-05 | 2019-04-30 | 2019-06-27 |  | 992451 |  |  | 99 |  | 138 |  | . | [5 empty] | 16 TAC 25.83(a)(3) | Property purchased
42736418 | Reading Substation: T-line Assets | Uvalde/Uvalde | Cut-in the Moore to Uvalde 138-kV transmission line into new Reading Substation. | 2018-07-05 | 2019-04-30 | 2019-06-07 |  | 798381 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42749716 | Whitepoint - STP (Emergency Project) | Refugio Victoria Calhoun | Replace 131 H-Frame Strom-Damaged 345-kV Structures along 27 miles of the AEP Texas Whitepoint to STP 345-kV transmission line. | 2017-12-14 | 2018-05-15 | 2018-05-15 |  | 49500000 |  |  | 99 | 345 |  |  |  | H-Frame Tubular Steel |  |  |  |  | 16 TAC 25.101 (c)(3) | Emergency Project (Hurricane Harvey Storm Damage)
42625110 | Blessing - Palacios 69-kV Rebuild | Matagorda | Rebuild and reconductor the Blessing to Palacios 69-kV transmission line to 138-kv standards. Will continue to operate at 69 kV. | 2018-08-05 | 2018-12-22 | 2019-02-11 |  | 9566153 |  |  | 99 | 69 |  | 9.8 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 9.8 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42630260 | N. Ella - Premont 69-kV Rebuild | Jim Wells | Rebuild and reconductor the N. Ella to Premont 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-08-05 | 2021-01-06 | 2020-12-15 |  | 8600000 |  |  | 99 | 69 |  | 10.47 | 795 KCM ACSS "Drake" | Concrete Mono Pole | Centerline | 10.47 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42692219 | Refugio - Heard Tap 69-kV Rebuild | Refugio/Refugio | Rebuild and reconductor the Refugio to Heard Tap 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-08-05 | 2018-10-21 | 2018-11-15 |  | 5131549 |  |  | 99 | 69 |  | 2.45 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 2.45 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42628938 | Turtle Creek - La Pryor 69-kV Rebuild | La Pryor/Zavala | Rebuild and reconductor the Turtle Creek to La Pryor 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-09-17 | 2019-11-11 | 2019-11-19 |  | 14890616.55 |  |  | 99 | 69 |  | 14.37 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 14.37 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42625121 | Heard Tap - Woodsboro 69-kV Rebuild | Refugio | Rebuild and reconductor the Heard Tap to Woodsboro 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-09-03 | 2018-12-01 | 2018-12-27 |  | 4572319 |  |  | 99 | 69 |  | 2.7 | 795 KCM ACSS "Drake" | Steel Mono Pole | 50 | 2.7 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42625122 | Woodsboro - Bonnieview 69-kV Rebuild | Refugio | Rebuild and reconductor the Woodsboro to Bonnieview 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-10-04 | 2019-02-10 | 2019-03-05 |  | 4572319 |  |  | 99 | 69 |  | 5.45 | 795 KCM ACSS "Drake" | Steel Mono Pole | 50 | 5.45 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42813702 | Karankawa I Windfarm: Goddard 345-kV Station | San Patricio | Construct new 3 breaker 345-kV ring bus station, expandable to breaker and a half, along the Lon Hill to Pawnee (STEC) 345-kV transmission line. | 2018-10-15 | 2019-04-30 | 2019-10-18 |  | 16995361 | 15901825 | -6.434% | 100 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Obtained written consent to construct from Landowner.
42817776 | Karankawa I Windfarm: Lon Hill 345-kV Station | San Patricio | Upgrade relays to accommodate new Goddard Station. | 2019-02-15 | 2019-04-30 | 2019-10-18 |  | 647531 | 535160 | -17.35% | 100 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42817784 | Karankawa I Windfarm: Jarvik 345-kV Station (Generator-Owned) | San Patricio | Install SDR, ME and RTY at generator's collector station. | 2019-02-15 | 2019-04-30 | 2019-10-22 |  | 640653 | 111503 | -82.6% | 100 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within generator-owned station property
42629736 | Coy City Tap - Sunniland 69-kV Rebuild | Live Oak Atacosa | Rebuild and reconductor the Sunniland to Coy City Tap 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-11-14 | 2019-02-07 | 2019-10-02 |  | 11607446 |  |  | 99 | 69 |  | 16.19 | 795 KCM ACSS "Drake" | Steel Mono Pole | 50 | 16.19 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42625111 | Palacios - Carancahua 69-kV Rebuild | Matagorda Jackson | Rebuild and reconductor the Palacios to Carancahua 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-12-22 | 2019-05-27 | 2019-05-14 |  | 9937197 |  |  | 99 | 69 |  | 13.25 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 13.25 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42625123 | Bonnieview - Rincon 69-kV Rebuild | Refugio | Rebuild and reconductor the Bonnieview to Rincon 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-12-04 | 2019-06-01 |  |  | 21910248.63 |  |  | 80 | 69 |  | 11.97 | 795 KCM ACSS "Drake" | Steel Mono Pole | 50 | 11.97 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42629734 | Pleasanton - Coy City Tap 69-kV Rebuild | Pleasanton/Atascosa | Rebuild and reconductor the Pleasanton to Coy City Tap 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-12-03 | 2020-03-21 | 2020-03-27 |  | 18603950 |  |  | 99 | 69 |  | 17.3 | 795 KCM ACSS "Drake" | Steel Mono Pole | 50 | 17.3 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42729406 | Uvalde - Campwood 69-kV Rebuild | Uvalde/Uvalde Campwood/Real | Rebuild and reconductor the Uvalde to Campwood 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-12-02 | 2021-03-01 |  |  | 47846000 |  |  | 75 | 69 |  | 37 | 795 KCM ACSS "Drake" | Steel Mono Pole | varies | 37 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42641112 | Alice - N. Ella 69-kV Rebuild | Alice/Jim Wells | Rebuild and reconductor the Alice to N. Ella 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-12-02 | 2021-04-29 | 2021-04-08 |  | 7500000 |  |  | 99 | 69 |  | 14.3 | 795 KCM ACSS "Drake" | Concrete Mono Pole | varies | 14.3 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42851421 | Karankawa I Windfarm: Tie-Line between new Goddard Station and Generator-Owned Jarvik Station | San Patricio | Install 0.10 mile of single-circuit 345-kV transmission line and OPGW to connect new Goddard Station to Generator-Owned Jarvik Station. | 2019-03-04 | 2019-04-30 | 2019-10-22 |  | 502334 | 438321 | -12.74% | 100 |  | 345 | 0.1 | 2-954 ACSR "Cardinal" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Transmission line within station properties. No additional easement requires.
42851413 | Karankawa I Windfarm: Cut-in to new Goddard Station | San Patricio | Terminate the Lon Hill to Pawnee (STEC) 345-kV transmission line into new Goddard Station. | 2019-03-04 | 2019-04-30 | 2019-10-18 |  | 2203395 | 1943538 | -11.79% | 100 | 345 |  | 0.5 | 2-954 ACSR "Cardinal" | Steel Mono Pole |  |  | 150 | 0.5 | 16 TAC 25.101 (c)(5)(A) | Obtained written consent to construct from Landowner.
42867785 | Karankawa II Windfarm: Goddard 345-kV Station | San Patricio | Goddard 345-kV Station: Install 345-kV Terminal which includes a 5000A, 50kA Breaker, SSO Relay, EPS Metering, and relay setting changes. | 2019-01-02 | 2019-04-30 | 2019-10-18 |  | 2673314 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42867838 | Karankawa II Windfarm: Tie-Line between new Goddard Station and Generator-Owned Welder Station | San Patricio | Install 0.10 mile of single-circuit 345-kV transmission line and OPGW to connect Goddard Station to Generator-owned Welder Station. | 2019-01-02 | 2019-04-30 | 2019-10-22 |  | 481281 |  |  | 99 |  | 345 | 0.1 | 2-954 ACSR "Cardinal" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Transmission line within stattion properties. No additional easement required.
42620186 | Javelina 138-kV Substation: Replace MLSE equipment | Corpus Christi/Nueces | Upgrade breakers, switches, and jumpers on Westside SW line terminal. Install new CCTV's. | 2019-01-05 | 2019-05-27 |  |  | 1843785 |  |  | 35 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Existing Property
42628940 | La Pryor - Uvalde 69-kV Rebuild | La Pryor/Zavala, Uvalde/Uvalde | Rebuild and reconductor the La Pryor to Uvalde 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2018-12-15 | 2020-03-13 | 2020-03-30 |  | 10291081 |  |  | 99 | 69 |  | 17.27 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 17.27 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42729705 | Asherton Substation: Transmission Assets Upgrades 69-kV Rebuild | Asherton/Dimmit | Upgrade high-side fuse with circuit switcher at the asherton 138/69-kV Substation. | 2020-02-24 | 2019-03-30 |  |  | 473017 |  |  | 0 | 138/69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42798095 | Cebolla 345-kV Substation | Willacy | Construct new 345-kV ring bus station for a permanent POI for the Bruenning's Breeze Wind Farm. | 2019-02-25 | 2019-10-31 | 2020-12-17 |  | 14938312 |  |  | 99 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchases has been signed, but awaiting document completion. Document completion will be complete before start of construction.
42623718 | Airline Substation Rehab | Corpus Christi/Nueces | Add breakers and switches for the Laguna Substation and Naval Base GIS Substation terminals. Add bays for Transformers 1, 2, 3, and 4 for 138-kV conversion. | 2019-03-04 | 2019-05-29 | 2020-12-11 |  | 7245338 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42725434 | Heines Substation: T-Station Assets | Corpus Christi/Nueces | Install 138-kV switches, circuit switcher, and buswork for the 138-kV portion of the new Heines Substation. | 2019-04-01 | 2019-05-29 | 2020-06-01 |  | 1199361 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42811629 | Heines Substation: T-Line Assets | Corpus Christi/Nueces | Install AEP Texas transmission fiber cable from LCRA Airline to Naval Base GIS 69-kV transmission line into new Heines substation. | 2019-04-01 | 2019-05-29 | 2020-06-01 |  | 1426191 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3)
42660796 | Gregory - Rincon 69-kV Rebuild | San Patricio | Partially rebuild and reconductor the Gregory to Rincon 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2019-04-06 | 2019-12-31 |  |  | 6500000 |  |  | 10 | 69 |  | 4.37 | 795 KCM ACSS "Drake" | Steel Mono Pole | 50 | 4.37 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42892575 | Pirate Substation: T-Station Assets | Sinton/San Patricio | Construct the 69-kV side of the Pirate Substation including the in & out transmission line work with two motor-operated switches, a manual bus tie switch, a switch on second bus terminal for futrue transformer, a Wave Trap. | 2019-05-01 | 2020-03-01 | 2020-02-11 |  | 2245202 |  |  | 35 |  | 69 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
42623720 | Naval Base GIS Station | Corpus Christi/Nueces | Reconfigure the Naval Base GIS station to be 138-kV with the Auto feeding the 69 kV line to North Padre Island. | 2019-05-29 | 2019-09-06 | 2020-09-02 |  | 1652000 |  |  | 99 | 69 | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
42817198 | Gibbs 138-kV Station | San Patricio | Construct a six (6) Breaker Ring Bus expandable to Breaker and a Half configuration to serve for GCGV owned Transformers. | 2019-05-09 | 2019-12-10 |  |  | 8264697 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | CIAC to be collected for cost of station. Land provided under long term lease.
42891917 | Gibbs to GCGV Circuit 1 T-Line | San Patricio | Install T-Line Structure outside of Gibbs 138-kV Substation Fence. This T-Line structure will serve as a Point of Interconnect (POI). Install conductor between Gibbs Substation and T-Line Sturcture. | 2019-05-09 | 2019-12-10 |  |  | 377801 |  |  | 99 |  | 138 | 0.01 | 477 ACSR/AW "Hawk" | Steel H-Frame |  |  |  | 0.01 | 16 TAC 25.101 (c)(5)(A) | CIAC to be collected for cost of station. Land provided under long term lease.
42894987 | Gibbs to GCGV Circuit 2 T-Line | San Patricio | Install T-Line Structure outside of Gibbs 138-kV Substation Fence. This T-Line structure will serve as a Point of Interconnect (POI). Install conductor between Gibbs Substation and T-Line Sturcture. | 2019-05-09 | 2019-12-10 |  |  | 377801 |  |  | 99 |  | 138 | 0.01 | 477 ACSR/AW "Hawk" | Steel H-Frame |  |  |  | 0.01 | 16 TAC 25.101 (c)(5)(A) | CIAC to be collected for cost of station. Land provided under long term lease.
42888098 | Gibbs to GCGV Circuit 3 T-Line | San Patricio | Install T-Line Structure outside of Gibbs 138-kV Substation Fence. This T-Line structure will serve as a Point of Interconnect (POI). Install conductor between Gibbs Substation and T-Line Sturcture. | 2019-05-09 | 2019-12-10 |  |  | 377801 |  |  | 99 |  | 138 | 0.01 | 477 ACSR/AW "Hawk" | Steel H-Frame |  |  |  | 0.01 | 16 TAC 25.101 (c)(5)(A) | CIAC to be collected for cost of station. Land provided under long term lease.
42888099 | Gibbs to GCGV Circuit 4 T-Line | San Patricio | Install T-Line Structure outside of Gibbs 138-kV Substation Fence. This T-Line structure will serve as a Point of Interconnect (POI). Install conductor between Gibbs Substation and T-Line Sturcture. | 2019-05-09 | 2019-12-10 |  |  | 377801 |  |  | 99 |  | 138 | 0.01 | 477 ACSR/AW "Hawk" | Steel H-Frame |  |  |  | 0.01 | 16 TAC 25.101 (c)(5)(A) | CIAC to be collected for cost of station. Land provided under long term lease.
42888102 | Gibbs 138-kV Cut-in | San Patricio | Construct approximately 0.87 mile double circuit cut-in to the existing Dupont to White Point Ckt#3 138-kV line from Gibbs 138-kv Station. | 2019-05-09 | 2019-12-10 |  |  | 2288847 |  |  | 99 |  | 138 | 1.74 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.87 | 16 TAC 25.101 (c)(5)(A) | Partial CIAC to be collected for cost of station. Land provided under long term lease.
42885861 | Raymond Wind Permanent Interconnection: Bonilla 345-kV Station | Cameron | Construct a new 345-kV expandable breaker and a half configuration station with three (3) breakers and SSO Relay. | 2019-07-14 | 2020-01-19 |  |  | 24500000 |  |  | 0 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
42757777 | Causeway 138-kV Substation: T-Station Assets | Port Isabel/Cameron | Replace 138-kV Circuit Switcher, extend bus to install new MOAB and create second terminal. Update remote relay settings. | 2019-06-17 | 2019-11-30 | 2020-03-27 |  | 980106 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42625112 | Carancahua - Pt. Comfrot 69-kV Rebuild | Jackson, Pt.Comfort/Calhoun | Partially rebuild and reconductor the Carancahua to Pt. Comfort 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2019-07-04 | 2019-12-31 |  |  | 12300000 |  |  | 15 | 69 |  | 9.25 | 795 KCM ACSS/AW "Drake" | Steel Mono Pole | Centerline | 9.25 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42725410 | Hamilton Rd. - Picacho 138-kV Rebuild | DelRio/Val Verde | Rebuild and reconductor the Hamilton Rd. to Picacho 138-kV transmission line. | 2019-07-08 | 2020-03-31 |  |  | 13290374 |  |  | 0 | 138 |  | 8.8 | 795 KCM ACSS/AW "Drake" | Steel Mono Pole | Centerline | 8.8 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42869661 | Weaver Road - Greenlake 69-kV Line Relocate for Port of Victoria | Victoria | Weaver Rd. to Greenlake 69-kV Line: Relocate transmission line structures 11/5, 11/6, and 11/7 for Port of Victoria's McCoy Road improvement project. | 2019-07-29 | 2019-10-18 | 2019-12-31 |  | 1001652 |  |  | 99 | 69 |  |  | 477 ACSR/AW "Hawk" | Steel Two-Pole & Steel Three-Pole | 100 | 0.18 | 100 | 0.18 | 16 TAC 25.101 (c)(5)(F) | Landowner consent obtained
42400057 | Bates -Garza 138-kV Relocation for TxDOT | McAllen/Hidalgo | Replace T-Line structures 3/5 & 3/6 with 3-pole dead end structures to increase the line height to allow for increased ROW width and elevated road. | 2019-09-13 | 2019-11-06 | 2019-11-04 |  | 1629267 |  |  | 99 | 138 |  |  | 477 ACSR/AW "Hawk" | Steel Three-Pole | Centerline |  |  |  | 16 TAC 25.101 (c)(5)(F) | Project is 100% Reimburseable. Landowners Noticed.
42885856 | Cranell wind Permanent Interconnect (Grissom 345-kV Substation) | Sinton/Refugio | Construct new 345-kV, 4000A, 50kA breaker and a half configuration substation along the Lon Hill to Coleto Creek 345-kV transmission line to interconnect a 220 MW wind generating facility. | 2019-10-04 | 2020-04-01 |  |  | 25900000 |  |  | 0 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Permanent easement obtained from Wind Developer
42658083 | Young 138-kV Substation: T-Line Assets | Edinburg/Hidalgo | Terminate the Pharr to Pole Ave 138-kV transmission line into the new Young 138-kV Substation. | 2019-11-15 | 2020-01-31 |  |  | 997917 |  |  | 99 | 138 |  | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42660915 | Young 138-kV Substation: T-Station Assets | Edinburg/Hidalgo | Install (2) 138-kV circuit switcher off of two buses with MOAB switches and associated 138 kV breaker bus work at the new Young 138-kV Substation. | 2019-10-04 | 2020-01-31 |  |  | 1141804 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
42821552 | Bunsen 138-kV Substation: Texstar Epic Y Grade Interconnect | Corpus Christi/Nueces | Construct approximately 0.75 miles of new double-circuit 138-kV transmission line from Bunsen Substation to Texstar's 138-kV Substation (Customer-Owned) to serve Epic Y Grade's Project of 21MW peak load. | 2019-10-28 | 2019-12-31 |  |  | 1085717 |  |  | 95 |  | 138 | 0.9 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.9 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
42949972 | Rio Hondo - Majadas 345-kV Transmission Line | Cameron Willacy | Construct a new 9.44 mile 345-kV transmission line from AEP Texas' Rio Hondo Switch Station to generator's (Las Majadas Wind Farm, LLC) Majadas 345-kV Substation. | 2019-12-10 | 2020-09-30 | 2020-08-25 | 18822576 | 27391061 |  |  | 98 |  | 345 | 9.44 | 954 KCM ACSR "Cardinal" | Steel Mono Pole |  |  | 150 | 9.44 | 48710 | CCN Approved 02/06/2019. Project site access found shallow water table throughout porject impaction structure and foundation design and construction cost.
42651863 | Port Isabel - Causeway 69-kV Rebuild | Laguna Vista, Port Isabel/Cameron | Rebuild and reconductor the Port Isabel to Causeway 138-kV transmission line. | 2019-11-04 | 2019-12-31 | 2020-08-08 |  | 21200000 |  |  | 99 | 138 |  | 6.67 | 795 KCM ACSS "Drake" | Steel Mono Pole | varies | 6.67 |  |  | 16 TAC 25.101 (c)(5)(B) | Landownder Noticed
42841652 | Dupont Switching Station: T-Station Assets | San Patricio | Dupont Switching Station: Expand station by adding breakers and other equipment to permanetly connect new Generator. | 2019-11-04 | 2021-01-15 | 2021-03-24 |  | 5663923 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42876413 | Pavlov 138-kV Substation | Matagorda | Construct a new three (3) Switch In & Out 138-kV Switching Substation. Install two(2) Circuit-Switchers, DICM, SCADA, Telecom, communication Equipment, & Relay Panels. | 2019-11-04 | 2020-05-01 |  |  | 1337489 |  |  | 95 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42921257 (P18209001) (P19209002) (P18209011) | Angstrom 345-kV Station | San Patricio | Construct a new 345-kV station with three (3) breaker ring bus for the future cut-in of the STP to Whitepoint 345 kV transmission line and service to a new customer substation. Added two (2) 50MVA Reactors. | 2020-01-04 | 2021-01-26 | 2021-01-26 |  | 22779000 |  |  | 99 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Customer provided property and access, partial CIAC provided.
42921280 | Whitepoint - STP 345-kV T-Line for Angstorm Cut-in | San Patricio | Terminate the Whitepoint to STP 345-kV transmission line into new Angstrom 345-kV Substation. | 2020-07-05 | 2021-01-26 | 2021-01-26 |  | 6138676 |  |  | 99 | 345 |  | 1 | 2 - 954 ACSR "Cardinal" | Steel Mono Pole |  |  | 300 | 0.5 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained Partial CIAC Provided
42761499 | Carrizo Springs - Crystal City 69-kV | Dimmit, Crystal City/Zavala | Rebuild and reconductor the Carrizo Springs to Crystal City 69-kV tranmission line to 138-kV standards. Will continue to operate at 69 kV. | 2020-02-03 | 2021-03-31 |  |  | 23089564 |  |  | 0 | 69 |  | 12.74 | 795 KCM ACSS "Drake" | Steel Mono Pole | varies | 12.74 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
43011798 | Rayos Del Sol Solar Interconnection: Luna 138-kV Substation | Cameron | Construct a new 138-kV Substation (Luna) and install three breakers and switches for a three breaker-ring bus station, EPS Metering, SSO Relaying, and Line relaying. | 2020-02-14 | 2020-07-31 | 2021-06-08 |  | 7985920 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property acquired
42926334 | Shakes Solar Interconnect: Asherton 138-kV Substation Expansion | Asherton/Dimmit | Expand Substation. Install 138-kV, 3000A, 40kA Breaker, breaker & disconnect switches. Add SSO Relaying, Line Relaying, & EPS Metering. | 2020-02-23 | 2020-04-30 |  |  | 1340347 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42906770 | Cabaniss 138-kV Substation: Add Second Bank T-Station Assets | Corpus Christi/Nueces | Upgrade RTU & Install Circuit Breaker. | 2020-03-06 | 2020-05-12 | 2020-06-09 |  | 622236 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
42909503 | Resaca 69-kV Substation: T-Station Assets | San Benito/Cameron | Construct 69-kV In &Out bus with manual bus tie switch for singel bank station. Accommodate space on bus on for future installation of breakers. Install (2) 69-kV Circuit Switchers, and all associated material install (2) 69-kV MOABs for the line terminals. Install Transmission RTU. | 2020-03-06 | 2020-06-15 | 2020-06-24 |  | 1377431 |  |  | 99 |  | 69 | [7 empty] | 16 TAC 25.83(a)(3) | Property acquired
42914845 | Resaca 69-kV Substation: T-Line Assets | San Benito/Cameron | Terminate the La Palma to Brownsville SS 69-kV transmission line into new Resaca Substation. | 2020-03-06 | 2020-06-15 | 2020-05-18 |  | 790805 |  |  | 99 | 69 |  | 0.02 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Public ROW and Station property
43009650 | Shakes Solar Interconnection: Asherton - Escondido 138-kV T-Line | Asherton/Dimmit | Construct POI for LCRA outside Asherton 138-kV Substation and reterminate the transmission line into the substation. | 2020-04-05 | 2020-04-30 |  |  | 628669 |  |  | 0 |  | 138 | 0.06 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.83(a)(3) | Within station property
42943319 | Primera Substation: T-Station Assets | Harlingen/Cameron | Construct 138-kV In & Out Bus with manual bus tie switch for single bank station. Install 1 - 138-kV circuit switcher, 2 - 138-kV breakers, & transmission RTU. | 2020-04-15 | 2020-06-19 |  |  | 2333263 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
T10086661 (DP20X07D0) | Pantera 138-kV Substation: T-Station Assets | Weslaco/Hidalgo | Install 2-138-kV circuit switcher off of each bus. Install Multiplexor, 2–Breakers & Bus-Tie Breaker. Ultimate layout in a 4-breaker 138-kV Ring Bus. | 2020-05-04 | 2021-03-23 | 2021-06-18 |  | 2367954 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
T10084785 (DP20X07C0) | Pantera 138-kV Substation: T-Line Assets | Weslaco/Hidalgo | Termiinate Weslaco - Wesmer SS 138-kV transmission line into new Pantera 138-kV Substation | 2020-05-04 | 2021-03-23 | 2021-06-18 |  | 1009261 |  |  | 99 |  | 138 | 0.1 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42977511 (P19034007) | Las Lomas Wind Interconnection: Revilla 138-kV Substation | Zapata | Construct a three-breaker ring bus 138-kV substation with three (3) 3000A, 40kA breakers. Install RTU, DICM, Wave traps. Install SSO relay, EPS metering. | 2020-05-18 | 2020-11-30 | 110/5/2020 |  | 12114379 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
42977096 (P19034004) | Las Lomas Wind Interconnection: Lopeno-Falcon 138-kV Line Cut-In | Zapata | Terminate the Lopeno - Falcon SW 138-kV transmission line into new Revilla 138-kV Substation | 2020-05-18 | 2020-11-30 | 110/5/2020 |  | 1854179 |  |  | 99 |  | 138 | 0.2 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42983330 (P19034005) | Las Lomas Wind Interconnection: Revilla-Venado 138-kV Tie-Line | Zapata | Construct approximately 0.10 mile of 138-kV transmisison line span from new Revilla 138-kV Substation to Las Lomas Wind's Venado Substation POI. | 2020-05-18 | 2020-11-30 | 110/5/2020 |  | 1489633 |  |  | 99 |  | 138 | 0.1 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42798105 (P15091015) | Ajo - Rio Hondo 345-kV Line: Cut-In to Cebolla 345-kV Station | Willacy | Terminate the Ajo - Rio Hondo 345-kV transmission line into new Cebolla 345-kV Subtation | 2020-06-04 | 2020-10-01 | 2020-12-17 |  | 1788455 |  |  | 99 |  | 345 | 0.2 | 954 KCM ACSR "Cardinal" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42882728 (P15091017) | Cebolla - Ladekidde 345-kV Line: POI Tie-Line | Willacy | Construct approximately 0.10 mile of 345-kV transmisison line span from new Cebolla 345-kV Substation to Bruenning's Breeze's Ladekidde Substation POI. | 2020-06-04 | 2020-11-02 | 2020-12-22 |  | 624309 |  |  | 99 |  | 345 | 0.1 | 954 KCM ACSR "Cardinal" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42907629 (P15177004) (P15177013) | Stewart Rd. 345-kV Station: Expansion | Hidalgo/Hidalgo | Expand the Stewart Road 138-kV Station with two 345-kV autotransformers. Relocate the last spans of Stewart Rd.-Weslaco unit 138-kV line to make room for tie-lines to autotransformers. Install two spans of 138-kV to the new 345-kV yard. | 2020-06-04 | 2021-10-31 |  | 27945000 | 34282826 |  |  | 95 |  | 345 | [7 empty] | 47603 | PUCT Docket 47973 Approved on 02/14/2019 BPID P15177004 & P15177013 will be summed together for total final costs.
42918594 (P15177007) | North Edinburg 345-kV Station: Multiplexor & Metering | Hidalgo/Hidalgo | Install new SEL Icon multiplexer at North Edinburg 345-kV Station in conjunction with the Stewart Rd. Project. Install new meters at Stewart Road on Palmito 345-kV line. | 2020-10-31 | 2021-04-15 | 2021-12-03 |  | 489376 |  |  | 99 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
T10093344 (DP19X18C0) | Haisley 138-kV Substation: T-Station Assets | Sinton/San Patricio | Install one (1) 138-kV, 3000A circuit switcher and one (1) 138-kV wave trap. | 2020-07-06 | 2020-11-04 |  |  | 559673 |  |  | 35 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
T10161800 (DP19X14D0) | Dimmit 138-kV Substation: T-Station Assets | Carrizo Springs/Dimmit | Install new bus work off the #1 and #2 to tie back into LCRA at station fence line. Work with LCRA to protect high side transformer bus via relay protection. | 2021-01-11 | 2021-07-01 |  |  | 799872 |  |  | 25 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
T10053977 (DP20X08C0) | Sand Crab 138-kV Substation: T-Line Assets | Port Lavaca/Calhoun | Termiinate Union Carbide - Joslin 138-kV transmission line into new Sand Crab 138-kV Substation | 2021-01-19 | 2021-02-17 | 2021-03-09 |  | 628876 |  |  | 99 |  | 138 | 0.1 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.1 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
T10033471 (DP20X08D0) | Sand Crab 138-kV Substation: T-Station Assets | Port Lavaca/Calhoun | Install In & Out transmission bus work with two motor-operated switches and manual bus tie. Install two 3000A, 40kA circuit switchers, and two motor-operated switches for the transformers. Install wave traps. | 2020-07-04 | 2021-03-09 | 2021-04-15 |  | 1801040 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42963078 (DP19X06D0) | Dustdevil 138-kV Substation: T-Station Assets (AEP Texas) | Laredo/Webb | Install one (1) 138-kV circuit switcher and switch for bank #1. Install switch on second bus terminal for future transformer. | 2020-08-15 | 2020-12-15 |  |  | 1010995 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42961436 (P17043001) | Harlingen 69-kV SS: Terminal Equipment | Harlingen/Cameron | Add new termination point on the 138-kV side for Harlingen SS to Raymondville #2 line to be converted to 138-kV. Upgrade three (3) 69-kV breakers within the station. | 2020-08-03 | 2021-01-27 | 2021-05-25 |  | 2958723 |  |  | 99 | 69 | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
42961002 (P17043002) | Raymondville #1 69-kV Substation: Terminal Equipment | Raymondville/Willacy | Upgrade existing station from 69-kV to 138-kV in order to convert the newly rebuilt Harlingen SS to Raymondville #2 line to 138-kV. | 2020-08-03 | 2021-01-27 | 2021-02-12 |  | 2567418 |  |  | 99 | 69 | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
42854433 (P17043003) | Raymondville #2 69-kV Substation: Terminal Equipment | Raymondville/Willacy | Rebuild the 138-kV side of the station to a 6 breaker ring, which would convert the newly rebuilt Harlingen SS to Raymondville #2 line to 138kV. | 2020-08-03 | 2021-12-31 |  |  | 7557122 |  |  | 60 | 69 | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
42961010 (P17043005) | Harlingen #1 69-kV Substation: CB Replacement | Harlingen/Cameron | Replace five (5) 69-kV circuit breakers within existing station | 2020-08-03 | 2020-10-10 | 2020-10-15 |  | 1916201 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
43011496 (P17043008) | Raymondville #2 - Armstrong 69-kV T-Line: Retermination | Raymondville/Willacy | Move the Raymondville #2 to Armstrong transmission line to new termination points within the Raymondville #2 Substation. Convert to 138-kV. | 2021-09-15 | 2021-12-31 | 2021-05-14 |  | 947891 |  |  | 98 | 69 | 138 | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
43011764 (P17043010) | Raymondville #2 - Rio Hondo 69-kV T-Line: Retermination | Raymondville/Willacy | Move the Raymondville #2 to Rio Hondo line to new termination points within the Raymondville #2 Station. Convert to 138-kV. | 2021-09-15 | 2021-12-31 |  |  | 716972 |  |  | 0 | 69 | 138 | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42957957 (P18010001) | Chaparrosa 69-kV POD Box Bay: New Construction | Zavala | Construct a new 138-kV rated POD Box Bay. Install 3-3000A Motor-Operated Switches, metering, 2x2000 AAC jumpers & SCADA. Will be operated at 69-kV. | 2020-08-21 | 2021-02-03 | 2020-12-18 |  | 2700000 |  |  | 99 |  | 69 | [7 empty] | 16 TAC 25.83(a)(3) | Consent Obtained
42917340 (P18010002) | Chaparrosa 69-kV POD Box Bay: Cut-In | Zavala | Terminate the Turtle Creek to Uvalde 69-kV transmission line into the new Chaparrosa 69-kV POD Box Bay. | 2020-08-21 | 2021-02-03 | 2020-12-18 |  | 500000 |  |  | 99 | 69 |  | 0.08 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline |  | 100 | 0.08 | 16 TAC 25.101 (c)(5)(A) | Consent Obtained
42935602 (P18152001) | Lemay Permanent 138-kV Box Bay | La Salle | Construct a 3000A, 40kA, 138-kV Box Bay with Motor-Operated Switches. Install B2500 Cabinet, RTU, Metering, & SCADA. | 2020-09-03 | 2021-01-26 |  |  | 1670498 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Landowner Consent Obtained
42999071 (P18152004) | Lemay Permanent 138-kV Box Bay Cut-In | La Salle | Terminate the North Laredo to Reveille 138-kV transmission line into the new Lemay Box Bay. | 2020-09-03 | 2021-01-26 |  |  | 780835 |  |  | 0 | 138 |  | 0.04 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline |  | 100 | 0.04 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
T10066092 (P19197001) | Bonilla-El Trueno 345-kV Line: Install DE POI | Cameron | Construct one 0 degree Dead-End engineered steel pole structure on concrete pier Dead End Structure outside of Bonilla 345-kV Station and Terminate 345-kV El Trueno gen-tie line | 2019-09-05 | 2020-12-15 |  |  | 589449 |  |  | 0 | 345 |  | 0.01 | 954 KCM ACSR 54/7 "Cardinal" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP-owned property
T10054462 (P19197004) | Bonilla 345- kV Station | Cameron | Install two (2) 5000A, 50kA, 345-kV breakers, EPS metering, and verify SSO relay requirements are met | 2020-09-03 | 2021-04-30 |  |  | 6111144 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42801057 (A17024001) | Whitepoint - Dupont SW#1 138-kV: Raise Transmission Line | San Patricio | Replace four (4) lattice tower structures with monopoles and ACCC conductor to provide clearance over new TxDOT bridge (approx 0.35 mi) | 2020-09-10 | 2020-11-15 |  |  | 1551779 |  |  | 0 | 138 |  | 0.35 | 795 KCM ACCC "Drake" | Steel Mono Pole | 150 | 0.35 |  |  | 16 TAC 25.101 (c)(5)(F) | Landowners Noticed
42801062 (A17024003) | Whitepoint - Dupont SW#2 138-kV: Raise Transmission Line | San Patricio | Replace four (4) lattice tower structures with monopoles and ACCC conductor to provide clearance over new TxDOT bridge (approx 0.35 mi) | 2020-09-10 | 2020-11-15 |  |  | 1346541 |  |  | 0 | 138 |  | 0.35 | 795 KCM ACCC "Drake" | Steel Mono Pole | 150 | 0.35 |  |  | 16 TAC 25.101 (c)(5)(F) | Landowners Noticed
42801070 (A17024005) | Gregory - Aransas Pass 69-kV: Raise Transmission Line | San Patricio | Replace five (5) existing wood pole structures with monopoles to provide clearance over new TxDOT roadway (approx. 0.21 mi) | 2020-09-10 | 2020-11-15 | 2021-06-15 |  | 758680 |  |  | 99 | 69 |  | 0.21 | 336.4 KCM ACSR "Linnet" | Steel Mono Pole | 75 | 0.21 |  |  | 16 TAC 25.101 (c)(5)(F) | Landowners Noticed
T10065046 (DP20X01D0) | Chocolate Bayou 138-kV Substation: T-Station Assets | Victoria | Upgrade remote end relays & replace transmission RTU with a DM 61.01 | 2020-09-03 | 2021-03-26 |  |  | 785687 |  |  | 2 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10021421 (P18209008) | Angstrom - SDI 345-kV Transmission Line | San Patricio | Construct a new double-circuit 345-kV transmission line from Angstrom 345-kV Station (currently under construction) to the SDI Buffalo 345-kV Station to serve a new SDI steel plant. | 2020-08-03 | 2021-02-05 | 2021-02-25 | 4351000 | 4350047 |  |  | 99 |  | 345 | 1.72 | 2 - 954 ACSR "Cardinal" | Steel Mono Pole |  |  | 150 | 0.86 | 50726 | PUCT Docket 50726 Approved on 07/17/2020.
42651938 (A16002037) | South Padre Island - Sunchase 138-kV Rebuild | South Padre Island/Cameron | Rebuild and reconductor the South Padre Island to Sunchase 138-kV transmission line. | 2020-09-20 | 2021-02-28 |  |  | 16000000 |  |  | 80 | 138 |  | 3.61 | 795 KCM ACSS "Drake" | Steel Monopole | Varies | 3.61 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed Supplemental easements acquired as necessary
43011781 (P18187001) | Aransas Pass - Sea Wall 69-kV Rebuild | Aransas Pass/ San Patricio | Rebuild and reconductor the Aransas Pass to Sea Wall 69-kV transmission line to 138-kV standards. Will continue to operate at 69-kV, | 2020-10-15 | 2021-05-15 | 2021-05-12 |  | 15000000 |  |  | 99 | 69 |  | 3.2 | 795 ACSR "Drake" | Steel Mono Pole | Centerline | 3.2 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
42998404 (P18048001) | Esperanza 138-kV Substation: Construction | Matagorda | Construct a new 138-kV 3-breaker ring bus station with DICM and associated equipment. | 2020-10-04 | 2021-01-25 | 2021-03-31 |  | 6046000 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Landowner Consent Obtained
T10150180 (P18048010) | Esperanza 138-kV Substation: Capacitor Banks | Matagorda | Install two (2) 28.8 MVAR Capacitor banks and associated breakers in the new Esperanza 138-kV Substation in conjunction with BPID P18048001. | 2020-10-04 | 2021-01-25 | 2021-04-06 |  | 1330000 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
42997581 (P18048003) | Celanese 138-kV Substation Fiber Panel | Matagorda | Update relaying and install Telecom panel to terminate fiber. | 2020-10-04 | 2021-04-11 |  |  | 360000 |  |  | 50 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
43018271 (P18048009) | Celanese 138-kV Subtation: Upgrades | Matagorda | Install DICM, Line Relaying, and Breaker Control Panels. | 2020-10-04 | 2021-04-11 |  |  | 2660000 |  |  | 50 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42983324 (P19034008) | Las Lomas Wind Interconnection: Falcon SW 138-kV Substation | Starr | Upgrade Remote End Relay Settings | 2020-10-15 | 2020-10-26 |  |  | 717342 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42983322 (P19034003) | Las Lomas Wind Interconnection: Zapata 138-kV Substation | Zapata | Upgrade Remote End Relay Settings | 2020-10-04 | 2020-11-02 | 2020-11-05 |  | 641464 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10097942 (P17043004) | Harlingen SS - Raymondville #2 69-kV T-Line: Reterminations | Raymondville / Willacy | Terminate the existing 69-kV transmission line to the new termination points at the Harlingen Switching, Raymondville #1, and Raymondville #2 Stations to convert the line from 69-kV to 138-kV. | 2021-10-05 | 2021-02-25 | 2021-02-17 |  | 1433305 |  |  | 90 | 69 | 138 | 0.25 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.25 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
T10015124 (P19164001) | Hecker - Whitepoint Ckt. #1 138-kV Line | San Patricio | Reconductor the Hecker to Whitepoint Ckt. #1 transmission line. Some lattice structures may require replacement | 10\20\2020 | 2022-01-30 |  |  | 4123423 |  |  | 0 | 138 |  | 5.61 | 795 KCM ACSS "Drake" | Steel Lattice Structures | Various | 5.61 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
T10060886 (P19164008) | Hecker - Whitepoint Ckt. #2 138-kV Line | San Patricio | Reconductor the Hecker to Whitepoint Ckt. #2 transmission line | 2020-10-20 | 2022-01-30 |  |  | 3321827 |  |  | 0 | 138 |  | 5.61 | 795 KCM ACSS "Drake" |  | Various | 5.61 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
T10053550 (P19164005) | Whitepoint 138-kV Switching Station | San Patricio | Reterminate jumpers and update relay settings | 2021-12-21 | 2022-01-30 |  |  | 322668 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10142154 (P20068003) | Lon Hill- Goddard 345-kV Line: Cut-In | San Patricio | Terminate the Lon Hill to Goddard 345-kV line into the new Katoen 345-kV Substation. | 2020-12-01 | 2021-10-15 |  |  | 2434423 |  |  | 79 | 345 |  | 0.2 | 795 ACSR "Drake" | Steel DE Structure |  |  | 150 | 0.2 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
T10139820 (P20068005) | Katoen - El Algodon 345-kV Line Extension | San Patricio | Construct a 345-kV span with DE Structure to Generator (El Algodon Alto Wind Farm, LLC) Point of Interconnect (POI) | 2020-12-01 | 2021-10-15 |  |  | 772614 |  |  | 79 |  | 345 | 0.04 | 795 ACSR "Drake" | Steel DE Structure |  |  | 150 | 0.04 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
T10139816 (P20068002) | Katoen 345-kV Substation | San Patricio | Construct a new 345 kV three-breaker ring bus Katoen Substation with two 345-kV rungs for line terminations with appropriate relays. Install three 345-kV, 50 kA, 3000 A breakers & EPS Metering for the El Algodon terminal. Install SSO relaying in monitoring mode for the El Algodon terminal | 2020-12-01 | 2021-10-15 |  |  | 14092089 |  |  | 79 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
42906744 (P18022010) | Los Fresnos 138-kV Substation: Add Metering | Los Fresnos/Cameron | Install metering equipment and CCVTs for Transmission interconnect metering, loss compensated toward Sharyland Stillman station | 2020-11-29 | 2021-04-12 | 2021-04-22 |  | 624058 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42899057 (P18022004) | Union Carbide 138-kV Substation | Brownsville/Cameron | Install new relays and MUX at Union Carbide 138-kV Substation | 2020-12-02 | 2021-04-12 |  |  | 865428 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42919629 (P18186001) | Rayos Del Sol Solar Interconnection: Luna 138-kV Substation T-Line Cut-In | Cameron | Terminate the Weslaco to Rangerville 138-kV transmission line into the new Luna 138-kV Substation. | 2020-11-03 | 2021-03-31 | 2021-06-08 |  | 565601 |  |  | 99 |  | 138 | 0.12 | 795 ACSR "Drake" | Steel Single Pole Deadend / Wood 3-Pole Guyed Deadend |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42977751 (P18186003) | Rayos Del Sol Solar Interconnection: Luna to Astros138-kV Line Span | Cameron | Construct a new 138-kV tie line between Luna 138-kV Substation and Generator's Astros 138-kV Collector Station. | 2020-11-03 | 2021-03-31 | 2021-06-08 |  | 425654 |  |  | 99 |  | 138 | 0.1 | 795 ACSR "Drake" | Steel Single Pole Deadend |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42960644 (A19447013) | Equistar 138-kV Substation: Meter Modernization | Corpus Christi/Nueces | Replace existing CTs with metering combo for both XFMR#1 & 2 | 2020-11-03 | 2021-01-25 | 2021-05-18 |  | 757755 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within customer station property
42729418 (P14131004) | Uvalde 69-kV Substation | Uvalde/Uvalde | Replace 69-kv breaker and associated switches and bus work. | 2020-12-01 | 2021-05-01 |  |  | 1516561.9 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10080057 (DR20X04D0) | Black Cat 138-kV Substation: T-Station Assets | Bay City/Matagorda | Construct 138KV In & Out capable bus with manual bus tie switch for double bank station. Install one 138-kV (3000A 40 kA) Circuit switcher, and all associated material. Install two 138-kV MOABs for the line terminals. Install switch on second bus terminal for future transformer. Install wave trap on line. | 2020-12-01 | 2021-05-14 | 2021-05-14 |  | 1420254 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42993359 (P19164002) | Whitepoint SS-Rincon 138-kV Line: Rebuild | San Patricio | Rebuild and reconductor a 4.59 mile portion of the Whitepoint SS to Rincon 138-kV transmission line. Reconductor the remaining 3.15 miles that are already on double-circuit structures. | 2020-11-10 | 2022-01-30 |  |  | 9099925 |  |  | 0 |  | 138 | 7.74 | 795 KCM ACSS "Drake" | Steel Pole Mono | 100 | 7.74 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed. Consent and new easements & supplements were acquired as necessary.
43018270 (P18048008) | Blessing - Celanese 138-kV T-Line: Cut-In | Matagorda | Terminate the Blessing - Celanese 138-kV transmission line into the new Esperanza 138-kV Substation with double-circuit construction. | 2020-11-14 | 2021-01-25 | 2021-03-31 |  | 2350000 |  |  | 99 |  | 138 | 1.38 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 75 | 0.69 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
43010991 (P17019002) | Resnik 138-kV Substation | San Patricio | Construct a new four-rung breaker and a half 138-kV substation expandable to six rungs | 2020-11-19 | 2022-01-30 |  |  | 13809441 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3)
T10007790 (P17019006) | Resnik North 138-kV Cut-In | San Patricio | Terminate the Resnik North 138-kV transmission line into the new Resnik 138-kV Substation | 2021-10-01 | 2022-01-30 |  |  | 668638 |  |  | 0 |  | 138 | 0.04 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10015001 (P17019007) | Resnik South 138-kV Cut-In | San Patricio | Terminate the Resnik South 138-kV transmission line into the new Resnik 138-kV Substation | 2021-10-01 | 2022-01-30 |  |  | 674416 |  |  | 0 |  | 138 | 0.04 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42901165 (P18022001) | La Palma-PUB Loma Alta 138-kV T-Line: Retermination | San Benito/Cameron | Reterminate the La Palma to PUB Loma Alta 138-kV transmission line into new Stillman 138-kV Station | 2021-01-10 | 2021-03-03 |  |  | 1603634 |  |  | 50 | 138 |  | 0.1 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Land Owner Consent Obtained
42902323 (P18022002) | Union Carbide-PUB Loma Alta 138-kV T-Line: Retermination | San Benito/Cameron | Reterminate the Union Carbide to PUB Loma Alta 138-kV transmission line into Stillman Station, include OPGW reroute | 2021-01-10 | 2021-03-03 |  |  | 1309256 |  |  | 40 | 138 |  | 0.21 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Land Owner Consent Obtained
T10075090 (P19219002) | Whitepoint 345-kV Station: Add 2nd Auto | San Patricio | Expand existing 345-kV to a four-breaker ring, add second 345/138kV Auto, and add a new rung to the 138kV to connect to the Auto. | 2021-01-04 | 2022-01-30 |  |  | 17678000 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Property Purchased
T10171059 (P19219005) | Pelican-Whitepoint 138-kV Relocate | San Patricio | Relocate and reterminate the Pelican-Whitepoint 138-kV line for 2nd Auto addition | 2021-01-04 | 2022-01-30 |  |  | 2242000 |  |  | 0 | 138 |  | 0.04 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10171135 (P19219006) | Nueces-Whitepoint 138-kV Relocate | San Patricio | Relocate and reterminate Nueces-Whitepoint 138-kV line for 2nd Auto addition | 2021-01-04 | 2022-01-30 |  |  | 1772000 |  |  | 0 | 138 |  | 0.04 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
42807101 (A17961001) | Kleberg - Loyola 138-kV Relocation | Kingsville/Kleberg | Relocate 12 structures of the 138-kV line adjacent to US 77 due to TxDOT widening the highway and rebuilding a bridge near FM 1717 just south of Kingsville, TX. | 2021-01-04 | 2021-04-01 | 2021-05-04 |  | 3377565 |  |  | 99 | 138 |  | 1.38 | 795 KCM ACSS "Drake" | Steel Mono Pole / Steel 3 Pole Dead-End | Centerline | 1.38 | 100 | 1.38 | 16 TAC 25.101 (c)(5)(F) | Project is 100% Reimburseable from TxDOT. Landowner supplemental easements obtained as necessary.
42983135 (P18043001) | Dilley - Charlotte 69-kV Rebuild | Dilley/Frio Charlotte/Atascosa | Rebuild and reconductor the Dilley to Charlotte 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2021-02-01 | 2022-04-11 |  |  | 26260304 |  |  | 45 | 69 |  | 34.34 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 34.34 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
T10224569 (P20195001) | Dupont 138-kV Switching Station: New Generator | San Patricio | Dupont 138-kV Switching Station: Connect new Generator into Station updating relaying, SCADA and metering. | 2021-05-24 | 2021-07-06 |  |  | 307819 |  |  | 25 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42978694 (P18186007) | Rayos Del Sol Solar Interconnection: Luna 138-kV Extension | Cameron | The Luna 138-kV Extension project is being constructed to tie the new Luna Substation into the existing La Palma – Wesmer 138-kV transmission line located in Rangerville, TX. This project involves installing approximately four (4) structures to the South and East of the proposed Luna Substation. | 2021-02-01 | 2021-04-27 | 2021-06-08 |  | 1090316 |  |  | 99 |  | 138 | 0.6 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.1 | 16 TAC 25.101 (c)(5)(A) | Exclusive Easement Obtained
T10180550 (P20106001) | Vancourt Solar Interconnection: Luna - Vancourt 138-kV Line Span | Cameron | Construct a new 138-kV tie line between Luna 138-kV Substation and Vancourt Solar's POI. | 2021-02-01 | 2021-04-27 |  |  | 615073 |  |  | 98 |  | 138 | 0.1 | 795 KCM ACSR "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10172911 (P20106002) | Vancourt Solar Interconnection: 138-kV Terminal | Cameron | Install station terminal at new Luna 138-kV Substation for Vancourt Solar Interconnection. Install one (1) 138-kV, 40kA, 3000A breaker, install relays and EPS Metering. | 2021-02-01 | 2021-04-27 |  |  | 1167629 |  |  | 98 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T101654020 (P20095002) | Bigfoot - Moore (STEC) 138-kV Rebuild | Frio | Rebuild and reconductor the Bigfoot to Moore (STEC) 138-kV transmission line to 138-kV standards. | 2021-02-10 | 2021-05-04 |  |  | 9945311 |  |  | 0 | 138 |  | 6.08 | 795 KCM ACSS "Drake" | Concrete Mono Pole | Varies | 6.08 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42937639 (P18027001) (P18027002) | Dolan Creek 138-kV POD Box Bay | Val Verde | Construct a 138-kV POD Box Bay (3000A ratings for all equipment) on center of the Transmission Line ROW. Install 138-kV revenue metering on the Box Bay. Install wave trap to control Carrier signal bleed by the tap load. | 2021-02-11 | 2021-05-15 |  |  | 1896733 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Exclusive Easement Obtained
42937666 (P18027004) (P18027003) | Maxwell - Sonora 138-kV T-Line: Cut-In | Val Verde | Terminate the existing Maxwell to Sonora 138-kV transmission into new Dolan Creek 138-kV POD Box Bay. | 2021-02-11 | 2021-05-15 |  |  | 1657836 |  |  | 0 | 138 |  | 0.36 | 477 KCM ACSR | Steel Mono Pole |  |  | 100 | 0.36 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
T10165411 (P20095003) | Big Foot 138-kV Switching Station | Frio | Upgrade jumpers to Moore line terminal to a minimum of 2000A. Upgrade any limiting elements on the Moore terminal to a minimum of 2000A. Upgrade relays and settings as necessary. Coordinate remote end settings at Moore with STEC | 2021-04-01 | 2021-10-15 |  |  | 295964 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10148046 (A20059001) | Lon Hill 345-kV Substation: RFL Comm | Corpus Christi/Nueces | Add fiber from ATT to control house, replace old and install new 2411 relay equipment, add 120ac power to ATT interconnect box.D197 | 2021-03-06 | 2021-03-30 |  |  | 274000 |  |  | 95 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10148109 (A20059003) | Westside 138-kV Switching Station: RFL Comm | Corpus Christi/Nueces | Add fiber from ATT to control house, replace old and install new 2411 relay equipment, add 120ac power to ATT interconnect box.D197 | 2021-03-06 | 2021-03-30 |  |  | 232000 |  |  | 95 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10148117 (A20059004) | McKenzie Rd. 138-kV Substation: RFL Comm | Corpus Christi/Nueces | Add fiber from ATT to control house, replace old and install new 2411 relay equipment, add 120ac power to ATT interconnect box.D197 | 2021-03-06 | 2021-03-30 |  |  | 256000 |  |  | 95 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10210657 (A19372013) | Rachal-North Edinburg 138-kV Line | Hidalgo,Brooks | Telecom Modernization Program: Install 40.7 miles of 96 count ADSS fiber via Transmission between North EdinburgStation and Rachal Station. For connectivity at North Edinburg Station, Red Gate Station, and Rachal Station tosupport ICON MUX. | 2021-07-05 | 2021-10-15 |  |  | 1937290 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
T10107252 (A19376059) | La Quinta 138-kV Substation | Webb | Telecom Modernization Program: Install 0.2 miles of 48 ct ADSS fiber via underground between La Quinta TS and La QuintaTelecom Shelter. For connectivity at La Quinta TS Telecom Shelter to support DWDM and CES. | 2021-02-15 | 2021-05-24 |  |  | 270592 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10107253 (A19376060) | Zapata 138-kV Substation | Zapata | Telecom Modernization Program: Install 0.2 miles of 48 ct ADSS fiber via underground between Zapata TS and Zapata Telecom Shelter. For connectivity at Zapata TS Telecom Shelter to support DWDM and CES. | 2021-04-19 | 2021-07-22 |  |  | 270592 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10107260 (A19376068) | Uvalde 138-kV Substation | Uvalde/Uvalde | Telecom Modernization Program: Install 2.7 miles of 48 ct ADSS fiber via distribution from Uvalde Telecom Shelter to existing fiber on the Turtle Creek - Uvalde 69-kV Circuit. For connectivity at Uvalde Telecom Shelter to support DWDM. | 2021-04-05 | 2021-06-29 |  |  | 253852 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10094875 (A19376069) | Kenedy 138-kV Substation | Kenedy/Karnes | Telecom Modernization Program: Install 0.2 miles of 48 ct ADSS fiber via underground between Kenedy SW Station and Kenedy SW Telecom Shelter. For connectivity at Kenedy SW Telecom Shelter to support DWDM and CES. | 2021-04-05 | 2021-09-29 |  |  | 270592 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
43018215 (P17019004) | DuPont-McCampbell North 138-kV Cut-In | San Patricio | Terminate the DuPont-McCampbell North 138-kV transmission line into the new Resnik 138-kV Substation | 2021-04-06 | 2022-01-30 |  |  | 2438743 |  |  | 0 | 138 |  | 0.5 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  | 200 | 0.5 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
43018234 (P17019005) | DuPont-McCampbell South 138-kV Cut-In | San Patricio | Terminate the DuPont-McCampbell South 138-kV transmission line into the new Resnik 138-kV Substation | 2021-04-06 | 2022-01-30 |  |  | 1703102 |  |  | 0 | 138 |  | 0.25 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  | 200 | 0.25 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
T10015019 (P17019015) | DuPont-Hecker 138-kV Cut-In | San Patricio | Terminate the DuPont-Hecker 138-kV transmission line into the new Resnik 138-kV Substation | 2021-04-06 | 2022-01-30 |  |  | 1975967 |  |  | 0 | 138 |  | 0.25 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  | 200 | 0.25 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
T10180506 (P20080002) | Tango 345-kV Station: Build Tango 345-kV Station | Bee | Build new 345-kV Tango station to cut into the Goddard - (STEC) Pawnee line to enable customer generation interconnect. | 2021-04-26 | 2022-02-16 |  |  | 13400000 |  |  | 0 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
T10207014 (P20136001) | Tango 345-kV Station: Install Terminal | Bee | Install 345 kV terminal, one (1) 345 kV, 50 kA, 3000 A breaker, EPS metering for Sparta terminal, & SSO relaying in monitoring mode for Sparta terminal. | 2021-04-26 | 2022-02-16 |  |  | 2400000 |  |  | 0 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
T10238591 (P20080003) | Goddard 345-kV Station: Upgrades | Bee | Make upgrades and modifications in Goddard station to support the new Tango station. | 2021-10-26 | 2022-01-21 |  |  | 330000 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10238629 (P20080004) | Tango - Foxtrot 345-kV T-Line: Span Outside Tango | Bee | Construct 0.10 mile span of 345-kV T-Line to Foxtrot Wind Interconnection | 2021-11-01 | 2022-01-06 |  |  | 900000 |  |  | 0 |  | 345 | 0.1 | 795 KCM ACSR "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10177955 (P20080006) | Goddard - (STEC) Pawnee 345-kV T-Line: Cut-In | Bee | Terminate the Goddard to Pawnee (STEC) 345-kV transmission line into the new Foxtrot 345-kV Substation. | 2021-11-01 | 2022-01-21 |  |  | 2600000 |  |  | 0 | 345 |  | 0.2 | 795 KCM ACSR "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10207016 (P20136003) | Tango - Sparta 345-kV T-Line: Build Span | Bee | Construct 0.10 mile span of 345-kV T-Line to Sparta Solar Interconnection | 2021-11-01 | 2021-12-31 |  |  | 1900000 |  |  | 0 |  | 345 | 0.1 | 795 KCM ACSR "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10261470 (A20141001) (A20141002) | Falfurrias - Rachal 138-kV T-Line | Falfurrias/Brooks | Modify existing mono pole davit arms to braced post construction. | 2021-10-04 | 2021-12-15 |  |  | 3748680 |  |  | 0 | 138 |  | 25.18 | 795 ACSR "Drake" | Steel Mono Pole | Centerline | 25.18 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners noticed
T10261473 (A20141003) (A20141004) | Rachal - N. Edinburg 138-kV T-Line | Edinburg/Hidalgo | Modify existing mono pole davit arms to braced post construction. | 2021-07-05 | 2021-08-31 |  |  | 5845320 |  |  | 0 | 138 |  | 39.78 | 795 ACSR "Drake" | Steel Mono Pole | Centerline | 39.78 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners noticed
42651786a (A16002193) | Causeway - Sunchase 138-kV Rebuild | South Padre Island/Cameron | Rebuild and reconductor the Causeway to Sunchase 138-kV transmission line. | 2021-04-08 | 2021-10-30 |  |  | 21000000 |  |  | 0 | 138 |  | 3.21 | 795 KCM ACSS "Drake" | Steel Monopole | Varies | 3.21 |  |  | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.101 (c)(5)E | Landowners Noticed. Landowner Consent obtained as needed.
43018170 (P19166001) (P19166002) | Port Aransas - Seawall 69-kV UG Sea Cables | Port Aransas /Nueces | Replace 0.48 miles of Undersea Cables and Conduit. | 2021-04-10 | 2021-07-31 |  |  | 19843136 |  |  | 75 | 69 |  | 0.48 | 795KCM ACSS/AW bundle of 7 cables and ACSS | Undersea Cables |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Landowner Consent Obtained
T10082775 (DR20X04C0) | Black Cat 138-kV Substation: T-Line Assets | Bay City / Matagorda | Terminate the Bay City to Conoco 138-kV transmission line into the new Black Cat 138-kV Substation. | 2021-04-19 | 2021-05-14 | 2021-05-14 |  | 1192214 |  |  | 99 | 138 |  | 0.02 | 795 ACSS "Drake" | Steel DE Structures |  |  | 100 | 0.02 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
T10127143 (P19289001) (P19289003) (P19289006) | Blessing - Markham Tap 69-kV Line | Markham/Matagorda | Rebuild and reconductor the Blessing to Markham Tap 69-kV transmission line to 138-kV standards. Will continue to operate at 69-kV. | 2021-06-17 | 2021-11-15 |  |  | 14867318 |  |  | 0 | 69 |  | 10.75 | 795 ACSR "Drake" | Steel Monopole | Centerline | 10.75 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
T10125915 (P19289004) | Blessing 69-kV Substation: Upgrade Terminal | Matagorda | Upgrade 69-kV terminal to 2000 A, 40 kA & Update relay settings at Blessing 69-kV Substation | 2021-06-21 | 2021-11-15 |  |  | 436516 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10126264 (P19289005) | Markham 69-kV Substation: Upgrade Thru Path | Markham/Matagorda | Upgrade thru-path to 2000 A, 40 kA at Markham 69-kV Substation | 2021-08-23 | 2021-11-15 |  |  | 153992 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10281928 (A20132008) | Lopeno 138-kV Substation | Zapata | Installing Physical Security to DICM, Telecom Network Splitting, RTAC (Station Data Repository) updates, and Firmware Upgrades. | 2021-08-02 | 2021-10-01 |  |  | 252719 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10281949 (A20132011) | N. Edinburg 138-kV Substation | Hidalgo | Installing Physical Security to DICM, Telecom Network Splitting, RTAC (Station Data Repository) updates, and Firmware Upgrades. | 2021-07-19 | 2021-08-24 |  |  | 278593 |  |  | 20 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10281961 (A20132014) | Raymondville #2 138-kV Substation | Willacy | Installing Physical Security to DICM, Telecom Network Splitting, RTAC (Station Data Repository) updates, and Firmware Upgrades. | 2021-07-26 | 2021-09-10 |  |  | 274096 |  |  | 20 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10214754 (P19312001) | Joslin 138-kV Substation: Install Terminal | Point Comfort/Calhoun | Construct new 138-kV rung with double breakers for existing Dupont lines. Install a new 138-kV breaker on the existing Dupont terminal. Install EPS metering on the terminal for Tres Bahias. Update relaying as necessary to accommodate the new line terminations at the Joslin 138-kV Substation | 2021-07-19 | 2022-02-22 |  |  | 1495265 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within AEP owned property
T10221296 (P19312002) | Joslin-Tres Bahias 138-kV Line: Install Span | Point Comfort/Calhoun | Install Interconnect deadend structure and one span of 138-kV transmission line into Joslin 138-kV Substation | 2021-07-19 | 2022-02-22 |  |  | 528715 |  |  | 0 | 138 |  | 0.04 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP owned property
T10214757 (P19312004) | Joslin-Dupont 138-kV Line: Reterminate Line | Point Comfort/Calhoun | Reterminate the existing Joslin to Dupont 138-kV transmisison line to new rung | 2021-10-12 | 2021-11-02 |  |  | 256334 |  |  | 0 | 138 |  | 0.04 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP owned property
T10221314 (P19312006) | Joslin-Formosa 138-kV Line: Reterminate Line | Point Comfort/Calhoun | Reterminate the existing Joslin to Formosa 138-kV transmisison line to new rung | 2021-12-17 | 2022-01-20 |  |  | 324879 |  |  | 0 | 138 |  | 0.04 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP owned property
T10189306 (P19011001) | Brightside 69-kV Temporary Tap: Metering | Live Oak | Install metering & RTU for Brightside Solar Farm | 2021-06-04 | 2020-12-24 |  |  | 630521 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Solar Farm owned property
T10190061 (P19011002) | Charter-Brightside 69-kV Temporary Tap | Live Oak | Install temporary tap along the Three Rivers to Beeville 69-kV transmission line to serve Brightside Solar Farm | 2021-06-04 | 2020-12-24 |  |  | 1679657 |  |  | 0 | 69 |  | 0.25 | 4/0 ACSR 6/1 "Penguin" | Steel Pole Mono |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Solar Farm owned property
42907529 (A18044001) | Garza 69-kV Substation | Starr | Install DICM, replace obsolete breakers & relays, & replace RTU & Metering, | 2021-07-30 | 2022-04-19 |  |  | 6264892 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Staion Property
T10057021 (P18043002) (P18043004) | Charlotte-Jourdanton 69-kV Rebuild | Charlotte,Jourdanton /Atascosa | Rebuild and reconductor the Charlotte to Jourdanton 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2021-10-25 | 2022-08-29 |  |  | 17087761 |  |  | 3 | 69 |  | 10.33 | 795 KCM ACCS "Drake" | Steel Mono Pole | Centerline | 10.33 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners noticed.
42994625 (A18018024) | Berclair 69-kV Substation | Bee | Expand existing Berclair 6-kV Substation on existing property, install new box bay structure and communication cabinets, build new station bus to connect to existing distribution transformers. | 2021-08-02 | 2022-03-31 |  |  | 2383987 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42651786b (A16002193) | Causeway - Sunchase 138-kV Rebuild (Channel Crossing) | South Padre Island/Cameron | Relocate, rebuild and reconductor the 0.13 mile channel crossing portion of the Causeway to Sunchase 138-kV transmission line. | 2021-08-02 | 2021-12-31 |  |  | 5500000 |  |  | 0 | 138 |  | 0.17 | 795 KCM ACSS "Drake" | Steel Monopole | Centerline | 0.13 | 100 | 0.17 | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.101 (c)(5)(E) | Utilizing Existing Easement Landowners Noticed Landowner Consent obtained as needed.
42898119 (A20217009) | Rangerville 138-kV Substation: RTU Reliability | San Benito/Cameron | Rangerville RTU Reliability - Replace existing IBOX RTUs with new Cooper RTUs | 2021-09-01 | 2021-10-01 |  |  | 292515 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
42757771 (A1704417) | Fulton 69-kV Substation: Hurricane Storm Recovery | Aransas | Rebuild damaged portions of the Fulton 69-kV Substation following Hurricane Harvey. | 2018-01-11 | 2021-05-06 | 2021-05-06 |  | 412430 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.101(c)(3) | Emergency Project (Hurricane Harvey Storm Damage)
T10131836 (P20026001) | Rio Hondo 345/138-kV Switching Station | Cameron | Update E. Rio Hondo terminal to meet 2000A requirement. Replacing jumpers with double 1272 and updating breaker switches to 2000A switches. | 2021-10-04 | 2021-11-17 |  |  | 396000 |  |  | 0 | 345/138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10244830 (P20209001) | Roma Tap 138-kV Station: Install Terminal | Starr | Construct a new 138 kV breaker terminal at the Roma Tap 138-kV station.Install EPS metering at the new 138 kV breaker terminal for the generator. | 2021-10-15 | 2021-04-28 |  |  | 1123544 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
T10244834 (P20209003) | Roma Tap to Starr Solar POI: 138-kV Span | Starr | Construct one 138-kV span from the new breaker terminal at Roma Tap to the POI structure just outside the station fence. | 2021-10-15 | 2021-04-28 |  |  | 362002 |  |  | 0 | 138 |  | 0.17 | 795 KCM ACSS "Drake" | Steel Monopole | Centerline | 0.13 | 100 | 0.17 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained