## MonthlyReportForm
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
TL101 | Rio Grande to Sunset 69kV and Rio Grande to Sunset North 115kV transmission lines rebuild and reconductoring. | El Paso, El Paso | Rebuild two 69kV lines from Rio Grande to Sunset, and one 115kV line from Rio Grande to Sunset North, by upgrading the conductor and replacing existing wooden poles with one double-circuit and one single-circuit steel monopole line. One line will carry a 69kV line. The second line will carry a 69kV line and a 115kV double-bundle line. | 2019-07-31 |  |  | 22888944 | 22888944 |  |  | 20% | 69 & 115 | n/a | 5.24-115kV & 10.04 -69KV | 69kV lines replace 336 and 556 ACSR single bundle conductor with 954 ACSR single bundle and replace the 115kV - 556 ACSR double bundle conductor with 954 ASCR double bundle | All steel structures varying between 75' to 120' in height; single circuit tangent structures, double circuit tangent monopoles, and drill pier foundation dead end | 50'-100' | 4.32-115kV & 9.12-69kV | n/a | n/a | 25.101(c)(5)(B)
TL106 | Wrangler to Sparks rebuild and reconductor | El Paso, El Paso | Rebuild a portion of the 115kV transmission line by replacing structures, upgrading the conductor, and adding optical ground wire. | 2020-12-15 | 2021-03-30 | 2021-03-31 | 1911367 | 3140272 |  |  | 100% | 115 | n/a |  | Replace 336 single bundle with 954 ACSR single bundle | 85' to 100' steel monopoles | TxDOT ROW | 2.66 | n/a | n/a | 25.101(c)(5)(B) | Communication (overhead fiber) portion of the project pending completion.
TS117 | Butterfield to Newman 115kV extend transmission service to a new Fort Bliss Military Reservation substation | El Paso, El Paso | 115kV in and out tap to service a new, North Bliss substation, inside the military reservation and install optical ground wire from Butterfield to North Bliss substations | 2020-09-17 |  |  | 450685 | 450685 |  |  | 92% | 115 | n/a | 0.42 | Replace 556 ACSR singlebundle with 954 ACSR single bundle for the new portion into North sub | 75' steel monopoles and 100' steel double circuit monopoles | 25 | 0.47 | 60 | 0.21 | 25.101(c)(5)(F) & 25.101(c)(5)(A) | Tap into North Sub completed. Fiber from Butterfield to the tap pending outage approval from System Operations and coordination with TxDOT.
TL244 | Pine-to-Seabeck 115-KV Transmission Line | El Paso, El Paso | Construction and operation of a new 115kV transmission line from Pine Substation to Seabeck Substation | 2024-02-01 |  |  | TBD by final order |  |  |  |  | n/a | 115 | TBD by final order | 954 ACSR rail, single circuit | 95' - 110' delta or vertical steel monopole, self-support or on drilled pier foundations | n/a | n/a | 150 | TBD | 51476
TL245 | Seabeck-to-San Felipe 115-KV Transmission Line | El Paso, El Paso | Construction and operation of a new 115kV transmission line from Seabeck Substation to San Flipe Substation | 2024-02-01 |  |  | TBD by final order |  |  |  |  | n/a | 115 | TBD by final order | 954 ACSR rail, single circuit | 95' - 110' delta or vertical steel monopole, self-support or on drilled pier foundations | n/a | n/a | 150 | TBD | 51480
TL297 | Dallas Sub Rebuild | El Paso, El Paso | Due to age, needed transformer replacements, and flooding, Dallas Substation will be completely rebuilt. The rebuild will require portions of the 5800-Ascarate to Dallas and 7600-Dallas to Santa Fe transmission lines to be raised and adjusted to accommodate the new substation transformers arrangement. | 2021-09-07 |  |  | 542520 |  |  |  |  | 69kV | n/a | 0.06 Ascarate to Dallas; 0.06 Dallas to Santa Fe | Upgrade both to 954 ACSR Rail single bundle from 556 single bundle | The adjustments to the 5800-Ascarate to Dallas line will require installing one 80’ dead-end structure and one 95’ tangent structure; and the adjustments to the 7600-Dallas to Santa Fe line will require two 85’ tangents. Both lines will share two 80’ dead-end structures. One 80’ temporary dead-end structure will be installed to tie the Ascarate to Dallas line into the temporary substation. | Street ROW | 0.06 Ascarate to Dallas; 0.06 Dallas to Santa Fe | n/a | n/a | 25.101(c)(5)(B)(i)
TL299 | 18900 Trowbridge to Marlow 115kV transmission rebuild | El Paso, El Paso | To meet required system load, a larger conductor needs to be installed on the 115kV line and replace the wood poles with steel structures to be able to carry the weight of the new conductor. | 2021-10-18 |  |  | 552493 |  |  |  |  | 115 |  | 1.16 | Replace the 556 ACSR single bundle with 954 ACSR Rail single bundle | 75' dead end self suport steel structures on foundations and 70'-90 steel tangent monopoles | 50 & 100 | 1.16 | 50 | 0.08 | 25.101(c)(5)(B)(ii) | EPE and Marathon have agreed on a new location for a portion of the transmission line to accommodate the upgrades to Marlow Substation. Landowners were notified on 9/2/2021. Affidavit is attached.
TL294 | 12800 Newman to Chaparral 115kV Transmission Line Upgrades | El Paso, El Paso | As required under a Transmission Service Agreement entered into by EPE and TEP, upgrade the transmission line from single bundle to double bundle. It will require adjustments to the Newman to Anthony 115kV, Newman to Picante 115kV, and Newman to Picante 345kV lines to maintain the appropriate clearance from or under the line. Distance in Texas is 1.22 miles and NM is 1.66 miles. | 2022-01-10 |  |  | 2508724 |  |  |  |  | 115 | n/a | 2.88 | Replace the 556 ACSR single bundle with 954 ACSR Rail double bundle | 70' to 120' steel tangent monopoles or H-frames and dead end structures | 100 & 150 | 2.88 | n/a | n/a | 25.101(c)(5)(B)
Note on H1: Author: Please enter only a single integer, if possible.
Note on I1: Author: Please enter only a single integer, if possible.
Note on M1: Author: If applicable.
Note on N1: Author: If applicable.