## MonthlyReportForm-ETT
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
ETT-142 P15153001 | Falfurrias 69-kV SVC | Brooks | Replace DSTATCOM with Static VAR Compensator (SVC) and install bus tie to SVC | 2016-11-29 | 2019-05-31 | 2019-12-19 |  | 19066707 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Corrected Voltage
ETT-140 ETT800211 | Oklaunion Substation | Wilbarger | Replace 138-kV and 345-kV breakers and switches | 2017-10-06 | 2017-12-31 | 2018-12-14 |  | 10440000 |  |  | 99 | 345 / 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-139 ET1600803 | Maplewood Interconnection: Add 2nd Circuit to serve Red Barn IPP-Owned Station | Pecos | Add new 345-kV transmission line circuit from the LCRA TSC Bakersfield Station to the point of interconnection at Red Barn | 2018-04-09 | 2020-04-24 | 2021-01-26 | 2401000 | 2270000 |  |  | 99 |  | 345 | 1.94 | 2-bundled Cardinal 954 KCM 54/7 ACSR |  | 150 | 1.94 |  |  | 47603 | PUCT Docket 47603 Approved on 12/27/2017
ETT-130 ETT2015126 | Rio Bravo 1 Wind Generator Temp Connection | Starr | Construct new 345-KV POI temporary tap on the Cenizo-Del Sol 345-kV transmission line for Long Road Energy (Rio Bravo 1) | 2018-04-18 | 2018-09-30 | 2018-10-08 |  | 1400000 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Utilizing Existing Easement
ETT-150 ETT000910 | Laguna Substation | Nueces | Replace insulators and switches for 138-kV conversion and operation | 2019-03-04 | 2020-05-29 |  |  | 1051790 |  |  | 99 | 69 | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-120 P09082009 | Heartland-Yellowjacket ETT | Menard/Menard, McCulloch | Heartland to Yellowjacket: Build 18.75 miles of new transmission line to 138-kV standards and operate at 69 kV | 2019-03-07 | 2019-10-21 | 2020-06-03 | 19824000 | 19824000 |  |  | 99 |  | 138 | 18.5 | 959.6 ACSR/TW | Single Pole Brace Post |  |  | 100 | 18.5 | 46234 | CCN approved on 8/31/2017 ETT Portion Only
ETT-146 P15177001 P15177002 P15177003 | Stewart Rd. 345-kV Hairpin | Hidalgo/Hildago | Construct a double-circuit 345-kV transmission line from the Stewart Rd. Station to the North Edinburg-SU Palmito 345-kV transmission line. Costs include CCN & ROW. | 2020-07-06 | 2021-05-19 | 2021-05-19 | 16834000 |  |  |  | 97 |  | 345 | 5 | 2-954 ACSR | Steel Mono Pole |  |  | 150 | 5 | 47603 | PUCT Docket 47973 Approved on 02/14/2019
ETT-130 P17216001 | Rio Bravo I Windfarm Permanent Interconnect | Starr,Zapata | Add second circuit to 26.6 miles of the Cenizo - Del Sol 345-kV double-circuit capable transmission line to permanently interconnent Rio Bravo Windfarm I | 2019-07-15 | 2020-02-17 | 2019-12-19 |  | 19400000 |  |  | 99 | 345 |  | 26.6 | 2-954 ACSR/AW 54/7 "Cardinal" | Steel Mono Pole | 150 | 26.6 |  |  | 16 TAC 25.83(a)(3) | Second 345-kV circuit previously certificated
ETT-120 P09082011 | Heartland-Yellowjacket 69-kV: Terminate line into Yellowjacket ETT | Menard/Menard | Add third rung and breakers to exising station to terminate new Hearland-Yellowjacket 69-kV transmission line. Replace RTU. | 2019-10-04 | 2019-12-20 | 2020-06-03 |  | 1303055 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-158 P18078001 | Vera Wind Interconnection | Wilbarger | Construct 3.80 miles of new single-circuit transmission line, except of an approximate 0.7 mile section, from the new ETT Coulomb Substation to the Vera Wind Collector Station. | 2019-09-23 | 2020-04-10 | 2020-04-27 | 10700000 | 7800000 |  |  | 99 |  | 345 | 3.8 | 2-954 ACSR | Steel Mono Pole |  |  | 150 | 3.8 | 48945 | CCN Approved on 03/27/2019
ETT-158 P18078011 | Vera Wind Interconnection | Wilbarger | Coulomb 345-kV Substation Cut-In: Terminate the Clear Crossing to Edith Clarke 345-kV transmission line into new Coulomb 345-kV Substation. | 2019-12-06 | 2020-04-10 | 2020-04-27 |  | 1500000 |  |  | 99 |  | 345 | 0.1 | 2-1590 ACSS | Steel Mono Pole |  |  | 150 | 0.1 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
ETT-158 P18078017 | Vera Wind Interconnection | Wilbarger | Coulomb 345-kV Substation: Construct a new three-breaker 345-kV substation to permanently interconnect Vera Wind's 220.4 MW Windfarm. | 2019-09-23 | 2020-04-24 | 2020-04-27 | 14000000 | 14000000 |  |  | 99 |  | 345 | [7 empty] | 48945 | CCN Approved on 03/27/2019
ETT-161 P19010001 | Reloj Del Sol Permanent Interconnection: Add New Circuit | Webb | Add second circuit to 15 miles of the Cenizo - Del Sol 345-kV double-circuit capable transmission line to permanently interconnent Reloj Del Sol's 209 MW Windfarm | 2020-02-03 | 2020-12-17 | 2020-12-22 |  | 20000000 |  |  | 99 | 345 |  | 15 | 2-954 ACSR |  | 150 | 15 |  |  | 16 TAC 25.83(a)(3) | Second 345-kV circuit previously certificated
ETT-161 P19010005 | Reloj Del Sol Permanent Interconnection: Cenizo Station Work | Webb | Cenizo 345-kV Substation: Install new 63kA Terminal, install SSO Relay, install P&C Equipment, & install Metering Equipment | 2020-05-01 | 2020-09-20 | 2020-09-20 |  | 4000000 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-153 P17254001 | Quihi 138-kV Switching Station | Medina | Construct a three (3) switch In and Out 138k-V Switching Station. Install SCADA, RTU, Telecom, and Relaying Panels. ETT will constuct, own, and operate the high side, and STEC will construct, own, and operate the low side (25 kV) | 2020-02-17 | 2020-06-30 | 2020-10-13 |  | 1505771 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | STEC Providing Station Property for Construction
ETT-168 A19600003 | Del Sol 345-kV Station: Replace RLS Circuit Switcher | Starr | Replace CS 4568 with 345 kV, 5000 A, 63 kA breaker with Pre-Insertion Resistors. Remove CB 1750 & Update Drawing. | 2020-04-07 | 2020-05-15 | 2020-06-29 |  | 1261206 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-168 A19600006 | Riley 345-kV Station: Replace RLS Circuit Switcher | Wilbarger | Replace CS's 9358, 11993, 7468, 7518, 14003, and 9048 with 345 kV, 5000 A, 63 kA breakers with Pre-Insertion Resistors. Remove CBs 13995 and 12375 & Update Drawing. | 2020-06-15 | 2021-04-30 | 2021-04-22 |  | 5505497 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-168 A19600007 | Tesla 345-kV Station: Replace RLS Circuit Switcher | Childress | Replace CS's 7238, 10812, 7247, 9007, and 8657 with 345 kV, 5000 A, 63 kA breakers with Pre-Insertion Resistors. Remove CB 12750 & Update Drawing. | 2020-06-01 | 2022-04-08 |  |  | 3368841 |  |  | 25 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-169 A19601002 | Riley 345-kV Station: Replace SSVTs | Wilbarger | Replace Alstom 345 kV SSVTs with (4) 50 kVA ABB SSVTs and (2) 100 kVA ABB SSVTs | 2020-09-18 | 2020-10-05 | 2020-06-26 |  | 2414815.25 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-139 ET1600801 | Maplewood Interconnection: LCRA Bakersfield 345-kV Station | Pecos | Add one breaker, two switches rated 345-kV, 5000A, 63kA. Install SSO relay on line to IPP. Frequency should be set for 1Hz to 10 Hz range. Intall PMU equipment on line to IPP. | 2020-09-29 | 2020-10-30 | 2021-01-26 | 2206000 | 1349176 |  |  | 99 | 345 | [8 empty] | 47603 | PUCT Docket 47603 Approved on 12/27/2017
ETT-139 ET1600802 | Maplewood Interconnection: Red Barn 345-kV Station IPP-Owned Station | Pecos | Add new 345-kV transmission line circuit from the LCRA TSC Bakersfield Station to the point of interconnection at Red Barn | 2020-09-29 | 2020-10-30 | 2021-01-26 | 748000 | 747997 |  |  | 99 | 345 | [8 empty] | 47603 | PUCT Docket 47603 Approved on 12/27/2017
ETT-164 DP19X06C0 | Dustdevil 138-kV Substation: T-Line Assets (ETT) | Laredo/Webb | Install two (2) in-line T-Line structures terminate the Laredo VFT #1 to Lobo transmission line into new Dustdevil 138-kV Substation. | 2020-08-15 | 2021-03-31 |  |  | 908963 |  |  | 30 |  | 138 | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
ETT-164 DP19X06D1 | Dustdevil 138-kV Substation: T-Station Assets (ETT) | Laredo/Webb | Install two (2) motor operated switches and a manual bus tie switch. Install DM 61.01 Transmission RTU Panel. Station transmission 138-kV bus will now be an in & out configuration. | 2020-08-15 | 2021-03-31 |  |  | 1010995 |  |  | 30 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
ETT-161 P19010002 | Reloj Del Sol Permanent Interconnection: New 345-kV Transmission Line | Webb | Construct six (6) miles of new single circuit 345-kV Transmission line to connect the Reloj Del Sol Windfarm | 2020-07-20 | 2020-12-17 | 2020-12-22 | 7100000 | 7500000 |  |  | 99 |  | 345 | 6 | 2-754 ACSR | Concrete & Steel Monopole |  |  | 150 | 6 | 50690 | PUCT Docket 50690 Approved on 06/30/2020
ETT-153 P17254002 | Quihi 138-kV Switching Staion: Cut-In | Medina | Terminate the Castroville to Razorback 138-kV transmission line into the new Quihi 138-kV Switching Station with double-circuit structures. | 2020-10-19 | 2020-11-16 | 2020-10-13 |  | 773419 |  |  | 99 |  | 138 | 0.08 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.08 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
ETT-169 A19601004 | Jim Treece 345-kV Station: Replace SSVTs | Wilbarger | Replace 345-kV SSVTs with (4) 50 kVA SSVTs | 2020-11-02 | 2020-11-22 | 2020-11-19 |  | 1603035 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-169 A19601006 | Bakersfield 345-kV Station: Replace SSVTs | Pecos | Replace 345-kV SSVTs with (2) 50 kVA SSVTs | 2020-11-02 | 2021-03-05 | 2021-01-29 |  | 929962 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-169 A19601007 | Big Hill 345-kV Station: Replace SSVTs | Schleicher | Replace 345-kV SSVTs with (2) 50 kVA SSVTs | 2020-11-02 | 2021-03-27 | 2020-12-03 |  | 912720 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-169 A19601008 | Kirchoff 345-kV Station: Replace SSVTs | Fisher | Replace 345-kV SSVTs with (2) 50 kVA SSVTs | 2020-11-02 | 2020-11-07 | 2020-10-22 |  | 920921 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-169 A19601009 | Edison 345-kV Station: Replace SSVTs | Kimble | Replace 345-kV SSVTs with (2) 50 kVA SSVTs | 2020-11-02 | 2021-01-29 | 2021-02-17 |  | 912755 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-169 A19601011 | Oersted 345-kV Station: Replace SSVTs | Sutton | Replace 345-kV SSVTs with (4) 50 kVA SSVTs | 2020-11-02 | 2021-01-07 | 2021-02-01 |  | 1617872 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-168 A19600004 | Edith Clarke 345-kV Station: Replace RLS Circuit Switcher | Foard | Replace CS's 385, 7083, 2737, 2567, and 7117 with 345-kV, 5000 A, 63 kA breakers with Pre-Insertion Resistors. Remove CB 165 & Update Drawing. | 2020-11-02 | 2021-04-30 | 2021-04-30 |  | 4253938 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-168 A19600005 | Oklaunion 345-kV Station: Replace RLS Circuit Switcher | Wilbarger | Replace CS 9292 with 345-kV, 5000 A, 63 kA breaker with Pre-Insertion Resistors. Remove CB 5640 & Update Drawing. | 2021-09-07 | 2021-10-29 |  |  | 1162820 |  |  | 75 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-163 P19045008 | Griffin Wind Interconnection: Line Extension | Knox | Construct 0.30 mile of new single-circuit transmission line, from the new Avogadro 345-kV substation to Griffin Windfarm Collector Station | 2020-12-11 | 2021-05-03 |  |  | 2500000 |  |  | 95 |  | 345 | 0.3 | 2-954 ACSR | Steel Mono Pole |  |  | 150 | 0.3 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
ETT-163 P19045006 | Griffin Wind Interconnection: Cut-In | Knox | Avogadro 345-kV Substation Cut-In: Terminate the Clear Crossing to Edith Clarke 345-kV transmission line into new Avogadro 345-kV Substation. | 2020-12-11 | 2021-05-03 | 2021-05-07 |  | 2000000 |  |  | 99 |  | 345 | 0.01 | 2-954 ACSR | Steel Mono Pole |  |  | 150 | 0.01 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
ETT-163 P19045005 | Griffin Wind Interconnection: Avogadro 345-kV Substation | Knox | Avogadro 345-kV Substation: Construct a new three-breaker 345-kV substation to permanently interconnect Griffin Wind Farm | 2020-11-02 | 2021-05-03 | 2021-05-07 |  | 15500000 |  |  | 99 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
ETT-173 A20120004 | Clear Crossing 345-kV Station Static Mast Pole Replacement | Haskell | Replace static mast structures at Clear Crossing 345-kV Station | 2020-11-03 | 2021-01-15 | 2021-05-27 |  | 1202366 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-173 A20120003 | Tesla 345-kV Station Static Mast Pole Replacement | Childress | Replace static mast structures at Tesla 345-kV Station | 2020-12-10 | 2021-02-26 | 2021-05-20 |  | 1293755 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-173 A20120002 | Riley 345-kV Station Static Mast Pole Replacement | Wilbarger | Replace static mast structures at Riley 345-kV Station | 2020-12-17 | 2021-03-22 | 2021-05-24 |  | 1031453 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-173 A20120001 | Edith Clarke 345-kV Station Static Mast Pole Replacement | Foard | Replace static mast structures at Edith Clarke 345-kV Station | 2020-11-03 | 2021-02-05 | 2021-05-12 |  | 1007216 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-170 P19279001 | Corazon Solar Interconnection: Lobo 345-kV Substation Terminal Addition | Webb | Construct (2) 345-kV CB's, metering equipment, relaying, and station fence expansion | 2020-12-04 | 2021-04-30 | 2021-05-10 |  | 8500000 |  |  | 99 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-170 P19279002 | Corazon Solar Interconnection: Construct 345-kV T-Line | Webb | Construct 3.90 miles of 345-kV single-circuit transmission line from the existing ETT Lobo 345-kV Station to the Corazon Solar interconnect | 2020-11-10 | 2021-05-10 | 2021-05-10 | 8029500 | 8029500 |  |  | 99 |  | 345 | 3.9 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 150 | 3.9 | 50964 | PUCT Docket 50964 Approved on 10/12/2020
ETT-160 P18158003 | TG East Wind Interconnection : Coulomb 345-kV Station Terminal Addition | Wilbarger | Construct a 345-kV CB, metering equipment, and relaying | 2021-02-08 | 2021-04-30 | 2021-04-21 |  | 3800000 |  |  | 99 | 345 | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-160 P18158001 | TG East Wind Interconnection POI | Wilbarger | Construct 345-kV Dead End POI | 2021-02-08 | 2021-04-30 |  |  | 850000 |  |  | 99 |  | 345 | 0.02 | 2 Bundled 954 ACSR | Steel Monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within ETT Property
ETT-171 P20064003 | Azure Sky Solar and Storage Connection: Edith Clarke 345-kV Station Terminal Addition | Throckmorton | Construct a 345-kV CB, metering equipment, and relaying | 2021-01-19 | 2021-04-30 | 2021-04-23 |  | 4500000 |  |  | 99 | 345 | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-171 P20064002 | Azure Sky Solar and Storage Connection: Line Span POI | Throckmorton | Construct a 0.10 mile 345-kV line to Interconnect Azure Sky Solar and Storage | 2021-01-19 | 2021-04-30 |  |  | 1200000 |  |  | 95 |  | 345 | 0.1 | 2 Bundled 954 ACSR | Steel Monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within ETT Property
ETT-168 A19600002 | Clear Crossing 345-kV Station: Replace RLS Circuit Switcher | Haskell | Replace CS’s 717, 667, 1357, 497, 2297, 12558, and 747 with 345 kV, 5000 A, 63 kA breakers with Pre-Insertion Resistors. Remove CB 647 & Update Drawing. | 2021-07-22 | 2022-10-28 |  |  | 5243020 |  |  | 40 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-152d A18048004 | Clear Crossing 345-kV Station: Physical Security | Haskell | Installation of sixteen foot tall fence and new chain link fence around the Clear Crossing 345-kV Station. | 2021-05-04 | 2021-10-19 |  |  | 16145456.33 |  |  | 90 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-175 A20800015 | Cenizo 345-kV Station | Webb | Installing Physical Security to DICM, Telecom Network Splitting, RTAC (Station Data Repository) updates, and Firmware Upgrades. | 2021-07-07 | 2021-08-27 | 2021-08-25 |  | 361273 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
ETT-175 A20800016 | Del Sol 345-kV Station | Starr | Installing Physical Security to DICM, Telecom Network Splitting, RTAC (Station Data Repository) updates, and Firmware Upgrades. | 2021-08-02 | 2021-08-19 | 2021-08-18 |  | 358444 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
ETT-175 A20800017 | Gauss 345-kV Station | Knox | Installing Physical Security to DICM, Telecom Network Splitting, RTAC (Station Data Repository) updates, and Firmware Upgrades. | 2021-05-17 | 2021-06-29 | 2021-08-13 |  | 385009 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
ETT-175 A20800021 | Edison 345-kV Station | Kimble | Installing Physical Security to DICM, Telecom Network Splitting, RTAC (Station Data Repository) updates, and Firmware Upgrades. | 2021-06-01 | 2021-07-07 | 2021-08-17 |  | 393459 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
ETT-172 P19301007 | Scout 69-kV POD Box Bay | Taylor | Construct POD with three (3) motor operated switches. All equipment will be designed for 2000A. Install B2500 Cabinet. | 2021-06-05 | 2021-10-03 |  |  | 1026417 |  |  | 0 |  | 69 | [7 empty] | 16 TAC 25.83(a)(3) | Landowner Consent Obtained
ETT-172 P19301002 P19301006 | Abilene South - Steamboat 69-kV T-Line | Taylor | Terminate the Abilene South to Steamboat 69-kV transmission line into new Scout 69-kV POD Box Bay. | 2021-06-05 | 2021-10-03 |  |  | 663660 |  |  | 0 | 69 |  | 0.01 | 4/0 ACSR 6/1 "Penguin" | Steel Mono Pole |  |  | 100 | 0.01 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
ETT-172 P19301008 | Scout - Jim Ned 69-kV POI Dead-End | Taylor | Construct 0.01 mile Dead-End span of 69-kV T-Line to Jim Ned POI. | 2021-06-05 | 2021-10-03 |  |  | 61776 |  |  | 0 | 69 |  | 0.01 | 4/0 ACSR 6/1 "Penguin" | Steel Mono Pole |  |  | 100 | 0.01 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
ETT-152a A18048001 | Edith Clarke 345-kV Station: Physical Security | Foard | Installation of sixteen foot tall fence and new chain link fence around the Edith Clarke 345-kV Station. | 2021-06-04 | 2021-12-15 |  |  | 14532737.38 |  |  | 60 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-800 P19213005 | Steamboat 69-kV Substation: T-Station Assets | Taylor | Install 69-kV Circuit Breaker 4200 and associated jumpers. Install 69kV Bus #2 CCVT, 69-kV Motor Operated Transformer Disconnect Switch 12783, 69kV Circuit Switcher 12782, and all associated bus work. | 2021-08-23 | 2021-11-18 |  |  | 963246 |  |  | 70 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
ETT-900 P19213001 P19213002 P19213003 | Bradshaw to Steamboat 69-kV T-Line | Taylor | Rebuild and reconductor the Bradshaw to Steamboat 69-kV transmission line to 138-kV standards. Will continue to operate at 69-kV. | 2021-09-01 | 2021-11-22 |  |  | 1058272 |  |  | 33 | 69 |  | 0.35 | 795 KCM ACSR "Drake" | Steel Mono Pole | 50 | 0.35 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
ETT-152b A18048002 | Riley 345-kV Station: Physical Security | Wilbarger | Installation of sixteen foot tall fence and new chain link fence around the Riley 345-kV Station. | 2021-09-03 | 2022-02-28 |  |  | 15045950.64 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-901 A19057001 A19057002 A19057003 | Tuscola to Bradshaw 69-kV T-Line | Tuscola/Taylor | Rebuild and reconductor the Tuscola to Bradshaw 69-kV transmission line to 138-kV standards. Will continue to operate at 69-kV. | 2021-10-15 | 2022-03-03 |  |  | 7431221 |  |  | 0 | 69 |  | 9.55 | 795 KCM ACSR "Drake" | Steel Mono Pole | Various | 9.55 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners noticed
ETT-157a P18126001 P18126009 | McKenzie - Westside 138-kV: Rebuild | Corpus Christi/ Nueces | Rebuild and reconductor the McKenzie to West Side 138-kV transmission line from the Westside Switch Station to structure 5/9. | 2021-10-04 | 2022-05-07 |  |  | 19805943 |  |  | 0 | 138 |  | 10.72 | 795 KCM ACSS "Drake" | Steel Monopole | Various | 10.72 |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
ETT-157 P18126010 | McKenzie - Westside 138-kV: Fiber Replacement | Corpus Christi/ Nueces | Replace the fiber on the McKenzie Rd. Substation to Westside Switch Station 138-kV transmission line. | 2021-10-04 | 2022-05-07 |  |  | 1763171 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
ETT-152c A18048003 | Tesla 345-kV Station: Physical Security | Childress | Installation of sixteen foot tall fence and new chain link fence around the Tesla 345-kV Station. | 2021-10-04 | 2022-04-30 |  |  | 14505930.55 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-800 P18045002 | Zapata 138-kV Substation: Add Reactor | Zapata | Install (1) 10-MVAR 138-kV Shunt Reactor. Install (1) 138-kV breaker compatible with shunt reactor, 3000A, 40kA. Install reactor bank relay protection. Expand existing control to accommodate relay panels, or DICM needed. Add area reactive controller. | 2021-03-22 | 2021-11-19 |  |  | 3500000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property (Project started in 1st Quarter of 2021 but was inadvertently missed - No Landowner Notice was required for this Project)
ETT-152d A18048006 | Clear Crossing 345-kV Station: Physical Security | Haskell | Installation of security equipment around the Clear Crossing 345-kV Station. | 2021-11-04 | 2021-11-30 |  |  | 868090 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-152a A18048007 | Edith Clarke 345-kV Station: Physical Security | Foard | Installation of security equipment around the Edith Clarke 345-kV Station. | 2021-12-01 | 2022-01-31 |  |  | 970326 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-176 P21200002 P21200001 | Nebula 345-kV Station | Scurry | Construct a new three (3) breaker ring, 345-kV Station. Install three (3) 345-kV, 5000A, 63kA breakers. Install DICM, RTU, SSO Relays, and EPS Meter. Install telecom equipment and terminate fiber. ONCOR – To update relay settings at Dermott. Update relaying and protection at Figaro. | 2022-01-10 | 2022-11-18 |  |  | 15903000 |  |  | 0 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Construction Right-of-Entry obtained
ETT-176 P21200003 P21200004 P21200005 | Dermott - Figaro 345-kV T-Line: Cut-In | Scurry | Terminate the existing Dermott to Figaro 345-kV transmission line into new Nebula 345-kV Station. | 2022-01-10 | 2022-11-18 |  |  | 1559400 |  |  | 0 | 345 |  | 0.05 | 1590 ACSR Bundled "Lapwing" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property Construction Right-of-Entry obtained for station property
ETT-176 P21200006 P21200007 P21200008 | Nebula - Andromenda 345-kV T-Line | Scurry | Construct a 1.70 mile 345-kV transmission line from Nebula 345-kV Station to Andromeda Solar Point of Interconnect (POI). | 2022-01-10 | 2022-11-18 |  |  | 3852500 |  |  | 0 |  | 345 | 1.7 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 150 | 1.7 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
ETT-178 P21208001 | Bakersfield 345-kV Station: Hydra BESS Terminal | Pecos | Construct (2) 345-kV CB, a 345-kV terminal, metering equipment, and relaying. | 2022-01-24 | 2022-05-15 |  |  | 4872881 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property