## MonthlyReportForm
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
TL282 | TxDOT SL375 Interchange Improvements | El Paso, El Paso | Adjust two 345kV transmission lines (Caliente to Amrad and Caliente to Picante) across State Highway Loop 375, south of Iron Medics Dr., to accommodate the new eastbound and westbound frontage roads to be constructed by TxDOT. EPE will replace several poles on either side of State Highway Loop 375 with taller steel poles for each line. | 2020-02-06 | 2021-01-30 | Caliente to Amrad 1/30/21 | 4292714 | 4292714 |  |  | 100% | 345 | n/a | 0.73 each | 954 ACSR corncrake double bundle conductor | Replace wood H-frame structures with 90'-125' steel H-frame or 3-pole structures. | 300 | 0.73 each | n/a | n/a | 25.101(c)(5)(F) | Final phase of the project completed. Remaining steel poles erected, new conductor, fiber, and static wire installed. Caliente Amrad 345kV line energized January 30, 2021.
TL283 | TxDOT SL375 Interchange Improvements | El Paso, El Paso | Adjust two 345kV transmission line (Caliente/Amrad and Caliente Picante) and two 115kV transmission lines (Global Reach/Picante and Liberty/Bliss Industrial) across State Highway Loop 375, north of Iron Medics Dr., to accommodate the new eastbound and westbound frontage roads to be constructed by TxDOT. EPE will replace several poles on either side of State Highway Loop 375 with taller steel poles for each line. | 2020-02-28 | 2021-01-30 | Caliente to Amrad 1/30/21 | 3372668 | 3372662 |  |  | 100% | 115 & 345 | n/a | 115kV-0.34 each & 345kV 0.37 each | 115kV-954 ACSR single bundle & 345kV 954 ACSR double bundle | 115kV each line install 100' tangent steel H-frame structures and 70'- 3 pole steel deadend structures. 345kV 90'-125' steel H-frame or 3-pole dead end structures | 115kV-100 & 345kV-300 | 115kV -0.34 each & 345kV 0.37 each | n/a | n/a | 25.101(c)(5)(F) | Final phase of the project completed. Remaining steel poles erected, new conductor, fiber, and static wire installed. Caliente Amrad 345kV line energized January 30, 2021.
TL101 | Rio Grande to Sunset 69kV and Rio Grande to Sunset North 115kV transmission lines rebuild and reconductoring. | El Paso, El Paso | Rebuild two 69kV lines from Rio Grande to Sunset, and one 115kV line from Rio Grande to Sunset North, by upgrading the conductor and replacing existing wooden poles with one double-circuit and one single-circuit steel monopole line. One line will carry a 69kV line. The second line will carry a 69kV line and a 115kV double-bundle line. | 2019-07-31 |  |  | 22888944 | 22888944 |  |  | 20% | 69 & 115 | n/a | 5.24-115kV & 10.04 -69KV | 69kV lines replace 336 and 556 ACSR single bundle conductor with 954 ACSR single bundle and replace the 115kV - 556 ACSR double bundle conductor with 954 ASCR double bundle | All steel structures varying between 75' to 120' in height; single circuit tangent structures, double circuit tangent monopoles, and drill pier foundation dead end | 50'-100' | 4.32-115kV & 9.12-69kV | n/a | n/a | 25.101(c)(5)(B)
TL106 | Wrangler to Sparks rebuild and reconductor | El Paso, El Paso | Rebuild a portion of the 115kV transmission line by replacing structures, upgrading the conductor, and adding optical ground wire. | 2021-12-15 |  |  | 1911367 | 3140272 |  |  | 40% | 115 | n/a |  | Replace 336 single bundle with 954 ACSR single bundle | 85' to 100' steel monopoles | TxDOT ROW | 2.66 | n/a | n/a | 25.101(c)(5)(B) | Completed 2 of 3 foundations, third foundation pending approval of traffic control plan by TxDOT. Hole digging and pole installation in progress.
TS117 | Butterfield to Newman 115kV extend transmission service to a new Fort Bliss Military Reservation substation | El Paso, El Paso | 115kV in and out tap to service a new, North Bliss substation, inside the military reservation and install optical ground wire from Butterfield to North Bliss substations | 2020-09-17 |  |  | 450685 | 450685 |  |  | 80% | 115 | n/a | 0.42 | Replace 556 ACSR singlebundle with 954 ACSR single bundle for the new portion into North sub | 75' steel monopoles and 100' steel double circuit monopoles | 25 | 0.47 | 60 | 0.21 | 25.101(c)(5)(F) & 25.101(c)(5)(A)
TL293 | Fabens to Felipe 69kV rebuild and reconductor | Fabens, El Paso | Rebuild a portion of the 69kV transmission line by replacing structures, upgrading the conductor and add optical ground wire | 2020-09-14 | 2020-12-15 | 2020-12-15 | 1243185 | 1695900 |  |  | 100% | 69 | n/a | 2.53 | Replace 4/0 ACSR single bundle with 954 ACSR single bundle | 70'-95' steel support structures on drill pier foundations and monopoles | Street ROW and 60' | 1.14 | Street ROW and 60' | 1.39 | 25.101(c)(5)(A)(ii)&(F)(i)
TL253 | Scotsdale to Farah and Farah to Viscount Osmose Pole Replacements | El Paso, El Paso | Replace wood poles that failed the integrity/strength test by Osmose | 2021-01-18 |  |  | 690086 |  |  |  |  | 69 | n/a | 0.29 & 1.39 | 556 ACSR single bundle | 85' steel monopoles | TxDOT ROW | 0.29 & 1.39 | n/a | n/a | 25.101(c)(5)(B)
TL244 | Pine-to-Seabeck 115-KV Transmission Line | El Paso, El Paso | Construction and operation of a new 115kV transmission line from Pine Substation to Seabeck Substation | 2024-02-01 |  |  | TBD by final order |  |  |  |  | n/a | 115 | TBD by final order | 954 ACSR rail, single circuit | 95' - 110' delta or vertical steel monopole, self-support or on drilled pier foundations | n/a | n/a | 150 | TBD | 51476 | Filed November 16, 2020
TL245 | Seabeck-to-San Felipe 115-KV Transmission Line | El Paso, El Paso | Construction and operation of a new 115kV transmission line from Seabeck Substation to San Flipe Substation | 2024-02-01 |  |  | TBD by final order |  |  |  |  | n/a | 115 | TBD by final order | 954 ACSR rail, single circuit | 95' - 110' delta or vertical steel monopole, self-support or on drilled pier foundations | n/a | n/a | 150 | TBD | 51480 | Filed November 16, 2020
Note on H1: Author: Please enter only a single integer, if possible.
Note on I1: Author: Please enter only a single integer, if possible.
Note on M1: Author: If applicable.
Note on N1: Author: If applicable.