## 2020 Draft L&R
SOAH Docket No. 473-21-2606
PUC Docket No. 52195
FMI's 1st, Q. No. FMI 1-3
Attachment 1
Page 1 of 1
El Paso Electric Company
Loads & Resources 2021-2030 w/ 2021 Updated Load Forecast
Issued 7/2/2020
|  | 170 Solar 100/50 Sol/Batt | Newman 6 |  | 48 Geo 100/100 Sol/Batt |  | 130 Solar CT 100 CT 228 |  |  | 48 Geo
Planned Generation Additions
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 100 MW Solar (25 MW at Peak) in 2022
1.0 GENERATION RESOURCES1 | [10 empty] | Solar/Batt Combo (100/50 MW) in 2022 (75 MW at Peak)
1.1 RIO GRANDE | 271 | 271 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | Newman 6 GT5 (228 MW) in 2023
1.2 NEWMAN | 729 | 729 | 809 | 809 | 809 | 809 | 496 | 496 | 496 | 496 | 70 MW Solar (18 MW at Peak) in 2022
1.3 COPPER | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | Unit Retirements
1.4 MONTANA | 352 | 352 | 352 | 352 | 352 | 352 | 352 | 352 | 352 | 352 | Rio Grande 6 (45MW) (inactive reserve)
1.5 PALO VERDE | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 622 | Rio Grande 7 (44MW) - December 2022
1.6 RENEWABLES2 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Newman 1 (74MW) - December 2022
1.7 STORAGE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Newman 2 (74MW) - December 2022
1.8 POSSIBLE EMERGING TECHNOLOGY EXPANSION3 | 0 | 0 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | Newman 3 (93MW) - December 2026
1.9 INTERRUPTIBLE4 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | Newman 4 CC (220MW) - December 2026
1.10 LINE LOSSES FROM OTHERS5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Copper (63MW) - December 2030
1.0 TOTAL GENERATION RESOURCES | 2107 | 2107 | 2143 | 2142 | 2182 | 2182 | 1869 | 1869 | 1869 | 1869 | Rio Grande 8 (139MW) - December 2033
Company Owned Renewables
2.0 RESOURCE PURCHASES | [10 empty] | Line 1.6 consists of EPE Community Solar,
2.1 RENEWABLE PURCHASE6 | 73 | 72 | 72 | 72 | 71 | 71 | 70 | 70 | 69 | 69 | Holloman Solar, EPCC, Stanton, Wrangler,
2.2 NEW RENEWABLE PURCHASE7 | 0 | 43 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | Rio Grande & Newman Carports and Van Horn
2.3 NEW RENEWABLE/ BATTERY PURCHASE8 | 0 | 75 | 75 | 75 | 75 | 75 | 74 | 74 | 74 | 74 | Renewable Purchases
2.4 NEW BATTERY PURCHASE9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Line 2.1 includes SunEdison, NRG, Macho Springs, Juwi,
2.5 MARKET RESOURCE PURCHASE10 | 195 | 100 | 95 | 125 | 0 | 20 | 15 | 45 | 100 | 100 | and Hatch solar purchases (70% availability at Peak)
2.0 TOTAL RESOURCE PURCHASES | 268 | 290 | 284 | 314 | 188 | 208 | 200 | 230 | 284 | 284 | New Renewable Purchase
Line 2.2 includes system solar resource 100 MW Solar
3.0 FUTURE RESOURCES11 | [10 empty] | (25 at Peak) and NM RPS solar resource 70 MW in 2022
3.1 RENEWABLE | 0 | 0 | 0 | 0 | 48 | 48 | 81 | 81 | 81 | 129 | (18 MW at Peak)
3.2 RENEWABLE/STORAGE | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | Resource Purchase
3.3 GAS GENERATION | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 328 | 328 | 328 | This purchase is supported by firm transmission
3.0 TOTAL RESOURCE PURCHASES | 0 | 0 | 0 | 0 | 148 | 148 | 509 | 509 | 509 | 557 | through (i) simultaneous buy/sell with
(i) Freeport McMoRan (formerly Phelps Dodge),
4.0 TOTAL NET RESOURCES (1.0 + 2.0 + 3.0) | 2375 | 2397 | 2427 | 2456 | 2518 | 2538 | 2578 | 2608 | 2662 | 2710 | (ii) Four Corners-West Mesa transmission
retired, and (iii) SPS via the Eddy Tie.
5.0 SYSTEM DEMAND12 | [10 empty] | Future Resources (subject to RFP results)
5.1 NATIVE SYSTEM DEMAND13 | 2137.6376 | 2188.7005 | 2226.5179 | 2254.5616 | 2296.0318 | 2335.4989 | 2378.8535 | 2417.0478 | 2471.4068 | 2522.2838 | Line 3.0 includes
5.2 DISTRIBUTED GENERATION | -9.2741 | -18.5018 | -21.9356 | -21.9356 | -21.9356 | -21.9356 | -21.9356 | -21.9356 | -21.9356 | -21.9356 | 48 MW Geothermal NM RPS resource in 2025
5.3 ENERGY EFFICIENCY | -7.688 | -15.3761 | -23.0641 | -30.7521 | -38.4402 | -46.1282 | -53.8162 | -61.5043 | -69.1923 | -76.8803 | 100/100 MW Solar/Batt Combo NM RPS in 2025
6.0 TOTAL SYSTEM DEMAND (5.1 - (5.2+5.3) ) | 2120.6755 | 2154.8226 | 2181.5182 | 2201.8738 | 2235.656 | 2267.4351 | 2303.1016 | 2333.6079 | 2380.2788 | 2423.4678 | 130 MW Solar (33 MW at Peak) system resource in 2027
7.0 MARGIN OVER TOTAL DEMAND (4.0 - 6.0) | 254.3245 | 242.1774 | 245.4818 | 254.1262 | 282.344 | 270.5649 | 274.8984 | 274.3921 | 281.7212 | 286.5322 | 100 MW CT system resource in 2027
8.0 PLANNING RESERVE 15% OF TOTAL DEMAND | 318.1013 | 323.2234 | 327.2277 | 330.2811 | 335.3484 | 340.1153 | 345.4652 | 350.0412 | 357.0418 | 363.5202 | 228 MW CT System Resource in 2027
9.0 MARGIN OVER RESERVE (7.0 - 8.0) | -64 | -81 | -82 | -76 | -53 | -70 | -71 | -76 | -75 | -77
1. Generation unit retirements are consistent with the 2018 IRP. Rio Grande 6 is classified as inactive reserve.
2. Existing EPE owned solar renewables at 70 percent contribution to peak.
3. Emerging technologies may include customer or other distributed resources as well as additional community solar.
4. Interruptible customer capacity shifted to the resource side of the L&R. Capacity MW contribution per 2020 Load Forecast.
5. Line losses from others shifted to resource side of the L&R and is the typical amount of repayment of transmission wheeling losses from transimission customers with in-kind energy during peak hours.
6. Existing renewable solar PPAs at 70 percent contribution to peak.
7. New renewable solar PPAs at 25 percent contribution to peak.
8. New solar and battery storage PPAs with solar at 25 percent contribution to peak.
9. 50 MW stand-alone battery was denied in NMPRC Case No. 19-00348-UT. The resource purchase on line 2.5 was adjusted to replace 50 MW capacity as required to meet the planning reserve margin.
10. Denotes market purchase either spot market or short-term purchased power. Amounts greater than 645 MW-PV output will need to come into EPE via exchange (Freeport), through the acquisition of additional transmission or on a non-firm path. Also, availability of such power is not guaranteed.
11. Future Resources from 2025 forward are to address both NM RPS and capacity needs. EPE will be initiating its 2021 IRP planning cycle which may result in changes to future planned resources.
12. System demand is based on the 2020 Long-Term Forecast dated April 1, 2021.
13. Native System Demand includes added load due to Electric Vehicles.