## Table
SOAH Docket No. 473-21-2606
PUC Docket No. 52195
FMI's 1st, Q. No. FMI 1-3
Attachment 3
Page 1 of 1
EL PASO ELECTRIC COMPANY
LOCAL PLANT UNIT CAPACITY PROJECTIONS
| Peak Period Capacity (1) |  |  |  | Off-Peak Period Capacity |  |  | Unit Minimum Capacity
UNIT | MANUAL CTRL | Gross MW | SS(2) | Net MW | Gross MW | SS(2) | Net MW | MANUAL CTRL | Gross MW ⁽⁴⁾ | SS(2) | Net MW
COP | 64 | 64 | 1 | 63 | 66 | 1 | 65 | 4 | 4 | 1 | 3
NWM 1 | 80 | 78 | 4 | 74 | 82 | 4 | 78 | 30 | 33 | 4 | 29
NWM 2 | 80 | 78 | 4 | 74 | 82 | 4 | 78 | 30 | 33 | 4 | 29
NWM 3 | 100 | 98 | 5 | 93 | 103 | 5 | 98 | 30 | 33 | 5 | 28
NWM 4GT1 | 68 | 68 | 1 | 67 | 72 | 1 | 71 | 10 | 35 | 1 | 34
NWM 4GT2 | 68 | 68 | 1 | 67 | 72 | 1 | 71 | 10 | 35 | 1 | 34
NWM 4GT, NWM 4ST(3) | 112 | 112 | 2 | 110 | 118 | 2 | 116 | 85 | 85 | 2 | 83
NWM4 GT1 & GT2, NWM4 ST & DF(3) | 224 | 224 | 4 | 220 | 236 | 4 | 232 | 98 | 98 | 4 | 94
NWM 5GT3 | 72 | 72 | 2 | 70 | 73 | 2 | 71 | 36 | 36 | 2 | 34
NWM 5GT4 | 72 | 72 | 2 | 70 | 73 | 2 | 71 | 36 | 36 | 2 | 34
NWM 5GT & NWM 5ST & DF | 138 | 138 | 4 | 134 | 139 | 4 | 135 | 108 | 108 | 3 | 105
NWM5 GT3 & GT4, NWM5 ST & DF | 276 | 276 | 8 | 268 | 279 | 8 | 271 | 128 | 128 | 7 | 121
RGD 6 | 47 | 47 | 2 | 45 | 49 | 2 | 47 | 18 | 20 | 2 | 18
RGD 7 | 47 | 46 | 2 | 44 | 50 | 2 | 48 | 18 | 20 | 2 | 18
RGD 8 | 150 | 145 | 6 | 139 | 153 | 6 | 147 | 46 | 50 | 6 | 44
RGD 9 | 90 | 90 | 2 | 88 | 92 | 2 | 90 | 20 | 20 | 2 | 18
MPS 1 | 90 | 90 | 2 | 88 | 95 | 2 | 93 | 20 | 20 | 2 | 18
MPS 2 | 90 | 90 | 2 | 88 | 95 | 2 | 93 | 20 | 20 | 2 | 18
MPS 3 | 90 | 90 | 2 | 88 | 95 | 2 | 93 | 20 | 20 | 2 | 18
MPS 4 | 90 | 90 | 2 | 88 | 95 | 2 | 93 | 20 | 20 | 2 | 18
Effective Date: January 1, 2020
NOTES:
1. Peak Period includes May thru September. |  |  |  |  | Reviewed:
Ambient conditions impact unit output. | [6 empty] | Fred Prutch |  |  |  | Date
Table data for peak period is based on
95-102 °F and relative humidity of 10-20%.
2. SS: Station Service values are average values for |  |  |  |  | Reviewed:
normal equipment in service. | [6 empty] | John D. Aranda |  |  |  | Date
3. U4 EVAP COOLERS OOS OCT-APR. Includes 20 MW for duct burners
4. Min capacities are based on boiler/turbine controls in auto mode.
Reviewed:
Duct Firing (DF): Included in table | [6 empty] | Albert Montano |  |  |  | Date
- Duct firing NM4 total output: 10MW per CT online added to Steamer output
- Duct Firing NM5 total output: 10MW per CT online added to Steamer output
Reviewed:
[7 empty] | Louie Guaderrama |  |  |  | Date