## PVGS1
EL PASO ELECTRIC COMPANY | [7 empty] | SCHEDULE H-6.1a
2021 TEXAS RATE CASE FILING | [7 empty] | PAGE 1 OF 4
SCHEDULE H-6.1a: NUCLEAR UNIT OUTAGE HISTORY
SPONSOR: DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
PALO VERDE GENERATING STATION (A) *
[5 empty] | TYPE | MAXIMUM | UNIT
UNIT | OUTAGE | DATE | DATE | OUTAGE | OF | POWER LEVEL | SHUTDOWN
NAME | NUMBER | STARTED | ENDED | DURATION | OUTAGE | PERMITTED | METHOD | REASON FOR OUTAGE
|  | (B) | (B) | (Hours) (C) | (Note 1) | (MWs) (D) | (Note 2)
PVGS | U1R22 | 2020-10-10 | 2020-12-03 | 1311:06 | S | 0 | M | 22nd Refueling Outage
Unit 1
NOTE 1: USE THE FOLLOWING OUTAGE CATEGORIES |  |  |  |  | NOTE 2: USE THE FOLLOWING UNIT SHUTDOWN CATEGORIES
| F = Forced Outage |  |  |  |  | AT = Automatic Trip |  | M = Manual Controlled Shutdown
| S = Scheduled Outage |  |  |  |  | MT = Manual Trip (Note F) |  | O = Other
* The letters in parentheses refer to additional notes by EPE. Refer to the last page of Schedule H-6.1a for further explanation.
For Downpowers, Maximum Power Level Permitted is calculated using Design Electric Rating.

## PVGS2
EL PASO ELECTRIC COMPANY | [7 empty] | SCHEDULE H-6.1a
2021 TEXAS RATE CASE FILING | [7 empty] | PAGE 2 OF 4
SCHEDULE H-6.1a: NUCLEAR UNIT OUTAGE HISTORY
SPONSOR: DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
.
PALO VERDE GENERATING STATION (A) *
[5 empty] | TYPE | MAXIMUM | UNIT
UNIT | OUTAGE | DATE | DATE | OUTAGE | OF | POWER LEVEL | SHUTDOWN
NAME | NUMBER | STARTED | ENDED | DURATION | OUTAGE | PERMITTED | METHOD | REASON FOR OUTAGE
|  | (B) | (B) | (Hours) (C) | (Note 1) | (MWs) (D) | (Note 2)
PVGS | N/A | 2020-03-03 | 2020-03-07 | 97:50 | F | 0 | AT | Automatic Reactor Trip on Low Steam Generator Level and Auxiliary Feedwater Actuation Signal due to both Main Feedwater Pumps tripping due to a human performance error.
Unit 2
| U2R22 | 2020-04-03 | 2020-05-05 | 749:23 | S | 0 | M | 22nd refueling outage
| N/A | 2020-05-25 | 2020-05-26 | 18:00 | F | 1233.95 | O | Power reduced in Unit to 92.5% due to Heater Drain Tank "B" High Level Control Valve failing open.
NOTE 1: USE THE FOLLOWING OUTAGE CATEGORIES |  |  |  |  | NOTE 2: USE THE FOLLOWING UNIT SHUTDOWN CATEGORIES
| F = Forced Outage |  |  |  |  | AT = Automatic Trip |  | M = Manual Controlled Shutdown
| S = Scheduled Outage |  |  |  |  | MT = Manual Trip (Note F) |  | O = Other
* The letters in parentheses refer to additional notes by EPE. Refer to the last page of Schedule H-6.1a for further explanation.
For Downpowers, Maximum Power Level Permitted is calculated using Design Electric Rating.

## PVGS3
EL PASO ELECTRIC COMPANY | [7 empty] | SCHEDULE H-6.1a
2021 TEXAS RATE CASE FILING | [7 empty] | PAGE 3 OF 4
SCHEDULE H-6.1a: NUCLEAR UNIT OUTAGE HISTORY
SPONSOR: DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
PALO VERDE GENERATING STATION (A) *
[5 empty] | TYPE | MAXIMUM | UNIT
UNIT | OUTAGE | DATE | DATE | OUTAGE | OF | POWER LEVEL | SHUTDOWN
NAME | NUMBER | STARTED | ENDED | DURATION | OUTAGE | PERMITTED | METHOD | REASON FOR OUTAGE
|  | (B) | (B) | (Hours) (C) | (Note 1) | (MWs) (D) | (Note 2)
PVGS | N/A | 2020-02-09 | 2020-02-17 | 1900-01-07 04:59 | F | 0 | M | Controlled shutdown to Mode 5 due to failed RCP 1B third stage water seal.
Unit 3
NOTE 1: USE THE FOLLOWING OUTAGE CATEGORIES |  |  |  |  | NOTE 2: USE THE FOLLOWING UNIT SHUTDOWN CATEGORIES
| F = Forced Outage |  |  |  |  | AT = Automatic Trip |  | M = Manual Controlled Shutdown
| S = Scheduled Outage |  |  |  |  | MT = Manual Trip (Note F) |  | O = Other
* The letters in parentheses refer to additional notes by EPE. Refer to the last page of Schedule H-6.1a for further explanation.
For Downpowers, Maximum Power Level Permitted is calculated using Design Electric Rating.

## NOTES
EL PASO ELECTRIC COMPANY |  | SCHEDULE H-6.1a
2021 TEXAS RATE CASE FILING |  | PAGE 4 OF 4
SCHEDULE H-6.1a: NUCLEAR UNIT OUTAGE HISTORY
SPONSOR: DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
PALO VERDE GENERATING STATION
NOTES AND ACRONYMS TO SCHEDULE H-6.1a
El Paso Electric Notes: (All information is from the NRC Monthly Operating Report unless noted otherwise)
(A) | Minor reactor power reductions (less than or equal to 5%) required for routine planned maintenance and testing and
chemistry control are not displayed.
(B) | Outages that began before or continued after the Test Year are included.
(C) | Duration in hours is based on dates and times from the page entitled "Summary of Operating Experience For The Month."
A reduction in power outage is complete when the power level returns to the original power level before the reduction.
An outage due to a trip of the Main Turbine or Reactor is complete when the Main Turbine is synchronized to the grid.
(D) | Maximum Power Level Permitted - This was interpreted to mean the reliable power level permitted during the reduction.
(E) | No outage number available. Refers to power reductions such as those listed on the NRC report page entitled, "Summary
of Operating Experience for the Month" and not included on the page entitled "Unit Shutdowns and Power Reductions."
(F) | Manual Trip definition is a trip that is not automatic and not from a controlled shutdown.