## H-6.2a
EL PASO ELECTRIC COMPANY
2021 TEXAS RATE CASE FILING
SCHEDULE H-6.2a: FOSSIL UNIT FORCED OUTAGE HISTORY
SPONSOR: J KYLE OLSON
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
UNIT | DATE | DATE | OUTAGE
NAME | STARTED | COMPLETE | DURATION | REASON FOR OUTAGE
HOURS
Copper | 2020-07-02 14:27 | 2020-07-02 17:09 | 2.7 | Trip was induced by a loose wire on the proximity probe that signaled the Bentley Nevada to trip the unit
Copper | 2020-07-30 13:06 | 2020-07-30 14:36 | 1.5 | Tripped due to high bearing oil temps
Copper | 2020-08-05 12:48 | 2021-01-01 | 3563.2 | Unit tripped due to high vibrations. Significant compressor damage
Montana 1 | 2020-01-20 17:42 | 2020-01-20 17:56 | 0.23333 | SF- Tempering air fan not running
Montana 1 | 2020-03-20 06:54 | 2020-03-20 10:30 | 3.6 | SF- Solenoid valve FV-436 stuck In closed position.
Montana 1 | 2020-07-08 13:52 | 2020-07-08 14:35 | 0.71667 | DCS rebooted causing loss of control to water injection supply valve.
Montana 1 | 2020-09-10 13:00 | 2020-09-10 19:24 | 6.4 | Intercooler Tube Leak.
Montana 1 | 2020-09-16 12:36 | 2020-09-16 14:01 | 1.4167 | Tempering fan failed
Montana 1 | 2020-10-08 19:11 | 2020-10-09 10:07 | 14.9333 | Low pressure compressor variable bleed valve indicating gross position error.
Montana 1 | 2020-10-17 12:56 | 2020-10-17 15:40 | 2.7333 | SF- NOX water pumps not receiving run command from Mark VI. Performed update on turbine DCS
Montana 1 | 2020-10-26 06:30 | 2020-10-26 10:00 | 3.5 | Front supercore leg bearing inspection
Montana 1 | 2020-10-29 03:05 | 2020-10-29 09:30 | 6.4167 | Hydraulic starter oil tank indicating error on tank level.
Montana 2 | 2020-01-23 23:21 | 2020-01-24 12:00 | 12.65 | Tempering air fan faulted and shutdown.
Montana 2 | 2020-01-28 06:00 | 2020-01-28 15:29 | 9.4833 | SF- Hydraulic Pump 7025 faulted during start-up.
Montana 2 | 2020-04-28 10:12 | 2020-05-02 12:57 | 98.75 | Low pressure compressor inlet guide vain indicating position error.
Montana 2 | 2020-05-12 14:49 | 2020-05-12 17:25 | 2.6 | Indicating position fault on gas valve 2201.
Montana 2 | 2020-05-16 15:05 | 2020-05-16 18:00 | 2.9167 | Indicating position fault on gas valve 2201.
Montana 2 | 2020-05-16 20:01 | 2020-05-17 10:48 | 14.7833 | Replaced gas valve 2201
Montana 2 | 2020-07-02 11:26 | 2020-07-02 12:40 | 1.2333 | SF- Tempering air fan failed to start.
Montana 2 | 2020-07-08 13:52 | 2020-07-08 14:35 | 0.71667 | DCS rebooted causing loss of control to water injection supply valve.
Montana 2 | 2020-10-12 12:40 | 2020-10-12 13:24 | 0.73333 | Hydraulic starter failed to engage during cooldown sequence.
Montana 2 | 2020-10-15 22:56 | 2020-10-16 12:15 | 13.3167 | Supercore failed to reach speed.
Montana 2 | 2020-10-21 03:25 | 2020-10-21 14:00 | 10.5833 | Hydraulic starter failed to engage during cooldown sequence.
Montana 2 | 2020-10-23 07:50 | 2020-10-24 13:30 | 29.6667 | Replaced hydraulic starter
Montana 2 | 2020-10-27 08:30 | 2020-10-27 10:39 | 2.15 | Installing Bleed Heat Piping.
Montana 2 | 2020-10-30 18:00 | 2020-10-31 14:35 | 20.5833 | SF- Troubleshooting variable stator vain position error.
Montana 2 | 2020-11-25 17:33 | 2020-11-26 02:59 | 9.4333 | Variable stator vain output and feedback not matching
Montana 3 | 2020-01-27 14:45 | 2020-01-27 16:08 | 1.3833 | Tempering air fan not receiving start command.
Montana 3 | 2020-04-21 00:11 | 2020-04-21 11:51 | 11.6667 | Vibrations drive end of generator
Montana 3 | 2020-04-22 13:41 | 2020-04-24 18:00 | 52.3167 | Low pressure compressor high vibrations J2 bearing
Montana 3 | 2020-07-20 10:29 | 2020-07-21 19:20 | 32.85 | SF-High vibrations on low pressure compressor.
Montana 3 | 2020-08-06 12:35 | 2020-08-07 12:08 | 23.55 | J3 and J4 bearing vibration issues
Montana 3 | 2020-08-07 18:41 | 2020-08-08 10:00 | 15.3167 | J3 and J4 bearing vibration issues
Montana 3 | 2020-08-31 09:00 | 2020-08-31 10:59 | 1.9833 | Repair LP Recoup Line
Montana 3 | 2020-09-02 20:25 | 2020-09-02 20:54 | 0.48333 | Replacing PX36 Acoustic Sensor.
Montana 3 | 2020-09-03 23:34 | 2020-09-04 14:59 | 15.4167 | High Vibration J3 and J4
Montana 3 | 2020-09-25 10:46 | 2020-09-27 23:59 | 61.2167 | High Vibration J3 and J4
Montana 4 | 2020-01-08 08:21 | 2020-01-08 10:00 | 1.65 | Loss of J3 pressurization air.
Montana 4 | 2020-01-13 20:12 | 2020-01-14 03:49 | 7.6167 | E-Stop Circuit Open
Montana 4 | 2020-03-20 04:12 | 2020-03-20 05:33 | 1.35 | 125VDC Battery Charger Loss of power alarm
Montana 4 | 2020-06-04 22:48 | 2020-06-05 10:20 | 11.5333 | Speed Sensor loss of signal.
Montana 4 | 2020-07-12 18:37 | 2020-07-12 21:20 | 2.7167 | CEMS stack sample pumps not operating correctly. Caused by misalignment of stacked sample pumps.
Montana 4 | 2020-08-20 11:41 | 2020-08-20 11:50 | 0.15 | SF- Hydraulic starter valve left in closed position. Lock out tag out not performed correctly.
Montana 4 | 2020-09-22 12:34 | 2020-09-22 13:56 | 1.3667 | SF- Low pressure compressor variable bleed valve #1 indicating coil fault.
Montana 4 | 2020-09-24 08:00 | 2020-09-24 09:00 | 1 | Replacing supercore turbine leg west side.
Montana 4 | 2020-10-17 13:50 | 2020-10-17 14:40 | 0.83333 | SF- Troubleshooting IGV Gross Position error alarm
Montana 4 | 2020-10-31 15:00 | 2020-10-31 17:09 | 2.15 | Replaced liquid fuel drain valve SOV 2009
Montana 4 | 2020-11-28 15:11 | 2020-11-28 16:44 | 1.55 | Generator winding temperature phase 3 loss of signal.
Newman 1 | 2020-07-16 20:45 | 2020-07-17 16:00 | 19.25 | Tripped due to AVR tripping on high temp.
Newman 1 | 2020-07-27 | 2020-08-01 | 120 | Unit removed from service to Repair boiler tube leak
Newman 1 | 2020-08-01 | 2020-08-26 13:50 | 613.8333 | Tripped due to Field fault. In addition, generator H2 seal repair
Newman 1 | 2020-11-04 06:45 | 2020-11-05 09:53 | 27.1333 | Loss of Instrument Air
Newman 1 | 2020-11-05 09:56 | 2020-11-05 11:45 | 1.8167 | Low Gas Pressure
Newman 1 | 2020-11-05 12:19 | 2020-11-05 13:41 | 1.3667 | Low Gas Pressure
Newman 1 | 2020-11-05 14:10 | 2020-11-06 00:54 | 10.7333 | Low Gas Pressure
Newman 1 | 2020-11-28 20:49 | 2020-11-29 14:34 | 17.75 | SF- Turbine Bearing Vibration High (bearing #3), one failed start
Newman 1 | 2020-12-03 06:29 | 2020-12-03 12:27 | 5.9667 | Loss of gas supply. East Fuel Regulating valve stuck in position due to failed valve positioner
Newman 1 | 2020-12-03 12:31 | 2020-12-03 13:15 | 0.73333 | Failure of Gas Burner #9, fuse
Newman 2 | 2020-11-04 06:37 | 2020-11-05 10:15 | 27.6333 | Loss of Instrument Air
Newman 2 | 2020-11-05 12:09 | 2020-11-05 13:06 | 0.95 | Loss of Vacuum
Newman 3 | 2020-05-02 16:46 | 2020-05-06 10:04 | 89.3 | Economizer tube leaks
Newman 3 | 2020-05-06 10:04 | 2020-05-06 12:36 | 2.5333 | Unit tripped on high drum level shortly after syncing. Drum level was not observed or corrected at this point in start up
Newman 3 | 2020-05-06 13:21 | 2020-05-06 14:23 | 1.0333 | Unit tripped due to high drum level
Newman 3 | 2020-05-26 21:12 | 2020-05-26 22:18 | 1.1 | Unit tripped on high gas pressure
Newman 3 | 2020-06-11 07:03 | 2020-06-13 02:00 | 42.95 | Unit tripped on 61G1T relay. Neutral overvoltage.
Newman 3 | 2020-06-13 17:32 | 2020-06-18 16:11 | 118.65 | RH Tube leak
Newman 3 | 2020-07-10 07:55 | 2020-07-12 06:43 | 46.8 | Boiler Tube Leak - Economizer
Newman 3 | 2020-08-07 02:48 | 2020-08-07 14:35 | 11.7833 | EH system developed oil leak causing unit trip
Newman 3 | 2020-08-13 16:46 | 2020-08-13 18:22 | 1.6 | Unit tripped due high furnace pressure caused by a tube leak
Newman 3 | 2020-09-11 12:12 | 2020-09-15 05:20 | 89.1333 | Unit tripped due to economizer tube leak.
Newman 3 | 2020-09-15 05:28 | 2020-09-15 05:37 | 0.15 | Upon synchronizing, the generator breaker opened with no relay operation. Brought unit back to synchronizing conditions and closed breaker.
Newman 3 | 2020-09-16 00:32 | 2020-09-16 23:54 | 23.3667 | Tripped on High gas pressure due to heavy load swings caused by the EH system. EH pressure fluctuation caused turbine to go from 50 MWs to 2 MWs.
Newman 3 | 2020-09-21 13:22 | 2020-09-25 16:28 | 99.1 | Unit removed from service due to Contaminated (water) Turbine Lube Oil
Newman 3 | 2020-09-26 13:42 | 2020-09-30 08:44 | 91.0333 | Unit removed from service to repair left reheat(intercept) turbine valve. Would not open
Newman 3 | 2020-09-30 09:39 | 2020-09-30 14:30 | 4.85 | Unit tripped due to turbine valve control fluctuation (Servo's cleaned)
Newman 3 | 2020-09-30 21:00 | 2020-09-30 21:46 | 0.76667 | Unit tripped due to issues with control valves fluctuating from 14% - 40% Open
Newman 3 | 2020-10-01 09:04 | 2020-10-02 20:50 | 35.7667 | Unit removed from service due to turbine control valve issues
Newman 3 | 2020-10-05 16:31 | 2020-10-09 23:48 | 103.2833 | Unit removed from service due to lube oil contamination. EH fluid in turbine lube oil
Newman 3 | 2020-11-04 06:44 | 2020-11-04 10:56 | 4.2 | Loss of Instrument Air
Newman 3 | 2020-11-27 06:27 | 2020-12-01 00:12 | 89.75 | Tripped due to Economizer Tube Leak
Newman 3 | 2020-12-05 18:40 | 2020-12-09 17:01 | 94.35 | Tripped due to Economizer Tube Leak
Newman 3 | 2020-12-09 18:59 | 2020-12-09 20:57 | 1.9667 | Tripped due to Left Reheat Stop Valve Position Error
Newman 3 | 2020-12-15 04:33 | 2020-12-15 11:03 | 6.5 | Loss of all Gas Burners
Newman 4-GT1 | 2020-01-27 14:26 | 2020-01-27 17:50 | 3.4 | Loss of Circulating water Pump
Newman 4-GT1 | 2020-02-03 18:49 | 2020-03-07 | 773.1833 | Unit trip due to Generator 86G relay trip
Newman 4-GT1 | 2020-04-17 | 2020-05-01 16:48 | 352.8 | OMC- Parts Delayed due to COVID 19 Out of managements control*
Newman 4-GT1 | 2020-05-01 18:54 | 2020-05-06 23:01 | 124.1167 | GT Compressor Joint Leak
Newman 4-GT1 | 2020-05-17 09:26 | 2020-05-17 16:46 | 7.3333 | High HP drum level trip when condenser available was enabled and main stm bypass opened 18%
Newman 4-GT1 | 2020-07-27 22:12 | 2020-07-28 07:50 | 9.6333 | Trip due to unknown reasons
Newman 4-GT1 | 2020-08-24 19:17 | 2020-08-24 20:03 | 0.76667 | Unit tripped on low lube oil pressure during cascade testing.
Newman 4-GT2 | 2020-01-27 14:26 | 2020-01-27 19:10 | 4.7333 | Loss of Circulating water Pump
Newman 4-GT2 | 2020-05-01 | 2020-06-05 14:21 | 854.35 | OMC- Turbine Major - Parts Delay due to COVID-19. Out of managements control*
Newman 4-GT2 | 2020-06-06 17:34 | 2020-06-06 21:57 | 4.3833 | When Standby BF pump was shut down the gas turbine tripped due to loss of BF pump. The logic in the DCS was reviewed and was changed to allow the shut down of the stand by BF pump when main BF pump is in operation
Newman 4-GT2 | 2020-08-11 06:54 | 2020-08-11 08:13 | 1.3167 | Unit tripped due to high gas pressure
Newman 4-GT2 | 2020-08-17 04:06 | 2020-08-17 05:07 | 1.0167 | Unit tripped when swapping turbine lube oil pumps. Second pump did not automatically start due to pump being in manual mode.
Newman 4-GT2 | 2020-08-18 11:18 | 2020-08-18 20:51 | 9.55 | Unit tripped on high exciter vibrations.
Newman 4-GT2 | 2020-09-08 08:48 | 2020-09-08 09:52 | 1.0667 | Unit tripped Due to High vibrations on Turbine Exhaust Bearing
Newman 4-ST | 2020-01-27 14:26 | 2020-01-27 20:30 | 6.0667 | Loss of Circulating water Pump
Newman 4-ST | 2020-02-18 23:19 | 2020-03-07 | 408.6833 | Due to GT1 FO and GT2 Summer Prep.
Newman 4-ST | 2020-04-17 | 2020-05-01 16:48 | 352.8 | OMC- Summer Prep due to GT1 Parts COVID-19 Delay Out of managements control*
Newman 4-ST | 2020-05-01 18:54 | 2020-05-06 23:01 | 124.1167 | GT Compressor Joint Leak
Newman 4-ST | 2020-05-17 09:26 | 2020-05-17 16:46 | 7.3333 | High HP drum level trip when condenser available was enabled and main stm bypass opened 18%
Newman 4-ST | 2020-05-21 08:56 | 2020-05-21 09:20 | 0.4 | Unit Trip due to speed pickup sensor DCS card failure
Newman 4-ST | 2020-05-26 11:15 | 2020-05-26 12:25 | 1.1667 | Steamer tripped due to low EH pressure alarm
Newman 4-ST | 2020-06-05 11:35 | 2020-06-05 12:02 | 0.45 | Unit tripped due to High HP Drum Level - HP Circ pump was not turned on.
Newman 4-ST | 2020-06-23 09:05 | 2020-06-23 09:22 | 0.28333 | Tripped when performing switching order from SysOps
Newman 4-ST | 2020-06-29 16:38 | 2020-06-29 17:25 | 0.78333 | Unit tripped due to High HP Drum Level
Newman 4-ST | 2020-07-27 22:12 | 2020-07-27 22:46 | 0.56667 | Unit tripped due to Loss of speed pick up.
Newman 4-ST | 2020-08-06 22:35 | 2020-08-07 11:47 | 13.2 | Tripped when GT2 electrical power at transformer surged and smoked. Speed sensor bad preventing immediate restart
Newman 5-GT3 | 2020-02-29 | 2020-03-02 13:41 | 61.6833 | SF- Due to Torque Converter not operating properly
Newman 5-GT3 | 2020-03-23 13:43 | 2020-03-23 23:51 | 10.1333 | Tripped while swapping scanner blowers, also "B" scanner blower is bad
Newman 5-GT3 | 2020-03-24 09:22 | 2020-03-24 16:43 | 7.35 | Tripped due to condenser low level- a direct result from the trip of U5 STM
Newman 5-GT3 | 2020-06-10 12:27 | 2020-06-10 13:43 | 1.2667 | GT tripped on compressor bleed valve trouble due to lose wire
Newman 5-GT3 | 2020-08-13 13:51 | 2020-08-13 15:46 | 1.9167 | OMC- Unit tripped due to Substation event - Out of Management Control
Newman 5-GT3 | 2020-08-13 17:47 | 2020-08-13 22:05 | 4.3 | Unit tripped due HRSG Drum Levels
Newman 5-GT3 | 2020-11-30 14:34 | 2020-11-30 21:23 | 6.8167 | Induced DC voltage to Switchyard RTU, Resulting in Open Ended Generator Circuit
Newman 5-GT4 | 2020-03-23 13:50 | 2020-03-23 15:08 | 1.3 | Tripped while swapping scanner blowers, also "B" scanner blower is bad
Newman 5-GT4 | 2020-03-24 09:22 | 2020-03-24 11:19 | 1.95 | Tripped due to condenser low level- a direct result from the trip of U5 STM
Newman 5-GT4 | 2020-05-02 01:58 | 2020-05-02 02:58 | 1 | GT4 tripped on low LP level
Newman 5-GT4 | 2020-08-13 13:51 | 2020-08-13 15:39 | 1.8 | OMC- Unit tripped due to Substation event - Out of Management Control
Newman 5-GT4 | 2020-11-30 14:44 | 2020-11-30 19:15 | 4.5167 | Induced DC voltage to Switchyard RTU, Resulting in Loss of Instrument Air
Newman 5-ST | 2020-01-18 09:09 | 2020-01-18 12:48 | 3.65 | Tripped due to high drum level in HRSG4 HP Drum
Newman 5-ST | 2020-01-19 00:06 | 2020-01-19 02:09 | 2.05 | Life shortening condition due to hp seal stm supply not swapping to crh seal steam supply.
Newman 5-ST | 2020-03-02 14:58 | 2020-03-02 16:53 | 1.9167 | Tripped on drum high drum level.
Newman 5-ST | 2020-03-23 13:50 | 2020-03-23 19:40 | 5.8333 | Result of GT3/GT4 Forced Outage
Newman 5-ST | 2020-03-24 08:55 | 2020-03-24 12:33 | 3.6333 | High IP drum level which tripped the steam turbine
Newman 5-ST | 2020-04-24 23:12 | 2020-04-25 00:13 | 1.0167 | LP exhaust pressure high. Further troubleshooting to determine cause.
Newman 5-ST | 2020-05-02 01:58 | 2020-05-02 02:58 | 1 | Due to GT4 trip on low LP level
Newman 5-ST | 2020-08-13 13:51 | 2020-08-13 21:31 | 7.6667 | OMC- Unit tripped due to Substation event - Out of Management Control
Newman 5-ST | 2020-11-30 14:44 | 2020-12-01 04:56 | 14.2 | Induced DC voltage to Switchyard RTU, Resulting in Open Ended Generator Circuit
Rio Grande 7 | 2020-01-01 | 2020-05-13 04:01 | 3196.0167 | Unit tripped on relay 86G
Rio Grande 7 | 2020-05-13 04:01 | 2020-05-22 04:01 | 216 | OMC- Parts Delay**
Rio Grande 7 | 2020-06-12 20:05 | 2020-06-12 22:47 | 2.7 | OMC- Thunderstorm-tripped on 86G relay
Rio Grande 7 | 2020-06-25 15:20 | 2020-06-26 11:26 | 20.1 | Due to Burner #3 Flamed Out causing High Gas Burner Header Pressure
Rio Grande 7 | 2020-07-05 11:26 | 2020-07-07 07:01 | 43.5833 | Due to Boiler Tube Leak
Rio Grande 7 | 2020-07-14 20:28 | 2020-08-01 18:31 | 430.05 | OMC- Due to Generator Stator Ground (Cracked busing on T-5)
Rio Grande 7 | 2020-08-03 23:39 | 2020-08-04 18:14 | 18.5833 | To repair #1 Burner Gas valve which failed to close and troubleshoot AVR
Rio Grande 7 | 2020-08-04 18:15 | 2020-08-04 21:16 | 3.0167 | Due to 86G relay on generator
Rio Grande 8 | 2020-03-11 00:33 | 2020-03-11 09:52 | 9.3167 | Master Fuel Trip relay failure
Rio Grande 8 | 2020-03-13 02:04 | 2020-03-17 11:11 | 105.1167 | Due to Main Fuel Trip #1 caused by a faulty wire
Rio Grande 8 | 2020-05-29 17:01 | 2020-06-30 15:47 | 766.7667 | Hydrogen seals damage, loss of H2
Rio Grande 8 | 2020-07-02 10:41 | 2020-07-02 12:01 | 1.3333 | Due to loss of under voltage trip circuit
Rio Grande 8 | 2020-07-02 12:35 | 2020-07-02 14:27 | 1.8667 | Due to Gas Valve Transition
Rio Grande 8 | 2020-07-16 17:18 | 2020-07-16 21:56 | 4.6333 | Due to Hot Spot on Boiler caused a short on wire to first stage pressure transmitter
Rio Grande 8 | 2020-07-17 14:00 | 2020-07-23 00:45 | 130.75 | Due to Hot Spot on Boiler caused a short on wire to first stage pressure transmitter
Rio Grande 8 | 2020-07-23 01:31 | 2020-07-23 02:45 | 1.2333 | Due to burner issues
Rio Grande 8 | 2020-08-03 17:53 | 2020-08-03 19:48 | 1.9167 | Drum level transmitter malfunctioned
Rio Grande 8 | 2020-09-12 16:48 | 2020-09-12 19:30 | 2.7 | Due to High Pressure Back Pressure
Rio Grande 8 | 2020-10-09 22:57 | 2020-10-12 05:47 | 54.8333 | Due to Tube Leaks
Rio Grande 8 | 2020-12-04 13:10 | 2020-12-05 22:33 | 33.3833 | Due to water chemistry excursion
Rio Grande 9 | 2020-05-11 07:39 | 2020-05-11 08:03 | 0.4 | Due to faulty sequencer
Rio Grande 9 | 2020-05-24 13:23 | 2020-05-24 17:47 | 4.4 | Due to NOX pumps shutting off and not restarting
Rio Grande 9 | 2020-07-20 08:55 | 2020-07-20 09:40 | 0.75 | SF- on Sync Switch Sequence
Notes:
SF= Start-up Failure
OMC= Outside of Management's Control
*Per GADS instructions, indicates a portion of a planned outage that was reported as a Forced Outage using an Outside of Management's control cause code due to the COVID-19 pandemic.
**Per GADS instructions, indicates a portion of a forced outage that was reported as a Forced Outage using an Outside of Management's control cause code due to the COVID-19 pandemic.