## H-6.2b
EL PASO ELECTRIC COMPANY
2021 TEXAS RATE CASE FILING
SCHEDULE H-6.2b: FOSSIL UNIT PLANNED OUTAGE DATA
SPONSOR: J KYLE OLSON
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
| SCHEDULED | SCHEDULED | SCHEDULED | ACTUAL | ACTUAL | ACTUAL
UNIT | START | END | LENGTH OF | START | END | LENGTH OF
NAME | DATE | DATE | OUTAGE | DATE | DATE | OUTAGE | REASON FOR OUTAGE
|  |  | (Days) |  |  | (Days)
Copper | 2020-04-18 | 2020-05-01 | 14 | 2020-04-18 | 2020-05-01 | 13.3 | Summer Prep
Montana 1 |  |  |  | 2020-01-06 07:00 | 2020-01-07 14:50 | 1.3 | Blackstart Testing
Montana 1 |  |  |  | 2020-02-24 07:00 | 2020-02-24 16:24 | 0.39167 | water wash
Montana 1 | 2020-02-03 | 2020-02-23 | 21 | 2020-02-25 | 2020-03-14 | 18.5 | Summer Prep
Montana 1 |  |  |  | 2020-03-14 | 2020-03-15 | 0.6 | Summer Prep
Montana 1 |  |  |  | 2020-04-25 06:30 | 2020-04-25 12:40 | 0.25694 | Replaced synthetic lube oil scavenging pump
Montana 1 |  |  |  | 2020-10-30 07:00 | 2020-10-30 09:00 | 0.083333 | Turbine exhaust duct inspection.
Montana 1 |  |  |  | 2020-11-06 08:00 | 2020-11-06 14:25 | 0.26736 | Intercooler tube leak repair.
Montana 1 |  |  |  | 2020-11-16 02:00 | 2020-11-19 09:12 | 3.3 | Black Start Testing
Montana 1 |  |  |  | 2020-12-17 06:00 | 2020-12-20 20:12 | 3.5917 | Main gas line section replaced
Montana 2 |  |  |  | 2020-02-22 15:00 | 2020-02-23 11:55 | 0.87153 | Water Wash
Montana 2 | 2020-02-15 | 2020-03-06 | 21 | 2020-03-07 | 2020-03-25 | 18.3 | Summer Prep
Montana 2 |  |  |  | 2020-07-05 08:00 | 2020-07-05 10:15 | 0.09375 | Replaced hydraulic starter pump.
Montana 2 |  |  |  | 2020-11-13 08:00 | 2020-11-13 11:30 | 0.14583 | Replaced anti- ice valve.
Montana 2 |  |  |  | 2020-11-16 02:00 | 2020-11-19 11:38 | 3.4014 | Black start testing
Montana 2 |  |  |  | 2020-12-17 06:00 | 2020-12-20 20:30 | 3.6042 | Main gas line section replaced | PAGE 1 OF 4 | SCHEDULE H-6.2b
Montana 3 |  |  |  | 2020-01-13 07:00 | 2020-01-13 11:43 | 0.19653 | Balancing Generator
Montana 3 |  |  |  | 2020-01-13 12:39 | 2020-01-13 13:58 | 0.054861 | Balancing Generator
Montana 3 |  |  |  | 2020-01-13 15:37 | 2020-01-13 17:58 | 0.097917 | Balancing Generator
Montana 3 |  |  |  | 2020-01-13 18:35 | 2020-01-13 19:55 | 0.055556 | Balancing Generator
Montana 3 |  |  |  | 2020-01-13 23:47 | 2020-01-14 10:50 | 0.46042 | Balancing Generator
Montana 3 |  |  |  | 2020-01-14 11:48 | 2020-01-14 17:38 | 0.24306 | Balancing Generator
Montana 3 |  |  |  | 2020-01-14 17:56 | 2020-01-15 09:47 | 0.66042 | Balancing Generator
Montana 3 |  |  |  | 2020-01-15 11:34 | 2020-01-15 18:44 | 0.29861 | Balancing Generator
Montana 3 |  |  |  | 2020-01-15 19:28 | 2020-01-16 08:45 | 0.55347 | Balancing Generator
Montana 3 |  |  |  | 2020-01-16 10:06 | 2020-01-16 12:06 | 0.083333 | Balancing Generator
Montana 3 |  |  |  | 2020-01-16 14:47 | 2020-01-16 17:45 | 0.12361 | Balancing Generator
Montana 3 |  |  |  | 2020-01-16 21:26 | 2020-01-16 23:52 | 0.10139 | Balancing Generator
Montana 3 |  |  |  | 2020-01-17 07:21 | 2020-01-17 16:10 | 0.36736 | Balancing Generator
Montana 3 |  |  |  | 2020-01-17 18:08 | 2020-01-17 19:00 | 0.036111 | Balancing Generator
Montana 3 |  |  |  | 2020-02-22 05:00 | 2020-02-22 16:20 | 0.47222 | water wash
Montana 3 | 2020-03-09 | 2020-03-29 | 21 | 2020-04-06 | 2020-04-16 | 10.4 | Summer Prep
Montana 3 |  |  |  | 2020-04-16 | 2020-04-18 | 2.1 | Summer Prep
Montana 3 |  |  |  | 2020-06-04 06:00 | 2020-06-04 09:08 | 0.13056 | Replacing turbine leg strut bearing supercore west side.
Montana 3 |  |  |  | 2020-06-12 06:00 | 2020-06-12 12:30 | 0.27083 | Replaced power turbine leg strut bearing west side.
Montana 3 |  |  |  | 2020-07-25 06:00 | 2020-07-25 10:20 | 0.18056 | Balancing Gen drive end
Montana 3 |  |  |  | 2020-07-25 15:00 | 2020-07-25 16:55 | 0.079861 | Balancing Gen drive end
Montana 3 |  |  |  | 2020-07-26 11:44 | 2020-07-26 15:00 | 0.13611 | Balancing Gen drive end
Montana 3 |  |  |  | 2020-09-28 | 2021-01-01 | 95 | Generator Rotor Refurbishment to reduce vibrations on J3 J4 and Generator. | PAGE 2 OF 4 | SCHEDULE H-6.2b
Montana 4 |  |  |  | 2020-02-23 10:30 | 2020-02-23 16:53 | 0.26597 | Water Wash
Montana 4 | 2020-03-21 | 2020-04-10 | 21 | 2020-04-11 | 2020-04-24 | 13 | Summer Prep
Montana 4 |  |  |  | 2020-05-22 06:00 | 2020-05-22 10:45 | 0.19792 | Replace supercore leg strut bearing west side.
Montana 4 |  |  |  | 2020-07-27 06:00 | 2020-07-27 14:00 | 0.33333 | Replace supercore leg strut bearing west side. Verified alignment on turbine and generator.
Montana 4 |  |  |  | 2020-08-28 11:30 | 2020-08-28 14:04 | 0.10694 | Maintenance outage to repair VSV actuator
Montana 4 |  |  |  | 2020-09-28 06:00 | 2020-10-04 10:43 | 6.1965 | Performed an alignment of the Turbine and Generator.
Montana 4 |  |  |  | 2020-11-16 02:00 | 2020-11-19 10:46 | 3.3653 | Black Start Testing
Montana 4 |  |  |  | 2020-12-17 06:00 | 2020-12-20 20:30 | 3.6042 | Main gas line section replaced
Newman 1 | 2020-01-04 | 2020-01-24 | 21 | 2020-01-03 | 2020-01-25 | 22 | Summer Prep
Newman 1 |  |  |  | 2020-02-29 11:31 | 2020-03-09 19:00 | 9.3118 | Boiler Roof Tube and Secondary Superheat Leaks
Newman 1 |  |  |  | 2020-07-17 16:00 | 2020-07-27 | 9.3333 | Loss of field in generator due to field fault, Generator H2 seal repair
Newman 1 |  |  |  | 2020-10-18 21:15 | 2020-11-01 04:03 | 13.2833 | Maintenance outage to repair boiler water wall tube leak
Newman 2 | 2020-01-11 | 2020-01-31 | 21 | 2020-01-06 | 2020-02-02 | 27.1 | Summer Prep
Newman 3 | 2020-01-04 | 2020-02-07 | 35 | 2020-01-03 | 2020-02-16 | 44.3 | Summer Prep
Newman 3 |  |  |  | 2020-08-14 21:41 | 2020-08-18 20:33 | 3.9528 | Unit removed from service to repair boiler tube leak
Newman 3 |  |  |  | 2020-12-28 07:00 | 2021-01-01 | 3.7083 | Boiler tube leak repairs
Newman 4-GT1 | 2020-03-07 | 2020-04-17 | 42 | 2020-03-07 | 2020-04-17 | 41 | Turbine Hot Gas and Summer Prep
Newman 4-GT1 |  |  |  | 2020-05-14 | 2020-05-17 | 3.4 | Outage to repair oil leak on exciter\starting package
Newman 4-GT1 |  |  |  | 2020-06-26 21:05 | 2020-06-27 13:38 | 0.68958 | Maint Outage to install balance shot and cooling shroud on exciter
Newman 4-GT1 |  |  |  | 2020-07-02 07:37 | 2020-07-02 11:00 | 0.14097 | Planned outage to install balance shot
Newman 4-GT1 |  |  |  | 2020-07-25 06:56 | 2020-07-25 09:25 | 0.10347 | Removed from service to collect vibration data
Newman 4-GT1 |  |  |  | 2020-10-02 21:28 | 2021-01-01 | 90.1056 | DCS Upgrade
Newman 4-GT2 | 2020-02-15 | 2020-04-17 | 63 | 2020-02-18 | 2020-05-01 | 102 | Turbine Major and Summer Prep
Newman 4-GT2 |  |  |  | 2020-06-27 19:17 | 2020-06-29 17:29 | 1.925 | Maint outage to repair DA make up valve and nozzles
Newman 4-GT2 |  |  |  | 2020-08-01 01:24 | 2020-08-01 14:05 | 0.52847 | Unit removed from service to replace BF pump packing
Newman 4-GT2 |  |  |  | 2020-08-05 08:12 | 2020-08-08 20:41 | 3.5201 | Unit removed from service to repair oil leak in tear drop that is causing fires.
Newman 4-GT2 |  |  |  | 2020-10-02 21:36 | 2021-01-01 | 90.1 | DCS Upgrade | PAGE 3 OF 4 | SCHEDULE H-6.2b
Newman 4-ST | 2020-03-07 | 2020-04-17 | 42 | 2020-03-07 | 2020-04-17 | 41 | Summer Prep
Newman 4-ST |  |  |  | 2020-05-14 00:41 | 2020-05-17 09:26 | 3.3646 | Outage to repair oil leak on exciter\starting package
Newman 4-ST |  |  |  | 2020-10-02 21:10 | 2021-01-01 | 90.1181 | DCS Upgrade and Valve Inspection
Newman 5-GT3 | 2020-02-08 | 2020-02-28 | 21 | 2020-02-07 | 2020-02-29 | 21.6 | Summer Prep and Hot Gas Inspection
Newman 5-GT3 |  |  |  | 2020-04-25 21:54 | 2020-04-27 21:38 | 1.9889 | Maintenance Outage to repair attemperator and relief valves
Newman 5-GT3 |  |  |  | 2020-05-02 01:51 | 2020-05-05 01:11 | 2.9722 | Maintenance outage to repair flange steam leak and attemperator
Newman 5-GT4 |  |  |  | 2020-01-18 08:56 | 2020-01-18 21:22 | 0.5 | Repairs to Phosphate Line leaking at HP Drum
Newman 5-GT4 | 2020-02-01 | 2020-02-28 | 28 | 2020-01-31 | 2020-02-27 | 27 | Summer Prep
Newman 5-ST | 2020-02-08 | 2020-02-28 | 21 | 2020-02-07 | 2020-02-29 | 22.1 | Summer Prep
Rio Grande 7 |  |  |  | 2020-12-14 07:00 | 2020-12-18 10:13 | 4.134 | To work on Boiler Tube Leaks, DA Level Column Transmitter and Condenser
Rio Grande 7 | 2020-02-24 | 2020-03-15 | 21 | (A) |  |  | Summer Prep
Rio Grande 8 | 2020-01-11 | 2020-02-14 | 35 | 2020-01-11 | 2020-02-19 | 39.6 | Boiler Cleaning and Summer Prep
Rio Grande 8 |  |  |  | 2020-04-15 07:50 | 2020-04-17 00:09 | 1.6799 | To repair Low Pressure Heater issue
Rio Grande 8 |  |  |  | 2020-05-15 23:08 | 2020-05-16 17:30 | 0.76528 | To change out MOOG valve for the left side governor valve on turbine
Rio Grande 8 |  |  |  | 2020-08-22 02:01 | 2020-08-24 11:24 | 2.391 | To repair Boiler Hot Spots
Rio Grande 8 |  |  |  | 2020-10-29 22:15 | 2020-11-08 01:19 | 9.1278 | To perform Boiler Inspection by Babcock & Wilcox
Rio Grande 9 |  |  |  | 2020-02-26 08:00 | 2020-02-27 15:00 | 1.2917 | To replace Generator Filters
Rio Grande 9 | 2020-04-11 | 2020-05-01 | 21 | 2020-03-25 | 2020-04-08 | 14 | Summer Prep
Rio Grande 9 |  |  |  | 2020-04-17 08:00 | 2020-04-23 13:10 | 6.2153 | To perform Water Wash and Generator Testing
Rio Grande 9 |  |  |  | 2020-05-19 20:26 | 2020-05-21 09:00 | 1.5236 | To replace Fuel Nozzle
Rio Grande 9 |  |  |  | 2020-05-22 14:20 | 2020-05-22 15:58 | 0.068056 | To input water mapping and ammonia data. | PAGE 4 OF 4 | SCHEDULE H-6.2b
Rio Grande 9 |  |  |  | 2020-06-15 20:57 | 2020-06-16 11:13 | 0.59444 | Due to Kinder-Morgan requesting outage to allow for installation of new pipe.
Rio Grande 9 |  |  |  | 2020-07-19 22:16 | 2020-07-20 08:55 | 0.44375 | To perform Borescope Inspections
Rio Grande 9 |  |  |  | 2020-07-23 20:54 | 2020-07-24 11:32 | 0.60972 | Rescheduled Borescope Inspection due to Vendor not available 7/19/20.
Rio Grande 9 |  |  |  | 2020-08-28 21:54 | 2020-08-31 17:38 | 2.8222 | To troubleshoot loss of MW and Water Wash.
Rio Grande 9 |  |  |  | 2020-09-14 07:00 | 2021-01-01 | 108.7083 | To replace lifting hoses on the J3 oil lines.
Note: Schedule reflects a combination of planned and maintenance outages.
(A) Summer Prep outage was completed during the generator rewind forced outage