## RGD 6
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 1 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
RIO GRANDE UNIT 6
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | Westinghouse Electric Corporation
2. TURBINE DESCRIPTION | 44,000 kW, Tandem Compound 3600 rpm Double Flow
3. INLET TEMPERATURES / PRESSURES
THROTTLE PRESSURE (psig) | 850 psig
SUPERHEAT TEMPERATURE | 900 F
REHEAT TEMPERATURE | N/A
4. NUMBER OF FEEDWATER HEATERS | 5
5. LAST ROW OF BLADING SIZE / RPMs | N/A / 3,600 RPM
6. GENERATOR MANUFACTURER | Westinghouse Electric Corporation
7. NAMEPLATE RATINGS | 58,882 KVA 0.85 pF
8. NOMINAL GROSS MW OUTPUT | 50 MW
9. TYPE OF COOLING | Hydrogen
10. TYPE OF EXCITATION | Shaft Driven Exciter
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | N/A
3. MW DERATING - ALTER FUEL USE | N/A
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | Babcock & Wilcox Company
6. TYPE OF BOILER | 2 Drum Stirling
7. TYPE OF FUEL FIRING | Front Fired
8. DESCRIPTION OF BURNER LAYOUT | Three Rows of Three
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 20.2 NMAC: .1,.7,.33 ,.61, .70, .71,.73,.74,.84; 40 CFR 50, 72,73,75,77
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | N/A
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | Off Stoichiometric Firing/BOOS
8. CURRENT LEVEL OF PARTICULATES | 0.0014 lb/MMBTU Test Data; 5.0 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | 0.0006 lbs. SO2/MMBTU AP-42
10. CURRENT LEVEL OF NOx | 0.188 lbs. NOx/MMBTU CEMS Data; 183 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | N/A
14. APPLICABLE WATER POLLUTION REG | EPA NPDES 40 CFR 122
15. APPLICABLE WASTE DISPOSAL REG | EPA RCRA 40 CFR 260-265
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Cooling Tower
2. MANUFACTURER OF COOLING WATER SYS | Fluor Products Company
3. PEAK MW LOAD OF COOLING WATER SYS | 0.954 Mw
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Two No. 4 CHTB-7 Stage Barrel Type Constant Speed Motor Driven
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Ingersoll-Rand Company
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | 0.6714 Mw
7. DESCRIPTION OF COMBUSTION AIR SYS | One Motor Driven Constant Speed Forced Draft Fan
8. MANUFACTURER OF COMBUSTION AIR SYS | Westinghouse Electric Corporation
9. PEAK MW LOAD OF COMBUSTION AIR SYS | 0.5968 Mw
10. DESCRIPTION OF AIR PREHEATER | Ljungstrom Regenerative Type Horizontal Shaft Air Preheater
11. MANUFACTURER OF AIR PREHEATER | The Air Preheater Corporation
12. PEAK MW LOAD OF AIR PREHEATER | 0.00559 Mw
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## RGD 7
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 2 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
RIO GRANDE UNIT 7
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric Company
2. TURBINE DESCRIPTION | 44,000 kW
3. INLET TEMPERATURES / PRESSURES
THROTTLE PRESSURE (psig) | 1,450 psig
SUPERHEAT TEMPERATURE | 1000 F
REHEAT TEMPERATURE | 1000 F
4. NUMBER OF FEEDWATER HEATERS | 5
5. LAST ROW OF BLADING SIZE / RPMs | N/A / 3,600 RPM
6. GENERATOR MANUFACTURER | General Electric Company
7. NAMEPLATE RATINGS | 58,824 KVA 0.85 pF
8. NOMINAL GROSS MW OUTPUT | 50 MW
9. TYPE OF COOLING | Hydrogen
10. TYPE OF EXCITATION | Shunt Wound, Direct Connected, Room Cooled, Main Exciter, Motor Driven
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | N/A
3. MW DERATING - ALTER FUEL USE | N/A
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | Babcock & Wilcox Company
6. TYPE OF BOILER | Radiant Type Boiler
7. TYPE OF FUEL FIRING | Front Fired
8. DESCRIPTION OF BURNER LAYOUT | Two Burners at each of Four Levels
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 20.2 NMAC: .1,.7,.33 ,.61, .70, .71,.73,.74,.84; 40 CFR 50, 72,73,75,77
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | N/A
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | Off Stoichiometric Firing/BOOS
8. CURRENT LEVEL OF PARTICULATES | 0.0011 lb/MMBTU Test data; 4.9 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | 0.0006 lbs. SO2/MMBTU AP-42
10. CURRENT LEVEL OF NOx | 0.116 lbs. NOx/MMBTU CEMS Data; 177 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | N/A
14. APPLICABLE WATER POLLUTION REG | EPA NPDES 40 CFR 122
15. APPLICABLE WASTE DISPOSAL REG | EPA RCRA 40 CFR 260-265
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Cooling Tower
2. MANUFACTURER OF COOLING WATER SYS | Hamon
3. PEAK MW LOAD OF COOLING WATER SYS | 0.6714 Mw
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Two Constant Speed Motor Driven Pumps
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Pacific Pumps Inc.
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | 0.819 Mw
7. DESCRIPTION OF COMBUSTION AIR SYS | Forced Draft Fan, Single Width, Single Inlet
8. MANUFACTURER OF COMBUSTION AIR SYS | Westinghouse Electric Corporation
9. PEAK MW LOAD OF COMBUSTION AIR SYS | 0.522 Mw
10. DESCRIPTION OF AIR PREHEATER | Ljungstrom Regenerative Horizontal Shaft
11. MANUFACTURER OF AIR PREHEATER | The Air Preheater Corporation
12. PEAK MW LOAD OF AIR PREHEATER | 0.00559 Mw
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## RGD 8
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 3 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
RIO GRANDE UNIT 8
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | Westinghouse Electric Corporation
2. TURBINE DESCRIPTION | 150,000 kW
3. INLET TEMPERATURES / PRESSURES
THROTTLE PRESSURE (psig) | 1,800 psig
SUPERHEAT TEMPERATURE | 1000 F
REHEAT TEMPERATURE | 1000 F
4. NUMBER OF FEEDWATER HEATERS | 5
5. LAST ROW OF BLADING SIZE / RPMs | 23" / 3,600 RPM
6. GENERATOR MANUFACTURER | Westinghouse Electric Coporation
7. NAMEPLATE RATINGS | 185,000 KVA 0.9 pF
8. NOMINAL GROSS MW OUTPUT | 150 MW
9. TYPE OF COOLING | Hydrogen
10. TYPE OF EXCITATION | Brushless
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | N/A
3. MW DERATING - ALTER FUEL USE | N/A
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | Babcock & Wilcox Company
6. TYPE OF BOILER | Radiant Type Boiler
7. TYPE OF FUEL FIRING | Return Flow
8. DESCRIPTION OF BURNER LAYOUT | Three Rows with Four Low NOx Burners
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 20.2 NMAC: .1,.7,.33 ,.61, .70, .71,.73,.74,.84; 40 CFR 50, 72,73,75,77
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | Flue Gas Recirculation, Dry-Low Nox Burners
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | Off Stoichiometric Firing/BOOS, Flue Gas Recirculation
8. CURRENT LEVEL OF PARTICULATES | 0.0076 lb./MMBTU Test Data; 12.6 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | 0.0006 lbs. SO2/MMBTU AP-42
10. CURRENT LEVEL OF NOx | 0.198 lbs. NOx/MMBTU CEMS Data; 415.0/460.5 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | 140 Mw
14. APPLICABLE WATER POLLUTION REG | EPA NPDES 40 CFR 122
15. APPLICABLE WASTE DISPOSAL REG | EPA RCRA 40 CFR 260-265
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Cooling Tower
2. MANUFACTURER OF COOLING WATER SYS | Mid West Cooling Tower
3. PEAK MW LOAD OF COOLING WATER SYS | 1.488 Mw
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Two Motor Driven Centrifugal Pumps
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Byron Jackson Pump Division
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | 3.356 Mw
7. DESCRIPTION OF COMBUSTION AIR SYS | One Double Width, Double Inlet Centrifugal FD Fan
8. MANUFACTURER OF COMBUSTION AIR SYS | Green Fuel Economizer Company
9. PEAK MW LOAD OF COMBUSTION AIR SYS | 1.745 Mw
10. DESCRIPTION OF AIR PREHEATER | Ljungstrom Regenerative Type
11. MANUFACTURER OF AIR PREHEATER | The Air Preheater Corporation
12. PEAK MW LOAD OF AIR PREHEATER | 0.011749 Mw
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## RGD 9
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 4 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
RIO GRANDE UNIT 9
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | LMS100 - GE Aeroderivative Gas Turbine
3. INLET TEMPERATURES / PRESSURES | NA
THROTTLE PRESSURE (psig) | NA
SUPERHEAT TEMPERATURE | NA
REHEAT TEMPERATURE | NA
4. NUMBER OF FEEDWATER HEATERS | NA
5. LAST ROW OF BLADING SIZE / RPMs | unknown / 3600
6. GENERATOR MANUFACTURER | Brush
7. NAMEPLATE RATINGS | 155070 KVA
8. NOMINAL GROSS MW OUTPUT | 90 MW
9. TYPE OF COOLING | Air Cooled Generator
10. TYPE OF EXCITATION | Brushless
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas - LMS100 Gas Turbine
2. DESCRIPTION OF ALTERNATE FUEL | NA
3. MW DERATING - ALTER FUEL USE | NA
4. STARTUP FUEL | Natural Gas - LMS100 Gas Turbine
5. BOILER MANUFACTURER | NA
6. TYPE OF BOILER | NA
7. TYPE OF FUEL FIRING | NA
8. DESCRIPTION OF BURNER LAYOUT | NA
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | NMAC 20.2.61,72,77,84;40 CFR 60 Subpart A & Subpart KKKK;40 CFR 72,73, 75,77
2. MANUFACTURER OF PART. CONTROL | NA
3. MANUFACTURER OF SOx CONTROL | NA
4. MANUFACTURER OF NOx CONTROL | Express Integrated Technologies manufacturers SCR’s.
5. TYPE OF PARTICULATE CONTROL | NA
6. TYPE OF SOx CONTROL | None. Fuel Low in sulfer content
7. TYPE OF NOx CONTROL | Selective Catalytic Reduction (SCR) & Water injection
8. CURRENT LEVEL OF PARTICULATES | 0.0014 lb/MMBTU Test Data; 3.6 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | Natural gas Sulfer Content low; less than 0.25 grains of total sulfur per 100 dry standard cubic feet
10. CURRENT LEVEL OF NOx | 0.012 lb/MMBTU CEMS Data; 22.9 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | NA
12. PEAK MW LOAD OF SOx SYSTEM | NA
13. PEAK MW LOAD OF NOx SYSTEM | 100 MW
14. APPLICABLE WATER POLLUTION REG | EPA NPDES 40 CFR 122
15. APPLICABLE WASTE DISPOSAL REG | EPA RCRA 40 CFR 260-265
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Air / Water Temperature exchange Tower Marley Class F400
2. MANUFACTURER OF COOLING WATER SYS | Marley - 2 Fan System
3. PEAK MW LOAD OF COOLING WATER SYS | CT : 112KW Cir Pumps: 75 KW Intercooler 224 KW TOTAL = 411 KW
4. DESCRIPTION OF BOILER FEEDPUMP SYS | NA - has none
5. MANUFACTURER OF BOILER FEEDPUMP SYS | NA - has none
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | NA - has none
7. DESCRIPTION OF COMBUSTION AIR SYS | Filter Air & cooled if required - Combustion ambient air to Turbine
8. MANUFACTURER OF COMBUSTION AIR SYS | Vent/Comb: 11.2 KW Ammonia 7.46 KW DI Injection: 37.3 KW Total approx. = 56KW
9. PEAK MW LOAD OF COMBUSTION AIR SYS | NA
10. DESCRIPTION OF AIR PREHEATER | NA
11. MANUFACTURER OF AIR PREHEATER | NA
12. PEAK MW LOAD OF AIR PREHEATER | NA
13. DESCRIPTION OF FUEL FEED SYS | Natural Gas
14. MANUFACTURER OF FUEL FEED SYS | Kobelco Gas Compressor feeding LMS100 GE turbine
15. PEAK MW LOAD OF FUEL FEED SYS | average = 870 KW Output = 250 Deg. F / 1102 PSIG Natural gas

## MPS 1
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 5 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
MONTANA POWER STATION 1
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | LMS100 - GE Aeroderivative Gas Turbine
3. INLET TEMPERATURES / PRESSURES | NA
THROTTLE PRESSURE (psig) | NA
SUPERHEAT TEMPERATURE | NA
REHEAT TEMPERATURE | NA
4. NUMBER OF FEEDWATER HEATERS | NA
5. LAST ROW OF BLADING SIZE / RPMs | unknown / 3600
6. GENERATOR MANUFACTURER | Brush
7. NAMEPLATE RATINGS | 155070 KVA
8. NOMINAL GROSS MW OUTPUT | 90 MW
9. TYPE OF COOLING | Air Cooled Generator
10. TYPE OF EXCITATION | Brushless
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas - LMS100 Gas Turbine
2. DESCRIPTION OF ALTERNATE FUEL | Diesel Fuel Oil
3. MW DERATING - ALTER FUEL USE | NA
4. STARTUP FUEL | Natural Gas - LMS100 Gas Turbine
5. BOILER MANUFACTURER | NA
6. TYPE OF BOILER | NA
7. TYPE OF FUEL FIRING | NA
8. DESCRIPTION OF BURNER LAYOUT | NA
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 30 TAC 111; 40 CFR 60 Subpart A & Subpart KKKK;40 CFR 72
2. MANUFACTURER OF PART. CONTROL | None
3. MANUFACTURER OF SOx CONTROL | None
4. MANUFACTURER OF NOx CONTROL | Express Integrated Technologies
5. TYPE OF PARTICULATE CONTROL | None
6. TYPE OF SOx CONTROL | None. Fuel Low in sulfer content
7. TYPE OF NOx CONTROL | Selective Catalytic Reduction (SCR) & Water injection
8. CURRENT LEVEL OF PARTICULATES | 0.007 lb/MMBTU Manufacturer's data; 6 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | Natural gas Sulfer Content Low; less than 0.05 gr/scf
10. CURRENT LEVEL OF NOx | 0.014 lb/MMBTU CEMS Data; 14 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | NA
12. PEAK MW LOAD OF SOx SYSTEM | NA
13. PEAK MW LOAD OF NOx SYSTEM | 100 MW
14. APPLICABLE WATER POLLUTION REG | TEXAS: Reclaimed water use 30 TAC 210
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | NA
17. TYPE OF WASTE WATER SYSTEM | NA
18. MANUF OF WASTE DISPOSAL SYSTEM | NA
19. TYPE OF WASTE DISPOSAL SYSTEM | NA
20. PEAK MW LOAD OF WASTE WATER SYS | NA
21. PEAK MW LOAD OF WASTE DISP SYS | NA
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Air / Water Temperature exchange Tower Marley Class F400
2. MANUFACTURER OF COOLING WATER SYS | Marley - 2 Fan System
3. PEAK MW LOAD OF COOLING WATER SYS | CT : 112KW Cir Pumps: 75 KW Intercooler 224 KW TOTAL = 411 KW
4. DESCRIPTION OF BOILER FEEDPUMP SYS | NA - has none
5. MANUFACTURER OF BOILER FEEDPUMP SYS | NA - has none
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | NA - has none
7. DESCRIPTION OF COMBUSTION AIR SYS | Filter Air & cooled if required - Combustion ambient air to Turbine
8. MANUFACTURER OF COMBUSTION AIR SYS | Vent/Comb: 11.2 KW Ammonia 7.46 KW DI Injection: 37.3 KW Total approx. = 56KW
9. PEAK MW LOAD OF COMBUSTION AIR SYS | NA
10. DESCRIPTION OF AIR PREHEATER | NA
11. MANUFACTURER OF AIR PREHEATER | NA
12. PEAK MW LOAD OF AIR PREHEATER | NA
13. DESCRIPTION OF FUEL FEED SYS | Natural Gas
14. MANUFACTURER OF FUEL FEED SYS | Kobelco Gas Compressor feeding LMS100 GE turbine
15. PEAK MW LOAD OF FUEL FEED SYS | average = 870 KW Output = 250 Deg. F / 1102 PSIG Natural gas

## MPS 2
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 6 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
MONTANA POWER STATION 2
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | LMS100 - GE Aeroderivative Gas Turbine
3. INLET TEMPERATURES / PRESSURES | NA
THROTTLE PRESSURE (psig) | NA
SUPERHEAT TEMPERATURE | NA
REHEAT TEMPERATURE | NA
4. NUMBER OF FEEDWATER HEATERS | NA
5. LAST ROW OF BLADING SIZE / RPMs | unknown / 3600
6. GENERATOR MANUFACTURER | Brush
7. NAMEPLATE RATINGS | 155070 KVA
8. NOMINAL GROSS MW OUTPUT | 90 MW
9. TYPE OF COOLING | Air Cooled Generator
10. TYPE OF EXCITATION | Brushless
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas - LMS100 Gas Turbine
2. DESCRIPTION OF ALTERNATE FUEL | Diesel Fuel Oil
3. MW DERATING - ALTER FUEL USE | NA
4. STARTUP FUEL | Natural Gas - LMS100 Gas Turbine
5. BOILER MANUFACTURER | NA
6. TYPE OF BOILER | NA
7. TYPE OF FUEL FIRING | NA
8. DESCRIPTION OF BURNER LAYOUT | NA
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 30 TAC 111; 40 CFR 60 Subpart A & Subpart KKKK;40 CFR 72
2. MANUFACTURER OF PART. CONTROL | None
3. MANUFACTURER OF SOx CONTROL | None
4. MANUFACTURER OF NOx CONTROL | Express Integrated Technologies
5. TYPE OF PARTICULATE CONTROL | None
6. TYPE OF SOx CONTROL | None. Fuel Low in sulfer content
7. TYPE OF NOx CONTROL | Selective Catalytic Reduction (SCR) & Water injection
8. CURRENT LEVEL OF PARTICULATES | 0.007 lb/MMBTU Manufacturer's data; 6 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | Natural gas Sulfer Content Low; less than 0.05 gr/scf
10. CURRENT LEVEL OF NOx | 0.014 lb/MMBTU CEMS Data; 14 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | NA
12. PEAK MW LOAD OF SOx SYSTEM | NA
13. PEAK MW LOAD OF NOx SYSTEM | 100 MW
14. APPLICABLE WATER POLLUTION REG | TEXAS: Reclaimed water use 30 TAC 210
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | NA
17. TYPE OF WASTE WATER SYSTEM | NA
18. MANUF OF WASTE DISPOSAL SYSTEM | NA
19. TYPE OF WASTE DISPOSAL SYSTEM | NA
20. PEAK MW LOAD OF WASTE WATER SYS | NA
21. PEAK MW LOAD OF WASTE DISP SYS | NA
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Air / Water Temperature exchange Tower Marley Class F400
2. MANUFACTURER OF COOLING WATER SYS | Marley - 2 Fan System
3. PEAK MW LOAD OF COOLING WATER SYS | CT : 112KW Cir Pumps: 75 KW Intercooler 224 KW TOTAL = 411 KW
4. DESCRIPTION OF BOILER FEEDPUMP SYS | NA - has none
5. MANUFACTURER OF BOILER FEEDPUMP SYS | NA - has none
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | NA - has none
7. DESCRIPTION OF COMBUSTION AIR SYS | Filter Air & cooled if required - Combustion ambient air to Turbine
8. MANUFACTURER OF COMBUSTION AIR SYS | Vent/Comb: 11.2 KW Ammonia 7.46 KW DI Injection: 37.3 KW Total approx. = 56KW
9. PEAK MW LOAD OF COMBUSTION AIR SYS | NA
10. DESCRIPTION OF AIR PREHEATER | NA
11. MANUFACTURER OF AIR PREHEATER | NA
12. PEAK MW LOAD OF AIR PREHEATER | NA
13. DESCRIPTION OF FUEL FEED SYS | Natural Gas
14. MANUFACTURER OF FUEL FEED SYS | Kobelco Gas Compressor feeding LMS100 GE turbine
15. PEAK MW LOAD OF FUEL FEED SYS | average = 870 KW Output = 250 Deg. F / 1102 PSIG Natural gas

## MPS 3
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 7 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
MONTANA POWER STATION 3
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | LMS100 - GE Aeroderivative Gas Turbine
3. INLET TEMPERATURES / PRESSURES | 125 to 184 degrees F / 920 PSIG - Turbine LMS 100
THROTTLE PRESSURE (psig) | NA
SUPERHEAT TEMPERATURE | NA
REHEAT TEMPERATURE | NA
4. NUMBER OF FEEDWATER HEATERS | NA
5. LAST ROW OF BLADING SIZE / RPMs | unknown / 3600
6. GENERATOR MANUFACTURER | Brush
7. NAMEPLATE RATINGS | 155070 KVA
8. NOMINAL GROSS MW OUTPUT | 90 MW
9. TYPE OF COOLING | Air Cooled Generator
10. TYPE OF EXCITATION | Brushless
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas - LMS100 Gas Turbine
2. DESCRIPTION OF ALTERNATE FUEL | Diesel Fuel Oil
3. MW DERATING - ALTER FUEL USE | NA
4. STARTUP FUEL | Natural Gas - LMS100 Gas Turbine
5. BOILER MANUFACTURER | NA
6. TYPE OF BOILER | NA
7. TYPE OF FUEL FIRING | NA
8. DESCRIPTION OF BURNER LAYOUT | NA
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 30 TAC 111; 40 CFR 60 Subpart A & Subpart KKKK;40 CFR 72
2. MANUFACTURER OF PART. CONTROL | None
3. MANUFACTURER OF SOx CONTROL | None
4. MANUFACTURER OF NOx CONTROL | Express Integrated Technologies
5. TYPE OF PARTICULATE CONTROL | None
6. TYPE OF SOx CONTROL | None. Fuel Low in sulfer content
7. TYPE OF NOx CONTROL | Selective Catalytic Reduction (SCR) & Water injection
8. CURRENT LEVEL OF PARTICULATES | 0.007 lb/MMBTU Manufacturer's data; 6 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | Natural gas Sulfer Content Low; less than 0.05 gr/scf
10. CURRENT LEVEL OF NOx | 0.014 lb/MMBTU CEMS Data; 14 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | NA
12. PEAK MW LOAD OF SOx SYSTEM | NA
13. PEAK MW LOAD OF NOx SYSTEM | 100 MW
14. APPLICABLE WATER POLLUTION REG | TEXAS: Reclaimed water use 30 TAC 210
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | NA
17. TYPE OF WASTE WATER SYSTEM | NA
18. MANUF OF WASTE DISPOSAL SYSTEM | NA
19. TYPE OF WASTE DISPOSAL SYSTEM | NA
20. PEAK MW LOAD OF WASTE WATER SYS | NA
21. PEAK MW LOAD OF WASTE DISP SYS | NA
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Air / Water Temperature exchange Tower Marley Class F400
2. MANUFACTURER OF COOLING WATER SYS | Marley - 2 Fan System
3. PEAK MW LOAD OF COOLING WATER SYS | CT : 112KW Cir Pumps: 75 KW Intercooler 224 KW TOTAL = 411 KW
4. DESCRIPTION OF BOILER FEEDPUMP SYS | NA - has none
5. MANUFACTURER OF BOILER FEEDPUMP SYS | NA - has none
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | NA - has none
7. DESCRIPTION OF COMBUSTION AIR SYS | Filter Air & cooled if required - Combustion ambient air to Turbine
8. MANUFACTURER OF COMBUSTION AIR SYS | Vent/Comb: 11.2 KW Ammonia 7.46 KW DI Injection: 37.3 KW Total approx. = 56KW
9. PEAK MW LOAD OF COMBUSTION AIR SYS | NA
10. DESCRIPTION OF AIR PREHEATER | NA
11. MANUFACTURER OF AIR PREHEATER | NA
12. PEAK MW LOAD OF AIR PREHEATER | NA
13. DESCRIPTION OF FUEL FEED SYS | Natural Gas
14. MANUFACTURER OF FUEL FEED SYS | Kobelco Gas Compressor feeding LMS100 GE turbine
15. PEAK MW LOAD OF FUEL FEED SYS | average = 870 KW Output = 250 Deg. F / 1102 PSIG Natural gas

## MPS 4
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 8 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
MONTANA POWER STATION 4
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | LMS100 - GE Aeroderivative Gas Turbine
3. INLET TEMPERATURES / PRESSURES | 125 to 184 degrees F / 920 PSIG - Turbine LMS 100
THROTTLE PRESSURE (psig) | NA
SUPERHEAT TEMPERATURE | NA
REHEAT TEMPERATURE | NA
4. NUMBER OF FEEDWATER HEATERS | NA
5. LAST ROW OF BLADING SIZE / RPMs | unknown / 3600
6. GENERATOR MANUFACTURER | Brush
7. NAMEPLATE RATINGS | 155070 KVA
8. NOMINAL GROSS MW OUTPUT | 90 MW
9. TYPE OF COOLING | Air Cooled Generator
10. TYPE OF EXCITATION | Brushless
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas - LMS100 Gas Turbine
2. DESCRIPTION OF ALTERNATE FUEL | Diesel Fuel Oil
3. MW DERATING - ALTER FUEL USE | NA
4. STARTUP FUEL | Natural Gas - LMS100 Gas Turbine
5. BOILER MANUFACTURER | NA
6. TYPE OF BOILER | NA
7. TYPE OF FUEL FIRING | NA
8. DESCRIPTION OF BURNER LAYOUT | NA
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 30 TAC 111; 40 CFR 60 Subpart A & Subpart KKKK;40 CFR 72
2. MANUFACTURER OF PART. CONTROL | None
3. MANUFACTURER OF SOx CONTROL | None
4. MANUFACTURER OF NOx CONTROL | Express Integrated Technologies
5. TYPE OF PARTICULATE CONTROL | None
6. TYPE OF SOx CONTROL | None. Fuel Low in sulfer content
7. TYPE OF NOx CONTROL | Selective Catalytic Reduction (SCR) & Water injection
8. CURRENT LEVEL OF PARTICULATES | 0.007 lb/MMBTU Manufacturer's data; 6 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | Natural gas Sulfer Content Low; less than 0.05 gr/scf
10. CURRENT LEVEL OF NOx | 0.014 lb/MMBTU CEMS Data; 14 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | NA
12. PEAK MW LOAD OF SOx SYSTEM | NA
13. PEAK MW LOAD OF NOx SYSTEM | 100 MW
14. APPLICABLE WATER POLLUTION REG | TEXAS: Reclaimed water use 30 TAC 210
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | NA
17. TYPE OF WASTE WATER SYSTEM | NA
18. MANUF OF WASTE DISPOSAL SYSTEM | NA
19. TYPE OF WASTE DISPOSAL SYSTEM | NA
20. PEAK MW LOAD OF WASTE WATER SYS | NA
21. PEAK MW LOAD OF WASTE DISP SYS | NA
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Air / Water Temperature exchange Tower Marley Class F400
2. MANUFACTURER OF COOLING WATER SYS | Marley - 2 Fan System
3. PEAK MW LOAD OF COOLING WATER SYS | CT : 112KW Cir Pumps: 75 KW Intercooler 224 KW TOTAL = 411 KW
4. DESCRIPTION OF BOILER FEEDPUMP SYS | NA - has none
5. MANUFACTURER OF BOILER FEEDPUMP SYS | NA - has none
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | NA - has none
7. DESCRIPTION OF COMBUSTION AIR SYS | Filter Air & cooled if required - Combustion ambient air to Turbine
8. MANUFACTURER OF COMBUSTION AIR SYS | Vent/Comb: 11.2 KW Ammonia 7.46 KW DI Injection: 37.3 KW Total approx. = 56KW
9. PEAK MW LOAD OF COMBUSTION AIR SYS | NA
10. DESCRIPTION OF AIR PREHEATER | NA
11. MANUFACTURER OF AIR PREHEATER | NA
12. PEAK MW LOAD OF AIR PREHEATER | NA
13. DESCRIPTION OF FUEL FEED SYS | Natural Gas
14. MANUFACTURER OF FUEL FEED SYS | Kobelco Gas Compressor feeding LMS100 GE turbine
15. PEAK MW LOAD OF FUEL FEED SYS | average = 870 KW Output = 250 Deg. F / 1102 PSIG Natural gas

## NWM 1
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 9 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
NEWMAN UNIT 1
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | Allis Chalmers
2. TURBINE DESCRIPTION | Tandem Compound, Reheat, Double Flow
3. INLET TEMPERATURES / PRESSURES
THROTTLE PRESSURE (psig) | 1,450 psig
SUPERHEAT TEMPERATURE | 1000 F
REHEAT TEMPERATURE | 1000 F
4. NUMBER OF FEEDWATER HEATERS | 5
5. LAST ROW OF BLADING SIZE / RPMs | 24" / 3,600 RPM
6. GENERATOR MANUFACTURER | Allis Chalmers
7. NAMEPLATE RATINGS | 96,000 KVA
8. NOMINAL GROSS MW OUTPUT | 82 MW
9. TYPE OF COOLING | Hydrogen Water Coolers
10. TYPE OF EXCITATION | Static Exciter
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | Fuel Oil
3. MW DERATING - ALTER FUEL USE | 3%
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | Babcock & Wilcox Company
6. TYPE OF BOILER | Pressurized, DrumType, Water Cooled
7. TYPE OF FUEL FIRING | Natural Gas
8. DESCRIPTION OF BURNER LAYOUT | Four Tiers, Three Burners per Tier of Multi-Spud
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | TAC Title 30 Sections 111, 112, 115, 116, 118, & 122
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | N/A
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | Off Stoichiometric Firing/BOOS
8. CURRENT LEVEL OF PARTICULATES | 0.0007 lb/MMBTU Test Data
9. CURRENT LEVEL OF SOx | 0.003 grains of S /dscf
10. CURRENT LEVEL OF NOx | 0.184 lb/MMBTU CEMS Data
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | N/A
14. APPLICABLE WATER POLLUTION REG | TEXAS TPDES 30 TAC 305; Reclaimed water use 30 TAC 210 prior to August 29, 2017
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Induced Draft Cross Flow - Five Cells - Surface Condenser
2. MANUFACTURER OF COOLING WATER SYS | Marley Towers - Westinghouse Condenser
3. PEAK MW LOAD OF COOLING WATER SYS | 1.07 Mw
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Dual - Half Load Pumps Used in Parallel
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Allis Chalmers
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | 1.8 Mw
7. DESCRIPTION OF COMBUSTION AIR SYS | Single - Double Inlet Centrifugal F. D. Fan
8. MANUFACTURER OF COMBUSTION AIR SYS | Westinghouse - Bailey Metering
9. PEAK MW LOAD OF COMBUSTION AIR SYS | .77 Mw
10. DESCRIPTION OF AIR PREHEATER | Regenerative Design Preheater
11. MANUFACTURER OF AIR PREHEATER | Ljungstrom - The Air Preheater Company
12. PEAK MW LOAD OF AIR PREHEATER | .02 Mw
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## NWM 2
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 10 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
NEWMAN UNIT 2
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | Tandem Compound, Reheat, Double Flow
3. INLET TEMPERATURES / PRESSURES
THROTTLE PRESSURE (psig) | 1,450 psig
SUPERHEAT TEMPERATURE | 1000 F
REHEAT TEMPERATURE | 1000 F
4. NUMBER OF FEEDWATER HEATERS | 5
5. LAST ROW OF BLADING SIZE / RPMs | 20" / 3,600 RPM
6. GENERATOR MANUFACTURER | General Electric
7. NAMEPLATE RATINGS | 96,000 KVA
8. NOMINAL GROSS MW OUTPUT | 82 MW
9. TYPE OF COOLING | Hydrogen Water Coolers
10. TYPE OF EXCITATION | D.C. Exciter
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | Fuel Oil
3. MW DERATING - ALTER FUEL USE | 3%
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | Babcock & Wilcox Company
6. TYPE OF BOILER | Pressurized, DrumType, Water Cooled
7. TYPE OF FUEL FIRING | Natural Gas
8. DESCRIPTION OF BURNER LAYOUT | Four Tiers, Three Burners per Tier of Multi-Spud
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | TAC Title 30 Sections 111, 112, 115, 116, 118, & 122
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | N/A
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | Off Stoichiometric Firing/BOOS
8. CURRENT LEVEL OF PARTICULATES | 0.0012 lb/MMBTU Test Data
9. CURRENT LEVEL OF SOx | 0.003 grains of S/dscf
10. CURRENT LEVEL OF NOx | 0.179 lb/MMBTU CEMS Data
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | N/A
14. APPLICABLE WATER POLLUTION REG | TEXAS TPDES 30 TAC 305; Reclaimed water use 30 TAC 210 prior to August 29, 2017
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Induced Draft Counter Flow - Six Cells - Surface Condenser
2. MANUFACTURER OF COOLING WATER SYS | CTTI - Allis Chalmers
3. PEAK MW LOAD OF COOLING WATER SYS | 1.06 Mw
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Dual - Halfload Centrifugal Pumps
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Allis Chalmers
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | 1.80 Mw
7. DESCRIPTION OF COMBUSTION AIR SYS | Double Inlet Forced Draft Fan
8. MANUFACTURER OF COMBUSTION AIR SYS | Westinghouse - Bailey Metering
9. PEAK MW LOAD OF COMBUSTION AIR SYS | .75 Mw
10. DESCRIPTION OF AIR PREHEATER | Regenerative Design Preheater
11. MANUFACTURER OF AIR PREHEATER | Ljungstrom - The Air Preheater Company
12. PEAK MW LOAD OF AIR PREHEATER | .02 Mw
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## NWM 3
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 11 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
NEWMAN UNIT 3
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | Tandem Compound, Reheat, Double Flow
3. INLET TEMPERATURES / PRESSURES
THROTTLE PRESSURE (psig) | 1,800 psig
SUPERHEAT TEMPERATURE | 1000 F
REHEAT TEMPERATURE | 1000 F
4. NUMBER OF FEEDWATER HEATERS | 5
5. LAST ROW OF BLADING SIZE / RPMs | 20" / 3,600 RPM
6. GENERATOR MANUFACTURER | General Electric
7. NAMEPLATE RATINGS | 135,300 KVA
8. NOMINAL GROSS MW OUTPUT | 102 MW
9. TYPE OF COOLING | Hydrogen Water Coolers
10. TYPE OF EXCITATION | Static Exciter
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | Fuel Oil
3. MW DERATING - ALTER FUEL USE | 3%
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | Babcock & Wilcox Company
6. TYPE OF BOILER | Pressurized, DrumType, Water Cooled
7. TYPE OF FUEL FIRING | Natural Gas
8. DESCRIPTION OF BURNER LAYOUT | Three Tiers with Three Burners of Multi-Spud
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | TAC Title 30 Sections 111, 112, 115, 116, 118, & 122
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | N/A
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | Off Stoichiometric Firing/BOOS, Flue Gas Recirculation
8. CURRENT LEVEL OF PARTICULATES | 0.0011 lb/MMBTU Test Data
9. CURRENT LEVEL OF SOx | 0.003 grains of S/dscf
10. CURRENT LEVEL OF NOx | 0.220 lb/MMBTU CEMS Data
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | N/A
14. APPLICABLE WATER POLLUTION REG | TEXAS TPDES 30 TAC 305; Reclaimed water use 30 TAC 210 prior to August 29, 2017
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Induced Draft Counter Flow Cooling Tower - Six Cells - Surface Condenser
2. MANUFACTURER OF COOLING WATER SYS | CTTI - Worthington
3. PEAK MW LOAD OF COOLING WATER SYS | 1.12 Mw
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Dual - Halfload Pumps
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Ingersoll Rand Mfg.
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | 2.30 Mw
7. DESCRIPTION OF COMBUSTION AIR SYS | Double Width - Double Inlet Forced Draft Fan
8. MANUFACTURER OF COMBUSTION AIR SYS | Westinghouse - Bailey Metering
9. PEAK MW LOAD OF COMBUSTION AIR SYS | .95 Mw
10. DESCRIPTION OF AIR PREHEATER | Regenerative Design Preheater
11. MANUFACTURER OF AIR PREHEATER | Ljungstrom - The Air Preheater Company
12. PEAK MW LOAD OF AIR PREHEATER | .04 Mw
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## NWM 4GT1
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 12 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
NEWMAN UNIT 4-GT1
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | Westinghouse
2. TURBINE DESCRIPTION | 501 B-6 Gas Turbine Exhausting to a HRSG
3. INLET TEMP./ PRES.- COMB. CYCLE PLANT
THROTTLE PRESSURE (psig) | N/A
SUPERHEAT TEMPERATURE | 950 F
REHEAT TEMPERATURE | N/A
4. NUMBER OF FEEDWATER HEATERS | 1
5. LAST ROW OF BLADING SIZE / RPMs | 19 in./ 3,600 RPM
6. GENERATOR MANUFACTURER | Westinghouse
7. NAMEPLATE RATINGS | 94,444 KVA
8. NOMINAL GROSS MW OUTPUT | 73 MW
9. TYPE OF COOLING | Hydrogen Water Coolers
10. TYPE OF EXCITATION | Brushless P.M.G. Exciter
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | NA
3. MW DERATING - ALTER FUEL USE | NA
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | Westinghouse
6. TYPE OF BOILER | Heat Recovery Steam Generator / Afterburners
7. TYPE OF FUEL FIRING | Natural Gas
8. DESCRIPTION OF BURNER LAYOUT | Afterburners 3 runner style burners
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | Federal 40 CFR Part 60; TAC Title 30 Sections 111, 112, 115, 116, 118, 122
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | Westinghouse
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | Water Injection
8. CURRENT LEVEL OF PARTICULATES | 0.001 lb/MMBTU Test Data; 2 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | 0.003 grains of S/dscf; 17 lbs/ hr permitted limit
10. CURRENT LEVEL OF NOx | 0.173 lb/MMBTU CEMS Data; 188 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | N/A
14. APPLICABLE WATER POLLUTION REG | TEXAS TPDES 30 TAC 305; Reclaimed water use 30 TAC 210 prior to August 29, 2017
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Induced Draft Cooling Tower - Surface Condenser
2. MANUFACTURER OF COOLING WATER SYS | Marley - Westinghouse
3. PEAK MW LOAD OF COOLING WATER SYS | 3.55 Mw
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Single Multi-Stage Pump
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Sulzer - Bingham
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | .98 Mw
7. DESCRIPTION OF COMBUSTION AIR SYS | Compressed Air - 17 Stage Compressor
8. MANUFACTURER OF COMBUSTION AIR SYS | Westinghouse
9. PEAK MW LOAD OF COMBUSTION AIR SYS | N/A
10. DESCRIPTION OF AIR PREHEATER | N/A
11. MANUFACTURER OF AIR PREHEATER | N/A
12. PEAK MW LOAD OF AIR PREHEATER | N/A
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## NWM 4GT2
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 13 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
NEWMAN UNIT 4-GT2
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | Westinghouse
2. TURBINE DESCRIPTION | 501 B-6 Gas Turbine Exhausting to a HRSG
3. INLET TEMP./ PRES.- COMB. CYCLE PLANT
THROTTLE PRESSURE (psig) | N/A
SUPERHEAT TEMPERATURE | 950 F
REHEAT TEMPERATURE | N/A
4. NUMBER OF FEEDWATER HEATERS | 1
5. LAST ROW OF BLADING SIZE / RPMs | 19 in. / 3,600 RPM
6. GENERATOR MANUFACTURER | Westinghouse
7. NAMEPLATE RATINGS | 94,444 KVA
8. NOMINAL GROSS MW OUTPUT | 73 MW
9. TYPE OF COOLING | Hydrogen Water Coolers
10. TYPE OF EXCITATION | Brushless P.M.G. Exciter
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | NA
3. MW DERATING - ALTER FUEL USE | NA
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | Westinghouse
6. TYPE OF BOILER | Heat Recovery Steam Generator / Afterburners
7. TYPE OF FUEL FIRING | Natural Gas
8. DESCRIPTION OF BURNER LAYOUT | Afterburners 3 runner style burners
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | Federal 40 CFR Part 60; TAC Title 30 Sections 111, 112, 115, 116, 118, 122
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | Westinghouse
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | Water Injection
8. CURRENT LEVEL OF PARTICULATES | 0.001 lb/MMBTU Test Data; 2 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | 0.003 grains of S/dscf; 17 lbs/hr permitted limit
10. CURRENT LEVEL OF NOx | 0.178 lb/MMBTU CEMS Data; 188 lbs/hr permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | N/A
14. APPLICABLE WATER POLLUTION REG | TEXAS TPDES 30 TAC 305; Reclaimed water use 30 TAC 210 prior to August 29, 2017
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Induced Draft Cooling Tower - Surface Condenser
2. MANUFACTURER OF COOLING WATER SYS | Marley - Westinghouse
3. PEAK MW LOAD OF COOLING WATER SYS | 3.55 Mw
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Single Multi-Stage Pump
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Salzer - Bingham
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | .98 Mw
7. DESCRIPTION OF COMBUSTION AIR SYS | Compressed Air - 17 Stage Compressor
8. MANUFACTURER OF COMBUSTION AIR SYS | Westinghouse
9. PEAK MW LOAD OF COMBUSTION AIR SYS | N/A
10. DESCRIPTION OF AIR PREHEATER | N/A
11. MANUFACTURER OF AIR PREHEATER | N/A
12. PEAK MW LOAD OF AIR PREHEATER | N/A
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## NWM 4ST
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 14 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
NEWMAN UNIT 4-ST
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | Westinghouse
2. TURBINE DESCRIPTION | 107 MW Condensing Turbine Single Cylinder
3. INLET TEMP./ PRES.- COMB. CYCLE PLANT
THROTTLE PRESSURE (psig) | 1,222 psig
SUPERHEAT TEMPERATURE | 950 F
REHEAT TEMPERATURE | N/A
4. NUMBER OF FEEDWATER HEATERS | 1
5. LAST ROW OF BLADING SIZE / RPMs | 28.5 / 3,600 RPM
6. GENERATOR MANUFACTURER | Westinghouse
7. NAMEPLATE RATINGS | 133,333 KVA
8. NOMINAL GROSS MW OUTPUT | 63 MW / Afterburners 92 MW
9. TYPE OF COOLING | Hydrogen Water Coolers
10. TYPE OF EXCITATION | Brushless P.M.G. Exciter
BOILER
1. DESCRIPTION OF PRIMARY FUEL | N/A
2. DESCRIPTION OF ALTERNATE FUEL | N/A
3. MW DERATING - ALTER FUEL USE | N/A
4. STARTUP FUEL | N/A
5. BOILER MANUFACTURER | N/A
6. TYPE OF BOILER | N/A
7. TYPE OF FUEL FIRING | N/A
8. DESCRIPTION OF BURNER LAYOUT | N/A
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | N/A
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | N/A
5. TYPE OF PARTICULATE CONTROL | N/A
6. TYPE OF SOx CONTROL | N/A
7. TYPE OF NOx CONTROL | N/A
8. CURRENT LEVEL OF PARTICULATES | N/A
9. CURRENT LEVEL OF SOx | N/A
10. CURRENT LEVEL OF NOx | N/A
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | N/A
14. APPLICABLE WATER POLLUTION REG | TEXAS TPDES 30 TAC 305; Reclaimed water use 30 TAC 210 prior to August 29, 2017
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Induced Draft Crossflow Cooling Tower - Surface Condenser
2. MANUFACTURER OF COOLING WATER SYS | Marley - Westinghouse
3. PEAK MW LOAD OF COOLING WATER SYS | 3.55 Mw
4. DESCRIPTION OF BOILER FEEDPUMP SYS | N/A
5. MANUFACTURER OF BOILER FEEDPUMP SYS | N/A
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | N/A
7. DESCRIPTION OF COMBUSTION AIR SYS | N/A
8. MANUFACTURER OF COMBUSTION AIR SYS | N/A
9. PEAK MW LOAD OF COMBUSTION AIR SYS | N/A
10. DESCRIPTION OF AIR PREHEATER | N/A
11. MANUFACTURER OF AIR PREHEATER | N/A
12. PEAK MW LOAD OF AIR PREHEATER | N/A
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## NWM 5GT3
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 15 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
NEWMAN UNIT 5-GT3
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | 7EA Gas Turbine
3. INLET TEMP./ PRES.- COMB. CYCLE PLANT | N/A
THROTTLE PRESSURE (psig) | N/A
SUPERHEAT TEMPERATURE | N/A
REHEAT TEMPERATURE | N/A
4. NUMBER OF FEEDWATER HEATERS | N/A
5. LAST ROW OF BLADING SIZE / RPMs | N/A/3600 rpm
6. GENERATOR MANUFACTURER | Brush
7. NAMEPLATE RATINGS | 101800 KVA
8. NOMINAL GROSS MW OUTPUT | 74390 kW
9. TYPE OF COOLING | Air
10. TYPE OF EXCITATION | Brushless
BOILER
1. DESCRIPTION OF PRIMARY FUEL | See NM5ST
2. DESCRIPTION OF ALTERNATE FUEL | See NM5ST
3. MW DERATING - ALTER FUEL USE | See NM5ST
4. STARTUP FUEL | See NM5ST
5. BOILER MANUFACTURER | See NM5ST
6. TYPE OF BOILER | See NM5ST
7. TYPE OF FUEL FIRING | See NM5ST
8. DESCRIPTION OF BURNER LAYOUT | See NM5ST
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 40 CFR 60, 40 CFR75
2. MANUFACTURER OF PART. CONTROL | NA
3. MANUFACTURER OF SOx CONTROL | NA
4. MANUFACTURER OF NOx CONTROL | General Electric
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | DRY LOW NOx BURNERS
8. CURRENT LEVEL OF PARTICULATES | 0.008 lb/MMBTU Test Data; permit limits vary based on operating conditions
9. CURRENT LEVEL OF SOx | 0.003 grains of S/dscf; permit limits vary based on operating conditions
10. CURRENT LEVEL OF NOx | 0.093 lbs/MMBTU CEMS Data; permit limits vary based on operating conditions
11. PEAK MW LOAD OF PART. SYSTEM | 70 MW
12. PEAK MW LOAD OF SOx SYSTEM | 70 MW
13. PEAK MW LOAD OF NOx SYSTEM | 70 MW
14. APPLICABLE WATER POLLUTION REG | TEXAS TPDES 30 TAC 305; Reclaimed water use 30 TAC 210 prior to August 29, 2017
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Closed Fin Fan Cooler
2. MANUFACTURER OF COOLING WATER SYS | Econodyne
3. PEAK MW LOAD OF COOLING WATER SYS | .221MW
4. DESCRIPTION OF BOILER FEEDPUMP SYS | See NM5ST
5. MANUFACTURER OF BOILER FEEDPUMP SYS | See NM5ST
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | See NM5ST
7. DESCRIPTION OF COMBUSTION AIR SYS | Inlet air house
8. MANUFACTURER OF COMBUSTION AIR SYS | General Electric
9. PEAK MW LOAD OF COMBUSTION AIR SYS | 0MW
10. DESCRIPTION OF AIR PREHEATER | Inlet bleed heat
11. MANUFACTURER OF AIR PREHEATER | General Electric
12. PEAK MW LOAD OF AIR PREHEATER | 0MW
13. DESCRIPTION OF FUEL FEED SYS | Natural Gas
14. MANUFACTURER OF FUEL FEED SYS | General Electric
15. PEAK MW LOAD OF FUEL FEED SYS | .498MW

## NWM 5GT4
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 16 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
NEWMAN UNIT 5-GT4
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | 7EA Gas Turbine
3. INLET TEMP./ PRES.- COMB. CYCLE PLANT | N/A
THROTTLE PRESSURE (psig) | N/A
SUPERHEAT TEMPERATURE | N/A
REHEAT TEMPERATURE | N/A
4. NUMBER OF FEEDWATER HEATERS | N/A
5. LAST ROW OF BLADING SIZE / RPMs | N/A/3600 rpm
6. GENERATOR MANUFACTURER | Brush
7. NAMEPLATE RATINGS | 101800 KVA
8. NOMINAL GROSS MW OUTPUT | 74390 kW
9. TYPE OF COOLING | Air
10. TYPE OF EXCITATION | Brushless
BOILER
1. DESCRIPTION OF PRIMARY FUEL | See NM5ST
2. DESCRIPTION OF ALTERNATE FUEL | See NM5ST
3. MW DERATING - ALTER FUEL USE | See NM5ST
4. STARTUP FUEL | See NM5ST
5. BOILER MANUFACTURER | See NM5ST
6. TYPE OF BOILER | See NM5ST
7. TYPE OF FUEL FIRING | See NM5ST
8. DESCRIPTION OF BURNER LAYOUT | See NM5ST
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 40 CFR 60, 40 CFR75
2. MANUFACTURER OF PART. CONTROL | NA
3. MANUFACTURER OF SOx CONTROL | NA
4. MANUFACTURER OF NOx CONTROL | General Electric
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | DRY LOW NOx BURNERS
8. CURRENT LEVEL OF PARTICULATES | 0.008 lb/MMBTU Test Data; permit limits vary based on operating conditions
9. CURRENT LEVEL OF SOx | 0.003 grains of S/dscf; permit limits vary based on operating conditions
10. CURRENT LEVEL OF NOx | 0.085 lb/MMBTU CEMS Data; permit limits vary based on operating conditions
11. PEAK MW LOAD OF PART. SYSTEM | 70 MW
12. PEAK MW LOAD OF SOx SYSTEM | 70 MW
13. PEAK MW LOAD OF NOx SYSTEM | 70 MW
14. APPLICABLE WATER POLLUTION REG | TEXAS TPDES 30 TAC 305; Reclaimed water use 30 TAC 210 prior to August 29, 2017
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Closed Fin Fan Cooler
2. MANUFACTURER OF COOLING WATER SYS | Econodyne
3. PEAK MW LOAD OF COOLING WATER SYS | .221MW
4. DESCRIPTION OF BOILER FEEDPUMP SYS | See NM5ST
5. MANUFACTURER OF BOILER FEEDPUMP SYS | See NM5ST
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | See NM5ST
7. DESCRIPTION OF COMBUSTION AIR SYS | Inlet air house
8. MANUFACTURER OF COMBUSTION AIR SYS | General Electric
9. PEAK MW LOAD OF COMBUSTION AIR SYS | 0MW
10. DESCRIPTION OF AIR PREHEATER | Inlet bleed heat
11. MANUFACTURER OF AIR PREHEATER | General Electric
12. PEAK MW LOAD OF AIR PREHEATER | 0MW
13. DESCRIPTION OF FUEL FEED SYS | Natural Gas
14. MANUFACTURER OF FUEL FEED SYS | General Electric
15. PEAK MW LOAD OF FUEL FEED SYS | .498MW

## NWM 5ST
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 17 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
NEWMAN UNIT 5-ST
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | FUJI
2. TURBINE DESCRIPTION | Tandem compound 2 casing reheat admission condensing steam turbine
3. INLET TEMP./ PRES.- COMB. CYCLE PLANT
THROTTLE PRESSURE (psig) | 1882 psia
SUPERHEAT TEMPERATURE | 1050 F
REHEAT TEMPERATURE | 1050 F
4. NUMBER OF FEEDWATER HEATERS | 0
5. LAST ROW OF BLADING SIZE / RPMs | 3600 rpm
6. GENERATOR MANUFACTURER | FUJI - 157.6 MVA, 0.85 PF, 3600 rpm, TEWAC
7. NAMEPLATE RATINGS | 142.1 MW, 3600 rpm, 13800 V, 2 pole
8. NOMINAL GROSS MW OUTPUT | 142 MW
9. TYPE OF COOLING | Totally Enclosed Water Air Cooled ---Water/glycol mixture
10. TYPE OF EXCITATION | FUJI - Brushless exciter
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | NA
3. MW DERATING - ALTER FUEL USE | NA
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | Nooter Eriksen
6. TYPE OF BOILER | Heat Recovery Steam Generator (three pressure)
7. TYPE OF FUEL FIRING | duct burners - natual gas
8. DESCRIPTION OF BURNER LAYOUT | burner elements (runners) equally spaced within duct system in the HRSG upstream of HP superheater tubes
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | NA
2. MANUFACTURER OF PART. CONTROL | NA
3. MANUFACTURER OF SOx CONTROL | NA
4. MANUFACTURER OF NOx CONTROL | NA
5. TYPE OF PARTICULATE CONTROL | NA
6. TYPE OF SOx CONTROL | NA
7. TYPE OF NOx CONTROL | NA
8. CURRENT LEVEL OF PARTICULATES | NA
9. CURRENT LEVEL OF SOx | NA
10. CURRENT LEVEL OF NOx | NA
11. PEAK MW LOAD OF PART. SYSTEM | NA
12. PEAK MW LOAD OF SOx SYSTEM | NA
13. PEAK MW LOAD OF NOx SYSTEM | NA
14. APPLICABLE WATER POLLUTION REG | TEXAS TPDES 30 TAC 305; Reclaimed water use 30 TAC 210 prior to August 29, 2017
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Induced Draft Counterflow Cooling Tower
2. MANUFACTURER OF COOLING WATER SYS | SPIG - cooling towers
3. PEAK MW LOAD OF COOLING WATER SYS | 3.1MW
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Horizontal ring section (12 stage), 1200 hp, 3600 rpm, 4160 volt (100% unfired)
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Flowserve
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | 3.528MW
7. DESCRIPTION OF COMBUSTION AIR SYS | N/A
8. MANUFACTURER OF COMBUSTION AIR SYS | N/A
9. PEAK MW LOAD OF COMBUSTION AIR SYS | N/A
10. DESCRIPTION OF AIR PREHEATER | N/A
11. MANUFACTURER OF AIR PREHEATER | N/A
12. PEAK MW LOAD OF AIR PREHEATER | N/A
13. DESCRIPTION OF FUEL FEED SYS | Natural Gas
14. MANUFACTURER OF FUEL FEED SYS | John Zink
15. PEAK MW LOAD OF FUEL FEED SYS | .498MW

## COP
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 18 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
COPPER UNIT 1
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR
1. TURBINE MANUFACTURER | Westinghouse
2. TURBINE DESCRIPTION | 501-B4 Gas Turbine
3. INLET TEMPERATURES / PRESSURES
THROTTLE PRESSURE (psig) | N/A
SUPERHEAT TEMPERATURE | N/A
REHEAT TEMPERATURE | N/A
4. NUMBER OF FEEDWATER HEATERS | N/A
5. LAST ROW OF BLADING SIZE / RPMs | 19" / 3,600 RPM
6. GENERATOR MANUFACTURER | Westinghouse
7. NAMEPLATE RATINGS | 80.55/86.85
8. NOMINAL GROSS MW OUTPUT | 70 MW
9. TYPE OF COOLING | Air Cooled Generator
10. TYPE OF EXCITATION | Brushless P.M.G. Exciter
BOILER
1. DESCRIPTION OF PRIMARY FUEL | Natural Gas
2. DESCRIPTION OF ALTERNATE FUEL | N/A
3. MW DERATING - ALTER FUEL USE | N/A
4. STARTUP FUEL | Natural Gas
5. BOILER MANUFACTURER | N/A
6. TYPE OF BOILER | N/A
7. TYPE OF FUEL FIRING | N/A
8. DESCRIPTION OF BURNER LAYOUT | N/A
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | 40 CFR Part 60 Subpart GG; TAC Title 30, 111, 112, 115, 116, 118, and 122
2. MANUFACTURER OF PART. CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | Westinghouse
5. TYPE OF PARTICULATE CONTROL | None. Pipeline Quality Natural Gas (Sweet)
6. TYPE OF SOx CONTROL | None. Low Sulfur Fuel
7. TYPE OF NOx CONTROL | Water Injection
8. CURRENT LEVEL OF PARTICULATES | 0.0066 lb/MMBTU AP-42; 34.1 lbs/hr permitted limit
9. CURRENT LEVEL OF SOx | 0.0006 lbs. SO2/MMBTU NADB; 266 lbs/hr permitted limit
10. CURRENT LEVEL OF NOx | 0.267 lb/MMBTU CEMS Data; 294 lbs/hrs permitted limit
11. PEAK MW LOAD OF PART. SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | 70 MW
14. APPLICABLE WATER POLLUTION REG | N/A
15. APPLICABLE WASTE DISPOSAL REG | TEXAS Industrial Solid waste 30 TAC 335
16. MANUF. OF WASTE WATER SYSTEM | N/A
17. TYPE OF WASTE WATER SYSTEM | N/A
18. MANUF OF WASTE DISPOSAL SYSTEM | N/A
19. TYPE OF WASTE DISPOSAL SYSTEM | N/A
20. PEAK MW LOAD OF WASTE WATER SYS | N/A
21. PEAK MW LOAD OF WASTE DISP SYS | N/A
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | N/A
2. MANUFACTURER OF COOLING WATER SYS | N/A
3. PEAK MW LOAD OF COOLING WATER SYS | N/A
4. DESCRIPTION OF BOILER FEEDPUMP SYS | N/A
5. MANUFACTURER OF BOILER FEEDPUMP SYS | N/A
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | N/A
7. DESCRIPTION OF COMBUSTION AIR SYS | Compressed Air - 17 Stage Compressor
8. MANUFACTURER OF COMBUSTION AIR SYS | Westinghouse
9. PEAK MW LOAD OF COMBUSTION AIR SYS | N/A
10. DESCRIPTION OF AIR PREHEATER | N/A
11. MANUFACTURER OF AIR PREHEATER | N/A
12. PEAK MW LOAD OF AIR PREHEATER | N/A
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A

## PV 123
EL PASO ELECTRIC COMPANY | SCHEDULE H-12.3b
2021 TEXAS RATE CASE FILING | PAGE 19 OF 19
SCHEDULE H-12.3b: GENERATING UNIT CHARACTERISTICS
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A ARZAGA
FOR THE TEST YEAR ENDING DECEMBER 31, 2020
PALO VERDE UNITS 1, 2, & 3
CATEGORY | DESCRIPTION / RESPONSE
TURBINE-GENERATOR - See Note #2
1. TURBINE MANUFACTURER | General Electric
2. TURBINE DESCRIPTION | Rated at 1800 RPM, Tandem Compound, 6-Flow, with Reheat, 1 HP-3 LP
3. INLET TEMPERATURES / PRESSURES | Inlet 546.1 F/1012 psia (100% Pwr) 545.4 F/1007 psia (VWO)
THROTTLE PRESSURE (psig)
SUPERHEAT TEMPERATURE
REHEAT TEMPERATURE
4. NUMBER OF FEEDWATER HEATERS | 3 Sets of 4 LP Feedwater Heaters, 2 Sets of 3 HP Feedwater Heaters
5. LAST ROW OF BLADING SIZE / RPM | Last Stage = 43" and 1800 RPM
6. GENERATOR MANUFACTURER | General Electric
7. NAMEPLATE RATINGS | Rating: 1559.1 MVA @ 24KV, 3 Phase, 60 Hz
8. NOMINAL GROSS MW OUTPUT-See Note #1 | Gross Output: 1411 MW (100% Pwr), 1443 MW (Valves Wide Open [VWO])
9. TYPE OF COOLING | Water Cooled
10. TYPE OF EXCITATION | U1/U3-Self, "Generex" System . U2-External transformer, "EX2100e'.
BOILER
1. DESCRIPTION OF PRIMARY FUEL | N/A
2. DESCRIPTION OF ALTERNATE FUEL | N/A
3. MW DERATING - ALTERNATE FUEL USE | N/A
4. STARTUP FUEL | N/A
5. BOILER MANUFACTURER | N/A
6. TYPE OF BOILER | N/A
7. TYPE OF FUEL FIRING | N/A
8. DESCRIPTION OF BURNER LAYOUT | N/A
POLLUTION CONTROL
1. APPLICABLE AIR POLLUTION REG | N/A
2. MANUFACTURER OF PARTICULATE CONTROL | N/A
3. MANUFACTURER OF SOx CONTROL | N/A
4. MANUFACTURER OF NOx CONTROL | N/A
5. TYPE OF PARTICULATE CONTROL | N/A
6. TYPE OF SOx CONTROL | N/A
7. TYPE OF NOx CONTROL | N/A
8. CURRENT LEVEL OF PARTICULATES | N/A
9. CURRENT LEVEL OF SOx | N/A
10. CURRENT LEVEL OF NOx | N/A
11. PEAK MW LOAD OF PARTICULATE SYSTEM | N/A
12. PEAK MW LOAD OF SOx SYSTEM | N/A
13. PEAK MW LOAD OF NOx SYSTEM | N/A
14. APPLICABLE WATER POLLUTION REG | Zero Discharge Site; Normal Industrial Federal and State Requirements
15. APPLICABLE WASTE DISPOSAL REG | Zero Discharge Site; Normal Industrial Federal and State Requirements
16. MANUFACTURER OF WASTE WATER SYSTEM | Clow Corp. (Installed by the Bechtel Corp.)
17. TYPE OF WASTE WATER SYSTEM | Contract Stabilization
18. MANUFACTURER OF WASTE DISPOSAL SYSTEM | (Same System as for Waste Water)
19. TYPE OF WASTE DISPOSAL SYSTEM | (Same System as for Waste Water)
20. PEAK MW LOAD OF WASTE WATER SYS | Plant System is Serviced by a 480V, 600A Motor Control Center Bus
21. PEAK MW LOAD OF WASTE DISPOSAL SYS | (Same System as for Waste Water)
AUXILIARIES & COOLING WATER SYSTEM
1. DESCRIPTION OF COOLING WATER SYS | Closed Loop/Mechanical Draft Towers, Make-Up is Reclaimed Effluent
2. MANUFACTURER OF COOLING WATER SYS | Bechtel (Prime Contractor)
3. PEAK MW LOAD OF COOLING WATER SYS | Four 3,730 kW Pumps per Unit (25% Capacity Each) = 14,920 KW at VWO
4. DESCRIPTION OF BOILER FEEDPUMP SYS | Two 65% Capacity, Turbine Driven, Var.-Speed, Single Stage, Horiz. Pumps
5. MANUFACTURER OF BOILER FEEDPUMP SYS | Byron Jackson Pump (As part of a Bechtel-designed system)
6. PEAK MW LOAD OF BOILER FEEDPUMP SYS | Each Pump is Rated at 14,000 HP (Steam Turbine Driven, Not Electrical)
7. DESCRIPTION OF COMBUSTION AIR SYS | N/A
8. MANUFACTURER OF COMBUSTION AIR SYS | N/A
9. PEAK MW LOAD OF COMBUSTION AIR SYS | N/A
10. DESCRIPTION OF AIR PREHEATER | N/A
11. MANUFACTURER OF AIR PREHEATER | N/A
12. PEAK MW LOAD OF AIR PREHEATER | N/A
13. DESCRIPTION OF FUEL FEED SYS | N/A
14. MANUFACTURER OF FUEL FEED SYS | N/A
15. PEAK MW LOAD OF FUEL FEED SYS | N/A
Note: 1 | Note 2: Data derived from updated GE heat balance 1LR0297-01 and 02.
Unit 2 had its steam generators and low pressure
turbine rotors replaced in late December 2003. Unit 1
the same changes made in December 2005. Unit 3
had same changes made in December 2007.
The new Design Electrical net rating for U1 is 1333 Mwe,
U2 is 1336 Mwe and U3 is 1334 Mwe.