## I-06
EL PASO ELECTRIC COMPANY | [10 empty] | SCHEDULE I-6
2021 TEXAS RATE CASE FILING | [10 empty] | PAGE 1 OF 1
SCHEDULE I-6: NATURAL GAS DELIVERY SYSTEM
SPONSOR: J KYLE OLSON
PREPARER: MELANEE DURAN
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
NATURAL GAS DELIVERY SYSTEMS TO EPE'S GAS FIRED STATIONS
|  |  | RIO GRANDE STATION |  | NEWMAN STATION |  | MONTANA STATION |  |  | COPPER STATION
A
1 | NUMBER OF PIPELINE |  |  | ONE |  | TWO |  | TWO |  | TWO
CONNECTIONS POSSIBLE
B
2 | NUMBER OF PIPELINES |  |  | ONE |  | TWO |  | TWO |  | TWO
CONNECTED
C
3 | OWNER/OPERATOR OF PIPELINE |  | a. | EPNG | a. | EPNG | a. | EPNG | b. | ONEOK
[5 empty] | b. | ONEOK | b. | ONEOK | c. | TGS
D
4 | MAXIMUM OPERATING CAPACITY |  | a. | 73990 | a. | 186000 | a. | 90000 | b. | 45000
| OF EACH CONNECTED PIPELINE |  |  |  | b. | 45000 | b. | 45000 | c. | 16490.6691
(MMBTU/D)
E
5 | MAXIMUM OPERATING CAPACITY
| OF EACH CONNECTED PIPELINE |  | a. | 94.33% | a. | 102.2% | a. | 107.2% | b. | 147%
| COMPARED TO NATURAL GAS |  |  |  | b. | 34.44% | b. | 53.6% | c. | 53.86%
REQUIREMENTS OF THE PLANT
AT FULL LOAD
NOTES/ASSUMPTIONS
A | This represents the number of possible connections and may not reflect actual pipeline connection.
B | For the Rio Grande Station, this pipeline is composed of an 8 inch and 6 inch pipeline representing EPNG'S mainline system to the Rio Grande Station.
C | a. EPNG - El Paso Natural Gas Company
b. ONEOK - ONEOK Westex Transmission LP
c. TGS - Texas Gas Service Company
D | The maximum capacity of each pipeline is based on meter design capabilities and pipeline operating constraints.
E | These are approximate percentages based on ideal full load burning capabilities over 24 hours. Pipeline maximum flow is divided by a station's full load burn over a 24-hour period.

## SEP2009 (hidden)
SEP | 2009 |  | Rio Grande Unit 6 |  | Rio Grande Unit 7 |  | Rio Grande Unit 8
|  |  | MTH | YTD | MTH | YTD | MTH | YTD
1. | Performance Factors
| Net Capacity Factor % |  | 0 | 23.1 | 0 | 25.6 | 39.8 | 21.1
| Equivalent Availability Factor % |  | 100 | 87.9 | 100 | 94.7 | 93.5 | 43.9
| Availability Factor % |  | 100 | 87.9 | 100 | 94.9 | 93.5 | 44.8
| Equivalent Forced Outage Rate % |  | 0 | 0.1 | 0 | 2.5 | 0 | 1.9
| Forced Outage Rate % |  | 0 | 0.1 | 0 | 2.3 | 0 | 0
| Scheduled Outage Rate % |  | 0 | 11.9811 | 0 | 2.8694 | 6.5278 | 55.2045
| Average Load % |  | 0 | 26.1351 | 0 | 24.9329 | 64.4562 | 71.2904
| Gross Heat Rate(BTU/KWH) |  | 0 | 11640.5077 | 0 | 10309.3561 | 10658.1526 | 10595.0537
| Net Heat Rate(BTU/KWH) |  | 0 | 12708.0958 | 0 | 11098.3394 | 11700.0709 | 11625.7567
2. | Generation Data
| Gross Generation MWH |  | 0 | 74302 | 0 | 83176 | 43379 | 209166
| Net Generation MWH |  | -70 | 68060 | -39 | 77263 | 39516 | 190622
| Station Service MWH |  | 70 | 6242 | 39 | 5913 | 3863 | 18544
| % Station Service |  | 0 | 8.4009 | 0 | 7.109 | 8.9052 | 8.8657
3. | Availability Data
| Period Hours |  | 720 | 6552 | 720 | 6552 | 720 | 6552
| Hours in Service |  | 0 | 2843 | 0 | 3336 | 673 | 2934
| Available Hours |  | 720 | 5761 | 720 | 6216 | 673 | 2934
| Forced Outage Hours |  | 0 | 6 | 0 | 148 | 0 | 1
| Planned Outage Hours |  | 0 | 476 | 0 | 188 | 0 | 3482
| Maintenance Outage Hours |  | 0 | 309 | 0 | 0 | 47 | 135
4. | Fuel Data
| Gas MMBTU Burned |  | 0 | 864913 | 0 | 857491 | 462340 | 2216125
| Oil Barrels Burned |  | 0 | 0 | 0 | 0 | 0 | 0
| Oil MMBTU Burned |  | 0 | 0 | 0 | 0 | 0 | 0
5.* | Cost of Fuel and Maintenance
Fuel, $ per MWH
Unit O&M, $ per MWH
Total, $ per MWH
NOTE: Emergency station service not chargeable to specific units:
| MTH: 113 | YTD: 1029
|  |  | Rio Grande Total |  | Newman Unit 1 |  | Newman Unit 2
|  |  | MTH | YTD | MTH | YTD | MTH | YTD
1. | Performance Factors
| Net Capacity Factor % |  | 23.8319 | 22.3217 | 48.4 | 42.9 | 9.3 | 51.3
| Equivalent Availability Factor % |  | 96.1 | 62.7507 | 98.5 | 91.7 | 99.9 | 96
| Availability Factor % |  | 96.083 | 63.3332 | 98.5 | 91.8 | 99.9 | 96
| Equivalent Forced Outage Rate % |  | 0 | 1.6668 | 1.5 | 0.8 | 0.1 | 0
| Forced Outage Rate % |  | 0 | 0.48166 | 1.5 | 0.8 | 0.1 | 0
| Scheduled Outage Rate % |  | 2.1759 | 23.3516 | 0 | 7.4786 | 0 | 3.9988
| Average Load % |  | 64.4562 | 40.2331 | 39.5628 | 40.9206 | 50.3091 | 48.8394
| Gross Heat Rate(BTU/KWH) |  | 10658.1526 | 10742.1068 | 11156.1497 | 10943.9028 | 10602.2768 | 10534.1791
| Net Heat Rate(BTU/KWH) |  | 11766.173 | 11759.7517 | 12124.3704 | 11889.2063 | 11574.8668 | 11265.179
2. | Generation Data
| Gross Generation MWH |  | 43379 | 366644 | 28050 | 226250 | 5534 | 273354
| Net Generation MWH |  | 39294 | 334916 | 25810 | 208261 | 5069 | 255616
| Station Service MWH |  | 4085 | 31728 | 2240 | 17989 | 465 | 17738
| % Station Service |  | 9.417 | 8.6536 | 7.9857 | 7.9509 | 8.4026 | 6.489
3. | Availability Data
| Period Hours |  | 2160 | 19656 | 720 | 6552 | 720 | 6552
| Hours in Service |  | 673 | 9113 | 709 | 5529 | 110 | 5597
| Available Hours |  | 2113 | 14911 | 709 | 6012 | 719 | 6289
| Forced Outage Hours |  | 0 | 155 | 11 | 50 | 1 | 1
| Planned Outage Hours |  | 0 | 4146 | 0 | 0 | 0 | 260
| Maintenance Outage Hours |  | 47 | 444 | 0 | 490 | 0 | 2
4. | Fuel Data
| Gas MMBTU Burned |  | 462340 | 3938529 | 312930 | 2476058 | 58673 | 2879560
| Oil Barrels Burned |  | 0 | 0 | 0 | 0 | 0 | 0
| Oil MMBTU Burned |  | 0 | 0 | 0 | 0 | 0 | 0
5.* | Cost of Fuel and Maintenance
| Fuel, $ per MWH |  | 68.91 | 67.45
| Unit O&M, $ per MWH |  | 15.96 | 26.79
| Total, $ per MWH |  | 84.87 | 94.24
|  |  | Newman Unit 3 |  | Newman Unit 4GT-1 |  | Newman Unit 4GT-2
|  |  | MTH | YTD | MTH | YTD | MTH | YTD
1. | Performance Factors
| Net Capacity Factor % |  | 53.9 | 47.2
| Equivalent Availability Factor % |  | 100 | 93.4 | 95.7 | 53.6 | 100 | 90.5
| Availability Factor % |  | 100 | 94.7 | 95.7 | 53.6 | 100 | 95.5
| Equivalent Forced Outage Rate % |  | 0 | 2.2 | 4.3 | 4.5 | 0 | 5.3
| Forced Outage Rate % |  | 0 | 0.8 | 4.3 | 4.5 | 0 | 0.4
| Scheduled Outage Rate % |  | 0 | 4.5482 | 0 | 43.8339 | 0 | 4.1056
| Average Load % |  | 56.0375 | 53.2398 | 41.9347 | 45.5058 | 44.0694 | 48.9146
| Gross Heat Rate(BTU/KWH) |  | 10137.8045 | 10280.6763
| Net Heat Rate(BTU/KWH) |  | 10862.2796 | 11050.3678
2. | Generation Data
| Gross Generation MWH |  | 40347 | 322154 | 28893 | 159589 | 31730 | 272503
| Net Generation MWH |  | 37656 | 299715
| Station Service MWH |  | 2691 | 22439
| % Station Service |  | 6.6696 | 6.9653
3. | Availability Data
| Period Hours |  | 720 | 6552 | 720 | 6552 | 720 | 6552
| Hours in Service |  | 720 | 6051 | 689 | 3507 | 720 | 5571
| Available Hours |  | 720 | 6206 | 689 | 3513 | 720 | 6260
| Forced Outage Hours |  | 0 | 48 | 31 | 167 | 0 | 23
| Planned Outage Hours |  | 0 | 298 | 0 | 2774 | 0 | 269
| Maintenance Outage Hours |  | 0 | 0 | 0 | 98 | 0 | 0
4. | Fuel Data
| Gas MMBTU Burned |  | 409030 | 3311961 | 452353 | 2423206 | 472089 | 3890910
| Oil Barrels Burned |  | 0 | 0 | 0 | 0 | 0 | 0
| Oil MMBTU Burned |  | 0 | 0 | 0 | 0 | 0 | 0
5.* | Cost of Fuel and Maintenance
Fuel, $ per MWH
Unit O&M, $ per MWH
Total, $ per MWH
|  |  | Newman Unit 4ST |  | Newman Unit 4 Total |  | Newman Unit 5GT-3
|  |  | MTH | YTD | MTH | YTD | MTH | YTD
1. | Performance Factors
| Net Capacity Factor % |  |  |  | 60.7 | 45.9 | 3.6 | 15
| Equivalent Availability Factor % |  | 97.8 | 69 | 98.7 | 81.2 | 82.8 | 95.8
| Availability Factor % |  | 100 | 84.3 | 99.1 | 89.1 | 82.8 | 95.8
| Equivalent Forced Outage Rate % |  | 0 | 12.1 | 1.4 | 6.2 | 0 | 0
| Forced Outage Rate % |  | 0 | 12.1 | 1.4 | 4.7 | 0 | 0
| Scheduled Outage Rate % |  | 0 | 4.0598 | 0 | 17.3331 | 17.2222 | 4.235
| Average Load % |  | 44.3472 | 37.2626 | 43.4725 | 43.687 | 72.625 | 28.0654
| Gross Heat Rate(BTU/KWH) |  |  |  | 9988.2446 | 9896.656 | 11086.6322 | 10243.9123
| Net Heat Rate(BTU/KWH) |  |  |  | 10213.7001 | 10146.4507 | 11144.1753 | 10306.9186
2. | Generation Data
| Gross Generation MWH |  | 31930 | 205913 | 92553 | 638005 | 1743 | 29609
| Net Generation MWH |  |  |  | 90510 | 622298 | 1734 | 29428
| Station Service MWH |  |  |  | 2043 | 15707 | 9 | 181
| % Station Service |  |  |  | 2.2074 | 2.4619 | 0.51635 | 0.6113
3. | Availability Data
| Period Hours |  | 720 | 6552 | 2160 | 19656 | 720 | 2928
| Hours in Service |  | 720 | 5526 | 2129 | 14604 | 24 | 1055
| Available Hours |  | 720 | 5526 | 2129 | 15299 | 596 | 2804
| Forced Outage Hours |  | 0 | 760 | 31 | 950 | 0 | 0
| Planned Outage Hours |  | 0 | 243 | 0 | 3286 | 0 | 0
| Maintenance Outage Hours |  | 0 | 23 | 0 | 121 | 124 | 124
4. | Fuel Data
| Gas MMBTU Burned |  |  |  | 924442 | 6314116 | 19324 | 303312
| Oil Barrels Burned |  |  |  | 0 | 0 | 0 | 0
| Oil MMBTU Burned |  |  |  | 0 | 0 | 0 | 0
5.* | Cost of Fuel and Maintenance
Fuel, $ per MWH
Unit O&M, $ per MWH
Total, $ per MWH
|  |  | Newman Unit 5GT-4 |  | Newman Unit 5 Total |  | Newman Total
|  |  | MTH | YTD | MTH | YTD | MTH | YTD
1. | Performance Factors
| Net Capacity Factor % |  | 2.1 | 15.7 | 2.8 | 15.2 | 38.0784 | 37.4067
| Equivalent Availability Factor % |  | 81.4 | 93.1 | 82.8 | 94.6 | 95.4 | 89.518
| Availability Factor % |  | 81.4 | 93.1 | 82.8 | 94.6 | 95.5185 | 92.5159
| Equivalent Forced Outage Rate % |  | 0 | 0 | 0 | 0 | 0.6922 | 2.6373
| Forced Outage Rate % |  | 0 | 0 | 0 | 0 | 0.6922 | 1.8808
| Scheduled Outage Rate % |  | 18.6111 | 6.8648 | 17.9167 | 5.5499 | 4.4792 | 10.5871
| Average Load % |  | 51.7368 | 64.2495 | 63.3953 | 39.3965 | 45.5969 | 45.6306
| Gross Heat Rate(BTU/KWH) |  | 12101.7294 | 10249.3528 | 11452.6779 | 10246.6908 | 10261.1843 | 10262.4477
| Net Heat Rate(BTU/KWH) |  | 12163.5992 | 10316.1152 | 11511.7994 | 10311.6144 | 10733.9713 | 10789.4299
2. | Generation Data
| Gross Generation MWH |  | 983 | 30904 | 2726 | 60513 | 169210 | 1520276
| Net Generation MWH |  | 978 | 30704 | 2712 | 60132 | 161757 | 1446022
| Station Service MWH |  | 5 | 200 | 14 | 381 | 7453 | 74254
| % Station Service |  | 0.50865 | 0.64717 | 0.51357 | 0.62962 | 4.4046 | 4.8842
3. | Availability Data
| Period Hours |  | 720 | 2928 | 1440 | 5856 | 5760 | 45168
| Hours in Service |  | 19 | 481 | 43 | 1536 | 3711 | 33317
| Available Hours |  | 586 | 2727 | 1182 | 5531 | 5459 | 39337
| Forced Outage Hours |  | 0 | 0 | 0 | 0 | 43 | 1049
| Planned Outage Hours |  | 0 | 0 | 0 | 0 | 0 | 3844
| Maintenance Outage Hours |  | 134 | 201 | 258 | 325 | 258 | 938
4. | Fuel Data
| Gas MMBTU Burned |  | 11896 | 316746 | 31220 | 620058 | 1736295 | 15601753
| Oil Barrels Burned |  | 0 | 0 | 0 | 0 | 0 | 0
| Oil MMBTU Burned |  | 0 | 0 | 0 | 0 | 0 | 0
5.* | Cost of Fuel and Maintenance
| Fuel, $ per MWH | [5 empty] | 51.31 | 58.25
| Unit O&M, $ per MWH | [5 empty] | 9.19 | 7.25
| Total, $ per MWH | [5 empty] | 60.5 | 65.5
|  |  | Copper Unit 1 |  | Total Local Units
|  |  | MTH | YTD | MTH | YTD
1. | Performance Factors
| Net Capacity Factor % |  | 0 | 3.6 | 31.6955 | 31.1071
| Equivalent Availability Factor % |  | 100 | 85 | 95.9 | 82.2423
| Availability Factor % |  | 100 | 85.2 | 95.9806 | 84.4156
| Equivalent Forced Outage Rate % |  | 0 | 0.3 | 0.6 | 2.2205
| Forced Outage Rate % |  | 0 | 0 | 0.46356 | 1.3848
| Scheduled Outage Rate % |  | 0 | 14.8199 | 3.5301 | 14.4909
| Average Load % |  | 0 | 33.484 | 48.492 | 44.3591
| Gross Heat Rate(BTU/KWH) |  | 0 | 12661.2573 | 10342.1861 | 10373.4314
| Net Heat Rate(BTU/KWH) |  | 0 | 12664.7115 | 10935.7079 | 10985.7273
2. | Generation Data
| Gross Generation MWH |  | 0 | 14666 | 212589 | 1901586
| Net Generation MWH |  | 0 | 14662 | 201051 | 1795600
| Station Service MWH |  | 0 | 4 | 11538 | 105986
| % Station Service |  | 0 | 0.027274 | 5.4274 | 5.5736
3. | Availability Data
| Period Hours |  | 720 | 6552 | 8640 | 71376
| Hours in Service |  | 0 | 438 | 4384 | 42868
| Available Hours |  | 720 | 5580 | 8292 | 59828
| Forced Outage Hours |  | 0 | 1 | 43 | 1205
| Planned Outage Hours |  | 0 | 963 | 0 | 8953
| Maintenance Outage Hours |  | 0 | 8 | 305 | 1390
4. | Fuel Data
| Gas MMBTU Burned |  | 0 | 185690 | 2198635 | 19725972
| Oil Barrels Burned |  | 0 | 0 | 0 | 0
| Oil MMBTU Burned |  | 0 | 0 | 0 | 0
5.* | Cost of Fuel and Maintenance
| Fuel, $ per MWH |  | 33340 | 62.42 | 54.91 | 60
| Unit O&M, $ per MWH |  | 22827 | 17.21
| Total O&M, $ per MWH |  |  |  | 10.63 | 10.98
| Total , $ per MWH |  | 56167 | 79.63 | 65.54 | 70.98