## RGD6
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 1 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
RIO GRANDE UNIT 6
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 0 | 62 | -62 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Feb | 0 | 39 | -39 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Mar | 0 | 72 | -72 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Apr | 0 | 74 | -74 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
May | 0 | 81 | -81 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Jun | 0 | 49 | -49 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Jul | 0 | 64 | -64 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Aug | 0 | 87 | -87 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Sep | 0 | 83 | -83 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Oct | 0 | 83 | -83 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Nov | 0 | 81 | -81 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Dec | 0 | 83 | -83 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Total | 0 | 858 | -858 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
Rio Grande Unit 6 was in inactive reserve status for all of 2020.
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 1 OF 20

## RGD7
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 2 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
RIO GRANDE UNIT 7
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 0 | 84 | -84 | 0 | 100 | 0 | -0.24 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Feb | 0 | 78 | -78 | 0 | 100 | 0 | -0.23 | NA | 1 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Mar | 0 | 71 | -71 | 0 | 100 | 0 | -0.2 | NA | 0 | 1 | 0 | N/A | N/A | 0 | 0 | 0
Apr | 0 | 60 | -60 | 0 | 100 | 0 | -0.17 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
May | 5480 | 470 | 5010 | 31.72 | 68.28 | 0 | 15.3 | NA | 1 | 0 | 236 | N/A | N/A | 65.785 | 65.785 | 13130.7385
Jun | 16922 | 1215 | 15707 | 96.83 | 3.17 | 0 | 49.58 | NA | 0 | 2 | 697.2 | N/A | N/A | 202.202 | 202.202 | 12873.3686
Jul | 7378 | 547 | 6831 | 38.42 | 61.17 | 0 | 20.87 | NA | 0 | 1 | 288.88 | N/A | N/A | 90.646 | 90.646 | 13269.7994
Aug | 17900 | 1235 | 16665 | 93.36 | 5.39 | 0 | 50.91 | NA | 1 | 2 | 703.87 | N/A | N/A | 228.624 | 228.624 | 13718.8119
Sep | 15809 | 1197 | 14612 | 100 | 0 | 0 | 46.12 | NA | 0 | 0 | 720 | N/A | N/A | 200.205 | 200.205 | 13701.4098
Oct | 17007 | 1220 | 15787 | 100 | 0 | 0 | 44.21 | NA | 0 | 0 | 744 | N/A | N/A | 205.904 | 205.904 | 13042.63
Nov | 15805 | 1146 | 14659 | 100 | 0 | 0 | 42.42 | NA | 0 | 0 | 720 | N/A | N/A | 192.71 | 192.71 | 13146.1901
Dec | 7252 | 578 | 6674 | 86.67 | 0 | 13.33 | 18.69 | NA | 0 | 1 | 331.6 | N/A | N/A | 85.003 | 85.003 | 12736.4399
Total | 103553 | 7901 | 95652 | 53.9167 | 44.8342 | 1.1108 | 23.9383 | N/A | 3 | 7 | 4441.55 | N/A | N/A | 1271.079 | 1271.079 | 13288.5773
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 2 OF 20

## RGD8
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 3 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
RIO GRANDE UNIT 8
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 14924 | 1481 | 13443 | 30.14 | 0 | 67.74 | 12.29 | NA | 0 | 0 | 240 | N/A | N/A | 159.11 | 159.11 | 11835.8997
Feb | 24456 | 2053 | 22403 | 35.94 | 0 | 64.06 | 21.9 | NA | 1 | 0 | 250.17 | N/A | N/A | 275.711 | 275.711 | 12306.8785
Mar | 57533 | 4262 | 53271 | 84.62 | 15.38 | 0 | 48.71 | NA | 0 | 1 | 629.6 | N/A | N/A | 631.596 | 631.596 | 11856.282
Apr | 60640 | 4501 | 56139 | 91.26 | 0 | 5.6 | 53.04 | NA | 1 | 1 | 679.7 | N/A | N/A | 654.449 | 654.449 | 11657.6533
May | 57629 | 4447 | 53182 | 89.98 | 7.58 | 2.47 | 51.43 | NA | 0 | 1 | 670.63 | N/A | N/A | 626.2 | 626.2 | 11774.6606
Jun | 461 | 292 | 169 | 1.14 | 98.86 | 0 | 0.17 | NA | 1 | 0 | 8.2 | N/A | N/A | 12.153 | 12.153 | 71911.2426
Jul | 53405 | 4121 | 49284 | 81.01 | 18.79 | 0 | 47.66 | NA | 1 | 5 | 604.18 | N/A | N/A | 596.893 | 596.893 | 12111.2937
Aug | 62480 | 4718 | 57762 | 92.03 | 0.28 | 7.72 | 55.85 | NA | 0 | 2 | 684.68 | N/A | N/A | 691.11 | 691.11 | 11964.7865
Sep | 65985 | 4878 | 61107 | 99.63 | 0.38 | 0 | 61.06 | NA | 0 | 1 | 717.3 | N/A | N/A | 727.905 | 727.905 | 11911.9741
Oct | 53549 | 4269 | 49280 | 85.94 | 7.9 | 6.69 | 45.06 | NA | 1 | 0 | 639.42 | N/A | N/A | 560.574 | 560.574 | 11375.2841
Nov | 42103 | 3563 | 38540 | 76.49 | 0 | 23.51 | 36.41 | NA | 1 | 0 | 550.7 | N/A | N/A | 451.502 | 451.502 | 11715.1531
Dec | 56044 | 4546 | 51498 | 95.51 | 4.49 | 0 | 47.09 | NA | 1 | 1 | 710.6 | N/A | N/A | 587.172 | 587.172 | 11401.8408
Total | 549209 | 43131 | 506078 | 71.9742 | 12.805 | 14.8158 | 40.0558 | N/A | 7 | 12 | 6385.18 | N/A | N/A | 5974.375 | 5974.375 | 11805.2454
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 3 OF 20

## RGD9
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 4 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
RIO GRANDE UNIT 9
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 21232 | 542 | 20690 | 94.44 | 0 | 0 | 30.9 | NA | 0 | 1 | 440.52 | N/A | N/A | 238.255 | 238.255 | 11515.4664
Feb | 37454 | 771 | 36683 | 88.82 | 0 | 4.45 | 58.56 | NA | 0 | 0 | 600.77 | N/A | N/A | 374.677 | 374.677 | 10213.9138
Mar | 14511 | 316 | 14195 | 75.49 | 0 | 20.07 | 21.2 | NA | 0 | 1 | 240.25 | N/A | N/A | 149.979 | 149.979 | 10565.6217
Apr | 14004 | 240 | 13764 | 50.28 | 0 | 46.76 | 21.24 | NA | 0 | 1 | 178.83 | N/A | N/A | 137.876 | 137.876 | 10017.1462
May | 42086 | 895 | 41191 | 88.87 | 0.68 | 5.13 | 62.91 | NA | 0 | 4 | 698.17 | N/A | N/A | 419.475 | 419.475 | 10183.6566
Jun | 41387 | 923 | 40464 | 92.45 | 0 | 1.98 | 63.86 | NA | 0 | 2 | 705.73 | N/A | N/A | 437.295 | 437.295 | 10807.0136
Jul | 58311 | 1001 | 57310 | 91.02 | 0.1 | 3.4 | 87.53 | NA | 0 | 2 | 717.97 | N/A | N/A | 492.324 | 492.324 | 8590.5427
Aug | 42741 | 975 | 41766 | 84.67 | 0 | 9.1 | 63.79 | NA | 0 | 1 | 676.27 | N/A | N/A | 440.571 | 440.571 | 10548.5562
Sep | 16447 | 361 | 16086 | 42.66 | 0 | 55.69 | 25.39 | NA | 0 | 0 | 248.73 | N/A | N/A | 162.551 | 162.551 | 10105.1225
Oct | 0 | 0 | 0 | 0 | 0 | 100 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0.011 | 0.011 | 0
Nov | 0 | 0 | 0 | 0 | 0 | 100 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0.03 | 0.03 | 0
Dec | 0 | 0 | 0 | 0 | 0 | 100 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0.053 | 0.053 | 0
Total | 288173 | 6024 | 282149 | 59.0583 | 0.065 | 37.215 | 36.2817 | N/A | 0 | 12 | 4507.24 | N/A | N/A | 2853.097 | 2853.097 | 10112.0224
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 4 OF 20

## NWM1
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 5 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
NEWMAN UNIT 1
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 3113 | 531 | 2582 | 28.91 | 0 | 71.09 | 4.45 | NA | 1 | 0 | 79.28 | N/A | N/A | 30.479 | 30.479 | 11804.4152
Feb | 33431 | 2229 | 31202 | 98.21 | 0 | 1.79 | 57.47 | NA | 0 | 0 | 683.52 | N/A | N/A | 403.165 | 403.165 | 12921.1269
Mar | 0 | 319 | -319 | 71.64 | 0 | 28.36 | -0.55 | NA | 1 | 0 | 0 | N/A | N/A | 3.499 | 3.499 | 0
Apr | 15769 | 1414 | 14355 | 97.13 | 0 | 0 | 25.56 | NA | 1 | 0 | 194.47 | N/A | N/A | 184.33 | 184.33 | 12840.822
May | 33136 | 2397 | 30739 | 99.79 | 0 | 0 | 55.83 | NA | 0 | 0 | 744 | N/A | N/A | 378.741 | 378.741 | 12321.1881
Jun | 34314 | 2383 | 31931 | 100 | 0 | 0 | 59.93 | NA | 0 | 0 | 720 | N/A | N/A | 386.403 | 386.403 | 12101.1869
Jul | 19398 | 1521 | 17877 | 51.18 | 26.78 | 30.11 | 32.47 | NA | 1 | 1 | 380.75 | N/A | N/A | 230.113 | 230.113 | 12872.0143
Aug | 6355 | 727 | 5628 | 17.5 | 82.5 | 0 | 10.22 | NA | 1 | 0 | 130.17 | N/A | N/A | 76.85 | 76.85 | 13654.9396
Sep | 33431 | 2302 | 31129 | 100 | 0 | 0 | 58.43 | NA | 0 | 0 | 720 | N/A | N/A | 384.835 | 384.835 | 12362.5879
Oct | 19928 | 1496 | 18432 | 57.69 | 0 | 42.31 | 31.76 | NA | 0 | 0 | 429.25 | N/A | N/A | 220.146 | 220.146 | 11943.6849
Nov | 12575 | 1241 | 11334 | 91.27 | 15.87 | 0.56 | 20.18 | NA | 2 | 6 | 311.68 | N/A | N/A | 130.897 | 130.897 | 11549.0559
Dec | 22522 | 1606 | 20916 | 98.68 | 1.4 | 0 | 36.04 | NA | 0 | 2 | 473.12 | N/A | N/A | 253.844 | 253.844 | 12136.3549
Total | 233972 | 18166 | 215806 | 76 | 10.5458 | 14.5183 | 32.6492 | N/A | 7 | 9 | 4866.24 | N/A | N/A | 2683.302 | 2683.302 | 12433.8619
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 5 OF 20

## NWM2
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 6 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
NEWMAN UNIT 2
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 0 | 150 | -150 | 16.13 | 0 | 83.87 | -0.26 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0.866 | 0
Feb | 29460 | 2151 | 27309 | 96.01 | 0 | 3.99 | 50.3 | NA | 0 | 0 | 656.95 | N/A | N/A | 270.674 | 270.674 | 9911.531
Mar | 30328 | 1974 | 28354 | 100 | 0 | 0 | 48.86 | NA | 0 | 0 | 664.75 | N/A | N/A | 338.685 | 338.685 | 11944.8755
Apr | 19789 | 1337 | 18452 | 100 | 0 | 0 | 32.86 | NA | 0 | 0 | 439.48 | N/A | N/A | 213.933 | 213.933 | 11594.0277
May | 33988 | 2166 | 31822 | 100 | 0 | 0 | 57.8 | NA | 0 | 0 | 744 | N/A | N/A | 359.875 | 359.875 | 11309.0001
Jun | 34978 | 2145 | 32833 | 100 | 0 | 0 | 61.62 | NA | 0 | 0 | 720 | N/A | N/A | 374.306 | 374.306 | 11400.2985
Jul | 36545 | 2301 | 34244 | 100 | 0 | 0 | 62.2 | NA | 0 | 0 | 744 | N/A | N/A | 402.06 | 402.06 | 11741.0349
Aug | 36312 | 2239 | 34073 | 100 | 0 | 0 | 61.89 | NA | 0 | 0 | 744 | N/A | N/A | 401.943 | 401.943 | 11796.5251
Sep | 35255 | 2164 | 33091 | 100 | 0 | 0 | 62.11 | NA | 0 | 0 | 720 | N/A | N/A | 382.035 | 382.035 | 11544.982
Oct | 37410 | 2258 | 35152 | 100 | 0 | 0 | 60.57 | NA | 0 | 0 | 744 | N/A | N/A | 383.208 | 383.208 | 10901.4565
Nov | 30464 | 2066 | 28398 | 96.03 | 3.97 | 0 | 50.57 | NA | 0 | 2 | 691.42 | N/A | N/A | 442.812 | 442.812 | 15593.0699
Dec | 37172 | 2184 | 34988 | 100 | 0 | 0 | 60.29 | NA | 0 | 0 | 744 | N/A | N/A | 412.584 | 412.584 | 11792.1573
Total | 361701 | 23135 | 338566 | 92.3475 | 0.33083 | 7.3217 | 50.7342 | N/A | 0 | 2 | 7612.6 | N/A | N/A | 3982.115 | 3982.981 | 11764.2675
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 6 OF 20

## NWM3
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 7 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
NEWMAN UNIT 3
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 0 | 89 | -89 | 7.85 | 0 | 92.2 | -0.12 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0.433 | 0
Feb | 13179 | 1388 | 11791 | 45.91 | 0 | 54.1 | 17.29 | NA | 1 | 0 | 319.52 | N/A | N/A | 133.405 | 133.405 | 11314.1379
Mar | 36158 | 3015 | 33143 | 100 | 0 | 0 | 45.46 | NA | 0 | 0 | 744 | N/A | N/A | 386.213 | 386.213 | 11652.9282
Apr | 37158 | 2754 | 34404 | 100 | 0 | 0 | 48.76 | NA | 0 | 0 | 720 | N/A | N/A | 395.373 | 395.373 | 11492.0649
May | 32894 | 2611 | 30283 | 87.37 | 12.63 | 0 | 43.77 | NA | 1 | 3 | 650.05 | N/A | N/A | 338.493 | 338.493 | 11177.6574
Jun | 29940 | 2321 | 27619 | 77.56 | 22.44 | 0 | 41.25 | NA | 2 | 0 | 558.4 | N/A | N/A | 303.4 | 303.4 | 10985.1914
Jul | 39142 | 2806 | 36336 | 93.71 | 6.29 | 0 | 52.51 | NA | 1 | 0 | 697.2 | N/A | N/A | 415.433 | 415.433 | 11433.0967
Aug | 34940 | 2604 | 32336 | 84.14 | 2.06 | 12.8 | 46.73 | NA | 1 | 2 | 635.75 | N/A | N/A | 376.318 | 376.318 | 11637.7412
Sep | 20142 | 1956 | 18186 | 57.17 | 42.88 | 0 | 27.16 | NA | 3 | 4 | 410.87 | N/A | N/A | 222.253 | 222.253 | 12221.1041
Oct | 31130 | 2483 | 28647 | 81.31 | 18.69 | 0 | 39.29 | NA | 2 | 0 | 604.95 | N/A | N/A | 320.266 | 320.266 | 11179.7396
Nov | 30535 | 2493 | 28042 | 86.98 | 13.02 | 0 | 39.74 | NA | 0 | 1 | 626.25 | N/A | N/A | 309.001 | 309.001 | 11019.2212
Dec | 13640 | 1439 | 12201 | 52.39 | 21.54 | 12 | 16.73 | NA | 2 | 3 | 375.23 | N/A | N/A | 152.769 | 152.769 | 12521.0229
Total | 318858 | 25959 | 292899 | 72.8658 | 11.6292 | 14.2583 | 34.8808 | N/A | 13 | 13 | 6342.22 | N/A | N/A | 3352.924 | 3353.357 | 11448.851
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 7 OF 20

## NWM4
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 8 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
NEWMAN UNIT 4 (GT-1, GT-2, ST)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 92894 | 2054 | 90840 | 99.3651 | 0.6391 | 0 | 52.6279 | NA | 0 | 4 | 740.6 | N/A | N/A | 924.612 | 924.612 | 10178.4676
Feb | 43391 | 1030 | 42361 | 35.7859 | 49.3575 | 12.7 | 26.2343 | NA | 3 | 0 | 431.32 | N/A | N/A | 871.725 | 871.725 | 20578.4802
Mar | 0 | 216 | -216 | 0 | 100 | 87.1 | -0.12514 | NA | 3 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Apr | 19 | 273 | -254 | 0 | 100 | 53.3 | -0.15206 | NA | 4 | 0 | 0 | N/A | N/A | 0 | 0 | 0
May | 42615 | 2585 | 40030 | 34.5757 | 52.1194 | 7.2 | 24.4563 | NA | 10 | 4 | 515.02 | N/A | N/A | 435.441 | 435.441 | 10877.8666
Jun | 97215 | 2293 | 94922 | 78.4231 | 5.5673 | 2.9 | 59.9255 | NA | 3 | 4 | 718.48 | N/A | N/A | 934.563 | 934.563 | 9845.589
Jul | 108386 | 2460 | 105926 | 98.8015 | 0.46136 | 0.3 | 64.7153 | NA | 0 | 6 | 744 | N/A | N/A | 1062.556 | 1062.556 | 10031.1161
Aug | 105558 | 2447 | 103111 | 92.3401 | 1.2141 | 4.4 | 62.9955 | NA | 3 | 4 | 743.18 | N/A | N/A | 1027.27 | 1027.27 | 9962.7586
Sep | 96264 | 2351 | 93913 | 99.9278 | 0.049537 | 0 | 59.2885 | NA | 0 | 1 | 720 | N/A | N/A | 958.772 | 958.772 | 10209.151
Oct | 6141 | 416 | 5725 | 6.1039 | 0 | 93.9 | 3.3168 | NA | 0 | 0 | 45.6 | N/A | N/A | 32.452 | 32.452 | 5668.4716
Nov | 0 | 0 | 0 | 0 | 0 | 100 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Dec | 0 | 0 | 0 | 0 | 0 | 100 | 0 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Total | 592483 | 16125 | 576358 | 45.4436 | 25.784 | 38.4833 | 29.4402 | N/A | 26 | 23 | 4658.2 | N/A | N/A | 6247.391 | 6247.391 | 10839.4279
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 8 OF 20

## NWM5
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 9 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
NEWMAN UNIT 5 (GT-3, GT-4, ST)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 155952 | 214 | 155738 | 99.1237 | 0.25692 | 0.59946 | 77.2418 | NA | 1 | 2 | 744 | N/A | N/A | 1147.111 | 1147.111 | 7365.6461
Feb | 22274 | 199 | 22075 | 13.6887 | 6.1151 | 81.2035 | 11.7037 | NA | 2 | 0 | 165.32 | N/A | N/A | 163.665 | 163.665 | 7414.043
Mar | 141274 | 213 | 141061 | 95.8392 | 3.1272 | 0 | 69.9624 | NA | 2 | 3 | 740.75 | N/A | N/A | 1172.651 | 1172.651 | 8313.0773
Apr | 144154 | 581 | 143573 | 95.5505 | 0.048289 | 2.2097 | 73.5819 | NA | 2 | 0 | 720 | N/A | N/A | 1177.628 | 1177.628 | 8202.2943
May | 140743 | 3165 | 137578 | 95.1416 | 0.092564 | 3.1958 | 68.9988 | NA | 1 | 2 | 743 | N/A | N/A | 1057.993 | 1057.993 | 7690.1321
Jun | 142806 | 3272 | 139534 | 99.9208 | 0.058796 | 0 | 72.3124 | NA | 0 | 1 | 720 | N/A | N/A | 1051.488 | 1051.488 | 7535.7117
Jul | 158524 | 3413 | 155111 | 99.9373 | 0 | 0 | 77.792 | NA | 0 | 0 | 744 | N/A | N/A | 1287.435 | 1287.435 | 8300.0883
Aug | 143736 | 3422 | 140314 | 99.2836 | 0.70296 | 0 | 70.3709 | NA | 1 | 3 | 742.2 | N/A | N/A | 1178.515 | 1178.515 | 8399.1262
Sep | 141080 | 3374 | 137706 | 100 | 0 | 0 | 71.365 | NA | 0 | 0 | 720 | N/A | N/A | 1133.342 | 1133.342 | 8230.157
Oct | 142790 | 3452 | 139338 | 100 | 0 | 0 | 69.1078 | NA | 0 | 0 | 744 | N/A | N/A | 1104.545 | 1104.545 | 7927.091
Nov | 140660 | 3327 | 137333 | 97.4995 | 0.95417 | 0 | 70.3839 | NA | 0 | 2 | 715.48 | N/A | N/A | 1040.067 | 1040.067 | 7573.3218
Dec | 143594 | 2845 | 140749 | 96.4005 | 0.22088 | 0 | 69.8077 | NA | 0 | 1 | 744 | N/A | N/A | 1158.768 | 1158.768 | 8232.8684
Subtotal | 1617587 | 27477 | 1590110 | 91.0321 | 0.96474 | 7.2674 | 66.8857 | N/A | 9 | 14 | 8242.75 | N/A | N/A | 12673.208 | 12673.208 | 7970.0197
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available. October 2015 data substituted with gas pipeline data due to issues with plant meter.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 9 OF 20

## COP1
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 10 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
COPPER
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 185 | 0 | 185 | 100 | 0 | 0 | 0.38 | NA | 2 | 0 | 16.37 | N/A | N/A | 6.126 | 6.126 | 33113.5135
Feb | 4839 | 0 | 4839 | 100 | 0 | 0 | 10.7 | NA | 7 | 0 | 159.65 | N/A | N/A | 92.232 | 92.232 | 19060.1364
Mar | 5380 | 506 | 4874 | 100 | 0 | 0 | 10.08 | NA | 7 | 0 | 209.53 | N/A | N/A | 106.897 | 106.897 | 21932.0886
Apr | 2990 | 330 | 2660 | 57.5 | 0 | 42.5 | 5.68 | NA | 12 | 0 | 161.8 | N/A | N/A | 71.485 | 71.485 | 26874.0602
May | 3324 | 103 | 3221 | 98.19 | 0 | 1.81 | 6.87 | NA | 12 | 0 | 94.52 | N/A | N/A | 63.401 | 63.401 | 19683.6386
Jun | 6550 | 32 | 6518 | 100 | 0 | 0 | 14.37 | NA | 23 | 1 | 214.25 | N/A | N/A | 121.651 | 121.651 | 18663.8539
Jul | 9635 | 27 | 9608 | 91.86 | 1.49 | 0 | 20.5 | NA | 29 | 3 | 278.62 | N/A | N/A | 176.531 | 176.531 | 18373.3347
Aug | 1523 | 16 | 1507 | 12.07 | 93.87 | 0 | 3.22 | NA | 5 | 0 | 41.45 | N/A | N/A | 27.397 | 27.397 | 18179.8275
Sep | 0 | 3 | -3 | 0 | 100 | 0 | -0.01 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Oct | 0 | 5 | -5 | 0 | 100 | 0 | -0.01 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Nov | 0 | 3 | -3 | 0 | 100 | 0 | -0.01 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Dec | 0 | 3 | -3 | 0 | 100 | 0 | -0.01 | NA | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Total | 34426 | 1028 | 33398 | 54.9683 | 41.28 | 3.6925 | 5.98 | N/A | 97 | 4 | 1176.19 | N/A | N/A | 665.72 | 665.72 | 19932.9301
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 10 OF 20

## MPS1
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 11 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
MONTANA UNIT 1
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 14433 | 449 | 13984 | 95.69 | 0.12 | 4.28 | 20.21 | NA | 0 | 27 | 191.69 | N/A | N/A | 133.997 | 133.997 | 9582.1653
Feb | 24038 | 564 | 23474 | 82.41 | 0 | 17.59 | 36.27 | NA | 0 | 25 | 348.08 | N/A | N/A | 225.675 | 225.675 | 9613.8281
Mar | 8246 | 417 | 7829 | 52.83 | 2.45 | 46.68 | 11.31 | NA | 0 | 12 | 143.23 | N/A | N/A | 81.491 | 81.491 | 10408.8645
Apr | 25633 | 524 | 25109 | 99.14 | 0 | 0.86 | 37.5 | NA | 0 | 31 | 392.28 | N/A | N/A | 242.282 | 242.282 | 9649.2094
May | 25175 | 475 | 24700 | 100 | 0 | 0 | 37.73 | NA | 0 | 27 | 338.22 | N/A | N/A | 227.159 | 227.159 | 9196.7206
Jun | 29550 | 566 | 28984 | 100 | 0 | 0 | 45.74 | NA | 0 | 28 | 441.22 | N/A | N/A | 276.343 | 276.343 | 9534.3293
Jul | 36180 | 667 | 35513 | 99.9 | 0.14 | 0 | 54.24 | NA | 0 | 25 | 510.61 | N/A | N/A | 336.097 | 336.097 | 9464.0554
Aug | 36181 | 617 | 35564 | 100 | 0 | 0 | 54.32 | NA | 0 | 28 | 534.27 | N/A | N/A | 334.186 | 334.186 | 9396.7495
Sep | 18890 | 381 | 18509 | 98.9 | 2.8 | 0 | 29.21 | NA | 0 | 23 | 275 | N/A | N/A | 177.923 | 177.923 | 9612.783
Oct | 22070 | 394 | 21676 | 96.02 | 7.2 | 0.27 | 31.33 | NA | 0 | 30 | 355.74 | N/A | N/A | 209.868 | 209.868 | 9682.0447
Nov | 16372 | 307 | 16065 | 88.11 | 0 | 11.89 | 23.99 | NA | 0 | 17 | 246.64 | N/A | N/A | 157.582 | 157.582 | 9809.0258
Dec | 20210 | 347 | 19863 | 88.41 | 0 | 11.59 | 28.71 | NA | 0 | 29 | 304.25 | N/A | N/A | 188.96 | 188.96 | 9513.1652
Total | 276978 | 5708 | 271270 | 91.7842 | 1.0592 | 7.7633 | 34.2133 | N/A | 0 | 302 | 4081.23 | N/A | N/A | 2591.563 | 2591.563 | 9553.4449
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 11 OF 20

## MPS2
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 12 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
MONTANA UNIT 2
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 17776 | 449 | 17327 | 97.03 | 8.47 | 0 | 25.04 | NA | 0 | 18 | 239.1 | N/A | N/A | 162.068 | 162.068 | 9353.4945
Feb | 24505 | 564 | 23941 | 96.99 | 0 | 3.01 | 36.99 | NA | 0 | 25 | 336.06 | N/A | N/A | 226.001 | 226.001 | 9439.9148
Mar | 14810 | 417 | 14393 | 41.04 | 0 | 58.96 | 20.8 | NA | 0 | 9 | 223.03 | N/A | N/A | 140.191 | 140.191 | 9740.2209
Apr | 36701 | 524 | 36177 | 91.42 | 10.02 | 0 | 54.03 | NA | 0 | 12 | 555.2 | N/A | N/A | 343.225 | 343.225 | 9487.3815
May | 20900 | 475 | 20425 | 92.31 | 17.01 | 0 | 31.2 | NA | 0 | 28 | 279.3 | N/A | N/A | 187.355 | 187.355 | 9172.8274
Jun | 25579 | 566 | 25013 | 100 | 0 | 0 | 39.48 | NA | 0 | 29 | 361.82 | N/A | N/A | 235.807 | 235.807 | 9427.3778
Jul | 33849 | 667 | 33182 | 99.44 | 0.42 | 0.3 | 50.68 | NA | 0 | 26 | 462.8 | N/A | N/A | 309.956 | 309.956 | 9341.0885
Aug | 30030 | 617 | 29413 | 100 | 0 | 0 | 44.92 | NA | 0 | 32 | 426.72 | N/A | N/A | 273.376 | 273.376 | 9294.3936
Sep | 18996 | 381 | 18615 | 100 | 0 | 0 | 29.38 | NA | 0 | 21 | 263.53 | N/A | N/A | 176.114 | 176.114 | 9460.8649
Oct | 14023 | 394 | 13629 | 89.51 | 26.97 | 0 | 19.7 | NA | 0 | 21 | 211.33 | N/A | N/A | 130.92 | 130.92 | 9605.9872
Nov | 12467 | 307 | 12160 | 86.86 | 4.95 | 11.82 | 18.16 | NA | 0 | 23 | 181.37 | N/A | N/A | 119.761 | 119.761 | 9848.7664
Dec | 11138 | 347 | 10791 | 88.36 | 0 | 11.64 | 15.6 | NA | 0 | 19 | 174.53 | N/A | N/A | 102.885 | 102.885 | 9534.3342
Total | 260774 | 5708 | 255066 | 90.2467 | 5.6533 | 7.1442 | 32.165 | N/A | 0 | 263 | 3714.79 | N/A | N/A | 2407.659 | 2407.659 | 9439.3569
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 12 OF 20

## MPS3
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 13 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
MONTANA UNIT 3
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 2999 | 449 | 2550 | 89.06 | 2.79 | 10.75 | 3.69 | N/A | N/A | 18 | 48.1 | N/A | N/A | 29.93 | 29.93 | 11737.2549
Feb | 8432 | 564 | 7868 | 98.37 | 0 | 1.63 | 12.16 | N/A | N/A | 16 | 138.97 | N/A | N/A | 84.736 | 84.736 | 10769.7001
Mar | 10658 | 417 | 10241 | 100 | 0 | 0 | 14.8 | N/A | N/A | 22 | 176.07 | N/A | N/A | 109.795 | 109.795 | 10721.121
Apr | 8132 | 524 | 7608 | 49.5 | 31.19 | 41.62 | 11.36 | N/A | N/A | 14 | 141.17 | N/A | N/A | 82.071 | 82.071 | 10787.4606
May | 11619 | 475 | 11144 | 100 | 0 | 0 | 17.02 | N/A | N/A | 15 | 179.6 | N/A | N/A | 110.658 | 110.658 | 9929.8277
Jun | 13209 | 566 | 12643 | 98.66 | 0 | 1.34 | 19.95 | N/A | N/A | 25 | 231.9 | N/A | N/A | 133.807 | 133.807 | 10583.4849
Jul | 16070 | 667 | 15403 | 94.32 | 11.2 | 1.27 | 23.53 | N/A | N/A | 27 | 260.35 | N/A | N/A | 158.255 | 158.255 | 10274.2972
Aug | 21100 | 617 | 20483 | 94.51 | 10.92 | 0 | 31.29 | N/A | 0 | 12 | 333.45 | N/A | N/A | 200.257 | 200.257 | 9776.7417
Sep | 7147 | 381 | 6766 | 79.28 | 39.48 | 10 | 10.68 | N/A | 0 | 15 | 118.28 | N/A | N/A | 70.397 | 70.397 | 10404.5226
Oct | 0 | 394 | -394 | 0 | 0 | 100 | -0.57 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Nov | 0 | 307 | -307 | 0 | 0 | 100 | -0.46 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Dec | 0 | 347 | -347 | 0 | 0 | 100 | -0.5 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Total | 99366 | 5708 | 93658 | 66.975 | 7.965 | 30.5508 | 11.9125 | N/A | 0 | 164 | 1627.89 | N/A | N/A | 979.906 | 979.906 | 10462.598
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 13 OF 20

## MPS4
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 14 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
MONTANA UNIT 4
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 26170 | 449 | 25721 | 98.75 | 2.56 | 0 | 37.17 | N/A | N/A | 32 | 353.45 | N/A | N/A | 237.579 | 237.579 | 9236.7715
Feb | 34297 | 564 | 33733 | 99.08 | 0 | 0.92 | 52.12 | N/A | N/A | 17 | 493.38 | N/A | N/A | 315.116 | 315.116 | 9341.4757
Mar | 29193 | 417 | 28776 | 99.82 | 0.3 | 0 | 41.59 | N/A | N/A | 21 | 441.97 | N/A | N/A | 274.314 | 274.314 | 9532.7356
Apr | 17497 | 524 | 16973 | 56.44 | 0 | 43.56 | 25.35 | N/A | N/A | 17 | 261.43 | N/A | N/A | 163.094 | 163.094 | 9609.0261
May | 19014 | 475 | 18539 | 99.36 | 0 | 0.64 | 28.32 | N/A | N/A | 18 | 254.88 | N/A | N/A | 167.772 | 167.772 | 9049.6791
Jun | 23310 | 566 | 22744 | 98.4 | 3.31 | 0 | 35.9 | N/A | N/A | 27 | 336.65 | N/A | N/A | 214.586 | 214.586 | 9434.84
Jul | 29258 | 667 | 28591 | 98.56 | 0.65 | 1.08 | 43.67 | N/A | N/A | 28 | 414.38 | N/A | N/A | 268.603 | 268.603 | 9394.6697
Aug | 22761 | 617 | 22144 | 99.63 | 0.04 | 0.35 | 33.82 | N/A | N/A | 30 | 338 | N/A | N/A | 208.37 | 208.37 | 9409.7724
Sep | 15705 | 381 | 15324 | 90.5 | 1.04 | 9.17 | 24.19 | N/A | N/A | 22 | 226.21 | N/A | N/A | 145.535 | 145.535 | 9497.1939
Oct | 14506 | 394 | 14112 | 88.48 | 1.29 | 11.12 | 20.4 | N/A | N/A | 24 | 229.51 | N/A | N/A | 135.94 | 135.94 | 9632.9365
Nov | 11795 | 307 | 11488 | 88.57 | 0.91 | 11.22 | 17.16 | N/A | N/A | 12 | 169.2 | N/A | N/A | 111.394 | 111.394 | 9696.5529
Dec | 12395 | 347 | 12048 | 88.43 | 0 | 11.57 | 17.41 | N/A | 0 | 21 | 190.79 | N/A | N/A | 112.961 | 112.961 | 9375.913
Total | 255901 | 5708 | 250193 | 92.1683 | 0.84167 | 7.4692 | 31.425 | N/A | 0 | 269 | 3709.85 | N/A | N/A | 2355.264 | 2355.264 | 9413.7886
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 14 OF 20

## GAS
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 15 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
GAS UNITS
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 349678 | 7003 | 342675 | 73.7 | 11.7 | 19.5 | 31.1 | NA | 54 | 102 | 3093.11 | N/A | N/A | 3069.267 | 3069.267 | 8956.787
Feb | 299756 | 12194 | 287562 | 55.1 | 23.4 | 25.5 | 27.9 | NA | 48 | 83 | 4583.71 | N/A | N/A | 3436.782 | 3436.782 | 11951.447
Mar | 348091 | 12632 | 335459 | 65.5 | 17.8 | 24.4 | 30.5 | NA | 56 | 70 | 4213.18 | N/A | N/A | 3395.311 | 3395.311 | 10121.3889
Apr | 382486 | 13660 | 368826 | 61.8 | 24.1 | 20.4 | 34.6 | NA | 51 | 76 | 4444.36 | N/A | N/A | 3665.746 | 3665.746 | 9938.9577
May | 468603 | 20820 | 447783 | 81.3 | 18 | 2.4 | 42.5 | NA | 58 | 102 | 6147.39 | N/A | N/A | 4438.348 | 4438.348 | 9911.8278
Jun | 496221 | 17189 | 479032 | 85.6 | 10.1 | 0.7 | 47 | NA | 81 | 119 | 6433.85 | N/A | N/A | 4684.004 | 4684.004 | 9778.0608
Jul | 606081 | 20929 | 585152 | 90.4 | 7.9 | 2.2 | 55.6 | NA | 87 | 124 | 6847.74 | N/A | N/A | 5826.902 | 5826.902 | 9957.9289
Aug | 561617 | 20938 | 540679 | 85.8 | 12.7 | 2.5 | 51.4 | NA | 54 | 116 | 6734.01 | N/A | N/A | 5464.787 | 5464.787 | 10107.267
Sep | 485151 | 20193 | 464958 | 83.6 | 11.4 | 4.4 | 45.6 | NA | 40 | 87 | 5859.92 | N/A | N/A | 4741.867 | 4741.867 | 10198.4846
Oct | 358554 | 17258 | 341296 | 59.8 | 14.2 | 31.9 | 31 | NA | 27 | 75 | 4747.8 | N/A | N/A | 3303.834 | 3303.834 | 9680.26
Nov | 312776 | 15148 | 297628 | 57.3 | 14.2 | 32.9 | 28 | NA | 15 | 63 | 4212.74 | N/A | N/A | 2955.756 | 2955.756 | 9931.0414
Dec | 323967 | 14672 | 309295 | 59.4 | 13.9 | 32.9 | 28.1 | NA | 24 | 77 | 4048.12 | N/A | N/A | 3054.999 | 3054.999 | 9877.2984
Total | 4992981 | 192636 | 4800345 | 71.6083 | 14.95 | 16.6417 | 37.775 | N/A | 595 | 1094 | 61365.93 | N/A | N/A | 48037.603 | 48037.603 | 10007.1147
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 15 OF 20

## PV1
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 16 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
PALO VERDE UNIT 1 (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) (C ) | [7 empty] | FUEL CONSUMPTION (D) |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 165712.928 | 8498.928 | 157214 | 99.8 | 0 | 0 | 102 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.2054 | 1598.2054 | 10165.8051
Feb | 154640.604 | 8017.604 | 146623 | 99.6 | 0 | 0 | 101.7 | N/A | 0 | 0 | 696 | N/A | N/A | 1495.325 | 1495.325 | 10198.4533
Mar | 165231.344 | 8598.344 | 156633 | 99.5 | 0 | 0 | 101.6 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.5083 | 1597.5083 | 10199.0334
Apr | 160215.95 | 8394.95 | 151821 | 99.7 | 0 | 0 | 101.8 | N/A | 0 | 0 | 720 | N/A | N/A | 1547.0286 | 1547.0286 | 10189.8403
May | 164838.872 | 8556.872 | 156282 | 99.3 | 0 | 0 | 101.4 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.3084 | 1598.3084 | 10227.0927
Jun | 158964.906 | 8254.906 | 150710 | 99 | 0 | 0 | 101.1 | N/A | 0 | 0 | 720 | N/A | N/A | 1545.8824 | 1545.8824 | 10257.3485
Jul | 162969.574 | 8532.574 | 154437 | 98.2 | 0 | 0 | 100.2 | N/A | 0 | 0 | 744 | N/A | N/A | 1596.6927 | 1596.6927 | 10338.7723
Aug | 162267.264 | 8542.264 | 153725 | 97.8 | 0 | 0 | 99.7 | N/A | 0 | 0 | 744 | N/A | N/A | 1593.1302 | 1593.1302 | 10363.5254
Sep | 158287.718 | 8291.718 | 149996 | 98.5 | 0 | 0 | 100.6 | N/A | 0 | 0 | 720 | N/A | N/A | 1544.9945 | 1544.9945 | 10300.2101
Oct | 45634.508 | 2998.508 | 42636 | 27.5 | 0 | 71 | 27.7 | N/A | 0 | 0 | 216 | N/A | N/A | 444.3703 | 444.3703 | 10422.3407
Nov | 0 | 0 | 0 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Dec | 139061.962 | 7818.962 | 131243 | 83.8 | 0 | 10.2 | 85.2 | N/A | 1 | 0 | 677.88 | N/A | N/A | 1373.3123 | 1373.3123 | 10463.9171
Total | 1637825.63 | 86505.63 | 1551320 | 83.5583 | 0 | 15.1 | 85.25 | N/A | 1 | 0 | 7469.88 | N/A | N/A | 15934.7579 | 15934.7579 | 10271.7414
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
ERRATA NO. 2 SCHEDULE H-12.3a PAGE 16 OF 20

## PV2
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 17 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
PALO VERDE UNIT 2 (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) (C ) | [7 empty] | FUEL CONSUMPTION (D) |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 165622.868 | 8009.868 | 157613 | 99.6 | 0 | 0 | 102 | N/A | 0 | 0 | 744 | N/A | N/A | 1596.9407 | 1596.9407 | 10132.0414
Feb | 155172.906 | 7913.906 | 147259 | 99.9 | 0 | 0 | 101.9 | N/A | 0 | 0 | 696 | N/A | N/A | 1494.5918 | 1494.5918 | 10149.4098
Mar | 138261.376 | 8030.376 | 130231 | 83.2 | 13.1 | 0 | 84.3 | N/A | 0 | 1 | 646.17 | N/A | N/A | 1352.0473 | 1352.0473 | 10381.9347
Apr | 15551.94 | 1517.94 | 14034 | 9.7 | 0 | 90 | 9.4 | N/A | 0 | 0 | 71.87 | N/A | N/A | 151.393 | 151.393 | 10787.7021
May | 134443.464 | 7837.464 | 126606 | 80.9 | 0 | 14.7 | 82 | N/A | 1 | 0 | 640.5 | N/A | N/A | 1317.9195 | 1317.9195 | 10409.6131
Jun | 159003.458 | 8195.458 | 150808 | 98.9 | 0 | 0 | 100.9 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.063 | 1546.063 | 10251.8965
Jul | 163475.806 | 8490.806 | 154985 | 98.4 | 0 | 0 | 100.3 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.586 | 1597.586 | 10308.0339
Aug | 163168.97 | 8510.97 | 154658 | 98.2 | 0 | 0 | 100.1 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.0194 | 1598.0194 | 10332.5984
Sep | 158721.744 | 8131.744 | 150590 | 98.7 | 0 | 0 | 100.7 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.6517 | 1546.6517 | 10270.624
Oct | 165163.562 | 8354.562 | 156809 | 99.4 | 0 | 0 | 101.5 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.8437 | 1597.8437 | 10189.7488
Nov | 160680.312 | 8084.312 | 152596 | 100 | 0 | 0 | 102.1 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.0889 | 1546.0889 | 10131.923
Dec | 165636.14 | 8136.14 | 157500 | 99.7 | 0 | 0 | 102 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.7148 | 1597.7148 | 10144.2351
Total | 1744902.546 | 91213.546 | 1653689 | 88.8833 | 1.0917 | 8.725 | 90.6 | N/A | 1 | 1 | 7934.54 | N/A | N/A | 16942.8598 | 16942.8598 | 10245.4934
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
[8 empty] | ` | [5 empty] | ERRATA NO. 2 SCHEDULE H-12.3a PAGE 17 OF 20

## PV3
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 18 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
PALO VERDE UNIT 3 (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) (C ) | [7 empty] | FUEL CONSUMPTION (D) |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 163865.276 | 8485.276 | 155380 | 98.7 | 0 | 0 | 100.7 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.9418 | 1597.9418 | 10284.0697
Feb | 106250.26 | 6457.26 | 99793 | 68.4 | 28.3 | 0 | 69.2 | N/A | 1 | 0 | 499.02 | N/A | N/A | 1041.7547 | 1041.7547 | 10439.1433
Mar | 163430.934 | 8497.934 | 154933 | 98.4 | 0 | 0 | 100.5 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.4119 | 1598.4119 | 10316.7888
Apr | 158443.19 | 8408.19 | 150035 | 98.6 | 0 | 0 | 100.5 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.6361 | 1546.6361 | 10308.5281
May | 163346.72 | 8691.72 | 154655 | 98.3 | 0 | 0 | 100.3 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.4065 | 1598.4065 | 10335.2908
Jun | 157419.666 | 8390.666 | 149029 | 97.9 | 0 | 0 | 99.8 | N/A | 0 | 0 | 720 | N/A | N/A | 1545.5675 | 1545.5675 | 10370.9076
Jul | 162049.856 | 8678.856 | 153371 | 97.6 | 0 | 0 | 99.4 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.2157 | 1598.2157 | 10420.5964
Aug | 161854.726 | 8707.726 | 153147 | 97.4 | 0 | 0 | 99.3 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.1483 | 1598.1483 | 10435.4166
Sep | 157528.212 | 8397.212 | 149131 | 98 | 0 | 0 | 99.9 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.6307 | 1546.6307 | 10370.9851
Oct | 163642.97 | 8667.97 | 154975 | 98.5 | 0 | 0 | 100.5 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.1337 | 1598.1337 | 10312.1737
Nov | 158467.838 | 8398.838 | 150069 | 98.6 | 0 | 0 | 100.5 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.0215 | 1546.0215 | 10302.0556
Dec | 164271.652 | 8511.652 | 155760 | 98.9 | 0 | 0 | 101 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.0243 | 1598.0243 | 10259.5122
Total | 1880571.3 | 100293.3 | 1780278 | 95.775 | 2.3583 | 0 | 97.6333 | N/A | 1 | 0 | 8587.02 | N/A | N/A | 18413.8926 | 18413.8926 | 10343.2681
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
[8 empty] | ` | [5 empty] | ERRATA NO. 2 SCHEDULE H-12.3a PAGE 18 OF 20

## NUCLEAR
EL PASO ELECTRIC COMPANY | [14 empty] | ERRATA NO. 2
2021 TEXAS RATE CASE FILING | [14 empty] | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA | [14 empty] | PAGE 19 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
NUCLEAR UNITS (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) (C ) | [7 empty] | FUEL CONSUMPTION (D) |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
TEST YEAR (TY)
Jan 2020 | 495201.072 | 24994.072 | 470207 | 99.3667 | 0 | 0 | 101.5667 | N/A | 0 | 0 | 2232 | N/A | N/A | 4793.0879 | 4793.0879 | 10193.5698
Feb | 416063.77 | 22388.77 | 393675 | 89.3 | 9.4333 | 0 | 90.9333 | N/A | 1 | 0 | 1891.02 | N/A | N/A | 4031.6714 | 4031.6714 | 10241.1162
Mar | 466923.654 | 25126.654 | 441797 | 93.7 | 4.3667 | 0 | 95.4667 | N/A | 0 | 1 | 2134.17 | N/A | N/A | 4547.9676 | 4547.9676 | 10294.2473
Apr | 334211.08 | 18321.08 | 315890 | 69.3333 | 0 | 30 | 70.5667 | N/A | 0 | 0 | 1511.87 | N/A | N/A | 3245.0576 | 3245.0576 | 10272.7457
May | 462629.056 | 25086.056 | 437543 | 92.8333 | 0 | 4.9 | 94.5667 | N/A | 1 | 0 | 2128.5 | N/A | N/A | 4514.6344 | 4514.6344 | 10318.1503
Jun | 475388.03 | 24841.03 | 450547 | 98.6 | 0 | 0 | 100.6 | N/A | 0 | 0 | 2160 | N/A | N/A | 4637.5129 | 4637.5129 | 10293.0725
Jul | 488495.236 | 25702.236 | 462793 | 98.0667 | 0 | 0 | 99.9667 | N/A | 0 | 0 | 2232 | N/A | N/A | 4792.4943 | 4792.4943 | 10355.5894
Aug | 487290.96 | 25760.96 | 461530 | 97.8 | 0 | 0 | 99.7 | N/A | 0 | 0 | 2232 | N/A | N/A | 4789.2979 | 4789.2979 | 10377.0023
Sep | 474537.674 | 24820.674 | 449717 | 98.4 | 0 | 0 | 100.4 | N/A | 0 | 0 | 2160 | N/A | N/A | 4638.2769 | 4638.2769 | 10313.7681
Oct | 374441.04 | 20021.04 | 354420 | 75.1333 | 0 | 23.6667 | 76.5667 | N/A | 0 | 0 | 1704 | N/A | N/A | 3640.3477 | 3640.3477 | 10271.2817
Nov | 319148.15 | 16483.15 | 302665 | 66.2 | 0 | 33.3333 | 67.5333 | N/A | 0 | 0 | 1440 | N/A | N/A | 3092.1104 | 3092.1104 | 10216.2799
Dec | 468969.754 | 24466.754 | 444503 | 94.1333 | 0 | 3.4 | 96.0667 | N/A | 1 | 0 | 2165.88 | N/A | N/A | 4569.0514 | 4569.0514 | 10279.0114
Subtotal | 5263299.476 | 278012.476 | 4985287 | 89.4056 | 1.15 | 7.9417 | 91.1611 | N/A | 3 | 1 | 23991.44 | N/A | N/A | 51291.5103 | 51291.5103 | 10288.5772
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
[8 empty] | ` | [5 empty] | ERRATA NO. 2 SCHEDULE H-12.3a PAGE 19 OF 20

## Notes
EL PASO ELECTRIC COMPANY |  |  | ERRATA NO. 2
2021 TEXAS RATE CASE FILING |  | SCHEDULE H-12.3a
SCHEDULE H-12.3a: UNIT DATA |  |  | PAGE 20 OF 20
SPONSOR: J KYLE OLSON/DAVID C. HAWKINS
PREPARER: AARON A. ARZAGA
FOR THE TEST YEAR ENDED DECEMBER 31, 2020
PALO VERDE NOTES
(A) | N/A = Not Available (EPE does not measure or record this data)
(B) | PRODUCTION MWH (represents EPE's 15.8% share of total production)
1. GROSS UNIT OUTPUT = Palo Verde Nuclear Generating Station Unit Monthly Operating Worksheet
2. STATION SERVICE = Gross Unit Output - Net Unit Output
3. NET UNIT OUTPUT = Palo Verde Nuclear Generating Station Unit Monthly Operating Worksheet
(C) | OPERATING STATISTICS
1. EQUIVALENT AVAILABILITY FACTOR = Palo Verde Nuclear Generating Station Unit Monthly Operating Worksheet
2. FORCED OUTAGE RATE = Palo Verde Nuclear Generating Station Unit Monthly Operating Worksheet
3. SCHEDULE OUTAGE FACTOR = (schedule outage hours + maintenance outage hours + schedule outage extension
hours) / period hours. Data from the Palo Verde Nuclear Generating Station Unit Monthly Outage Worksheet
4. NET CAPACITY FACTOR = {Net Unit Output / (number of hours on line x Design Electrical Rating)} x 100%
Design Electrical Ratings approved by all Palo Verde Participants
DER Ratings - U1 1333 MWe
DER Ratings - U2 1336 MWe
DER Ratings - U3 1334 MWe
5. TIME ON AGC = On a system dispatch basis the plant output is controlled by licensed reactor operators.
6. NUMBER OF COLD STARTS = Reactor startup from Modes 4, 5, or 6 to Mode 1.
7. NUMBER OF HOT STARTS = Reactor startup from Modes 2 or 3 to Mode 1.
8. HOURS CONNECTED TO LOAD = Palo Verde Nuclear Generating Station Unit Monthly Operating Worksheet
(D) | (A) N/A = Not Available.
1. COLD START = No data available. Typical Cold Start = 35.6 Billion (B) BTU = Reactor Coolant Pumps (RCP's)
operating for 613 hours from Mode 5 to 18% power (grid synchronization).
2. HOT START = No data available. Typical Hot Start = 1.2 B BTU = RCP operating for 20 hours from Mode 3
to 18% power (grid synchronization).
3. OPERATION = [Thermal Generation MMBTU *15.8%]/1000
4. TOTAL = Cold starts + Hot starts + Operations
(E) | NET HEAT RATE = Palo Verde Nuclear Generating Station Monthly Unit Operating Worksheet | `
OPERATING STATISTICS FORMULAS
The following prescribed NERC/GADS formulas were used to calculate EAF, FOR, SOF, and NCF:
1. EAF= (Available Hours - Equivalent Derated Hours)/(Period Hours) *100
2. FOR = (Forced Outage Hours)/(Forced Outage Hours + Service Hours + Synchronous Hours + Pumping Hours) *100
3. SOF = (Maintenance Outage Hours + Planned Outage Hours)/(Period Hours) *100
4. NCF = (Net Generation)/(Period Hours * Net Maximum Capacity) *100