## CEP 19-19
| SCHEDULED | SCHEDULED | SCHEDULED | ACTUAL | ACTUAL | ACTUAL
UNIT | START | END | LENGTH OF | START | END | LENGTH OF
NAME | DATE | DATE | OUTAGE | DATE | DATE | OUTAGE | REASON FOR OUTAGE
|  |  | (Hours) |  |  | (Hours)
Copper 1 |  |  |  | 2016-01-21 07:00 | 2016-01-23 14:36 | 55.6 | Substation maintenance outage request.
Copper 1 | 2016-04-02 | 2016-04-09 | 168 | 2016-04-02 | 2016-04-13 | 264 | Summer Prep
Copper 1 |  |  |  | 2016-06-29 04:26 | 2016-06-29 12:26 | 8 | Exhaust gas leak repairs
Copper 1 | 2016-11-25 | 2016-12-16 | 504 | 2016-11-26 10:01 | 2016-12-16 14:18 | 484.2833 | Summer Prep
Copper 1 | 2017-11-25 | 2017-12-08 | 312 | 2017-11-26 | 2017-12-01 | 120 | Oil Cooler Repairs
Copper 1 |  |  |  | 2017-12-01 | 2017-12-09 16:11 | 208.1833 | Lube oil cooler replacement
Copper 1 |  |  |  | 2017-12-15 08:30 | 2017-12-16 07:20 | 22.8333 | OneOk gas line repair
Copper 1 |  |  |  | 2018-08-20 07:30 | 2018-08-20 12:57 | 5.45 | Substation to repair/replace parts on 3662B disconnect
Copper 1 |  |  |  | 2018-09-13 07:00 | 2018-09-19 12:28 | 149.4667 | Outside of Management Control (Oneok Outage)
Copper 1 |  |  |  | 2018-10-31 06:30 | 2018-10-31 15:30 | 9 | Water Injection Pump Repairs
Copper 1 | 2020-04-18 | 2020-05-01 | 312 | 2020-04-18 06:00 | 2020-05-01 13:30 | 319.5 | Summer Prep
Copper 1 | 2019-02-16 | 2019-03-15 | 648 | 2019-02-16 | 2019-03-17 17:35 | 713.5833 | Summer Prep
Copper 1 |  |  |  | 2021-04-01 | 2021-04-30 23:59 | 719.9833 | Major Inspection
Copper 1 |  |  |  | 2021-05-01 00:01 | 2021-05-01 10:00 | 9.9833 | Inlet Replacement Project
Copper 1 |  |  |  | 2021-05-01 13:15 | 2021-05-01 17:05 | 3.8333 | Tuning and testing
Copper 1 |  |  |  | 2021-05-01 23:30 | 2021-05-03 13:05 | 37.5833 | Conducting balancing activities
Copper 1 |  |  |  | 2021-05-03 16:11 | 2021-05-03 19:23 | 3.2 | Conducting balancing activities
Copper 1 |  |  |  | 2021-05-03 21:57 | 2021-05-04 18:53 | 20.9333 | Conducting balancing activities
Copper 1 |  |  |  | 2021-05-04 20:54 | 2021-05-05 08:55 | 12.0167 | Conducting balancing activities
Copper 1 |  |  |  | 2021-11-17 06:59 | 2021-11-18 07:00 | 24.0167 | Outage to perform gas supply line pigging operations
Montana 1 |  |  |  | 2016-08-27 05:00 | 2016-08-27 12:00 | 7 | Outage for gas line tie in Gas compressor "C"
Montana 1 | 2017-01-07 | 2017-01-20 | 312 | 2017-01-07 07:00 | 2017-02-12 | 857 | Summer Prep
Montana 1 |  |  |  | 2017-07-28 03:00 | 2017-07-28 08:28 | 5.4667 | VSV inspection
Montana 1 | 2018-01-20 | 2018-02-02 | 312 | 2018-01-20 07:00 | 2018-02-07 19:30 | 444.5 | Summer Prep/Supercore replacement
Montana 1 |  |  |  | 2018-05-02 07:00 | 2018-05-02 09:00 | 2 | Inspected SCR system and added logic and dual element TE
Montana 1 |  |  |  | 2018-05-12 06:00 | 2018-05-12 06:15 | 0.25 | Perform software Build and download to correct SCR issue
Montana 1 |  |  |  | 2018-05-25 04:00 | 2018-05-25 06:00 | 2 | Turbine support strut replacement
Montana 1 |  |  |  | 2018-06-02 04:00 | 2018-06-02 09:20 | 5.3333 | Turbine support leg bearing replacement
Montana 1 |  |  |  | 2018-06-23 04:00 | 2018-06-23 07:30 | 3.5 | Replace suction valve internals CT 1 forwarding pump "B"
Montana 1 |  |  |  | 2018-07-13 06:00 | 2018-07-13 17:25 | 11.4167 | Borescope HPT Supercore
Montana 1 |  |  |  | 2018-08-05 20:34 | 2018-08-18 15:07 | 306.55 | Replaced blades in 1st stage and 2nd stage hot section
Montana 1 |  |  |  | 2018-10-01 04:00 | 2018-10-01 05:17 | 1.2833 | Preventive maintenance natural gas supply valves Performed by Kinder Morgan
Montana 1 |  |  |  | 2018-10-23 08:00 | 2018-10-23 10:18 | 2.3 | Re-install anti-icing piping
Montana 1 |  |  |  | 2018-11-02 12:30 | 2018-11-02 15:00 | 2.5 | Perfom build and download black start project
Montana 1 |  |  |  | 2018-11-03 05:30 | 2018-11-07 10:00 | 100.5 | Black start testing
Montana 1 |  |  |  | 2018-11-18 07:00 | 2018-11-19 11:22 | 28.3667 | Black start testing
Montana 1 | 2019-01-07 | 2019-01-14 | 168 | 2019-01-08 07:00 | 2019-01-08 17:41 | 10.6833 | Controls upgrade
Montana 1 | 2019-01-14 | 2019-01-25 | 264 | 2019-01-13 07:00 | 2019-01-29 09:48 | 386.8 | Summer Prep
Montana 1 |  |  |  | 2019-02-12 07:00 | 2019-02-14 20:00 | 61 | 4160 electrical bus and breaker inspection
Montana 1 |  |  |  | 2019-03-10 06:00 | 2019-03-12 | 42 | Generator vibration
Montana 1 |  |  |  | 2019-03-25 23:00 | 2019-03-26 01:30 | 2.5 | Balance of plant build and dowload for upgraded control system
Montana 1 |  |  |  | 2020-01-06 07:00 | 2020-01-07 14:50 | 31.8333 | Blackstart Testing
Montana 1 |  |  |  | 2020-02-24 07:00 | 2020-02-24 16:24 | 9.4 | water wash
Montana 1 | 2020-02-03 | 2020-02-23 | 480 | 2020-02-25 07:00 | 2020-03-14 20:03 | 445.05 | Summer Prep
Montana 1 |  |  |  | 2020-03-14 | 2020-03-15 12:00 | 36 | Summer Prep
Montana 1 |  |  |  | 2020-04-25 06:30 | 2020-04-25 12:40 | 6.1667 | Replaced synthetic lube oil scavenging pump
Montana 1 |  |  |  | 2020-10-30 07:00 | 2020-10-30 09:00 | 2 | Turbine exhaust duct inspection
Montana 1 |  |  |  | 2020-11-06 08:00 | 2020-11-06 14:25 | 6.4167 | Intercooler tube leak repair
Montana 1 |  |  |  | 2020-11-16 02:00 | 2020-11-19 09:12 | 79.2 | Black Start Testing
Montana 1 |  |  |  | 2020-12-17 06:00 | 2020-12-20 20:12 | 86.2 | Main gas line section replaced
Montana 1 |  |  |  | 2021-02-24 08:00 | 2021-02-24 12:00 | 4 | Synthetic lube oil system inspection
Montana 1 |  |  |  | 2021-03-06 08:00 | 2021-03-07 | 16 | water wash
Montana 1 |  |  |  | 2021-03-07 | 2021-03-25 12:00 | 444 | Summer prep
Montana 1 |  |  |  | 2021-04-22 06:00 | 2021-04-22 06:59 | 0.98333 | Opportunity outage from 0600-0700 MST to remove exhaust catalyst sample
Montana 1 |  |  |  | 2021-11-23 | 2021-11-23 05:29 | 5.4833 | Changing relay settings/breaker status verfication
Montana 1 |  |  |  | 2021-11-29 02:00 | 2021-12-01 | 45.9997 | Black Start Testing
Montana 1 |  |  |  | 2021-12-01 | 2021-12-03 15:29 | 63.4833 | Black Start Testing
Montana 2 |  |  |  | 2016-08-27 05:00 | 2016-08-27 11:54 | 6.9 | Outage for gas line tie in gas compressor "C"
Montana 2 | 2017-01-16 | 2017-02-03 | 432 | 2017-01-14 07:00 | 2017-02-16 | 785 | Summer Prep
Montana 2 | 2018-01-27 | 2018-02-09 | 312 | 2018-01-27 07:00 | 2018-02-10 23:29 | 352.4833 | Summer Prep
Montana 2 |  |  |  | 2018-03-29 10:00 | 2018-03-29 11:45 | 1.75 | Changed ignitor
Montana 2 |  |  |  | 2018-05-12 06:00 | 2018-05-12 08:00 | 2 | Repaired service water system leak
Montana 2 |  |  |  | 2018-05-25 04:00 | 2018-05-25 06:00 | 2 | Build and download on DCS system
Montana 2 |  |  |  | 2018-06-23 04:00 | 2018-06-23 07:30 | 3.5 | Replaced suction valve internals cooling tower 1 forwarding pump "B"
Montana 2 |  |  |  | 2018-08-22 06:30 | 2018-08-22 07:20 | 0.83333 | Replaced hydraulic starter Oring
Montana 2 |  |  |  | 2018-08-23 09:45 | 2018-08-23 10:30 | 0.75 | Replaced Jacking oil pump expansion joint
Montana 2 |  |  |  | 2018-10-01 04:00 | 2018-10-01 05:17 | 1.2833 | PM Natural Gas Supply Valves from Gas Supplier (Kinder Morgan)
Montana 2 |  |  |  | 2018-10-23 13:00 | 2018-10-23 15:00 | 2 | Re-install anti-icing piping
Montana 2 |  |  |  | 2018-11-02 12:30 | 2018-11-02 15:00 | 2.5 | Perform build and download to incorporate black start logic
Montana 2 |  |  |  | 2018-11-03 05:30 | 2018-11-07 10:00 | 100.5 | Black start testing
Montana 2 |  |  |  | 2018-11-18 07:00 | 2018-11-19 11:31 | 28.5167 | Black start Testing
Montana 2 | 2019-01-07 | 2019-01-14 | 168 | 2019-01-09 07:00 | 2019-01-09 14:11 | 7.1833 | Controls upgrade
Montana 2 | 2019-01-19 | 2019-01-27 | 192 | 2019-01-18 07:00 | 2019-01-30 | 281 | Summer Prep
Montana 2 |  |  |  | 2019-02-12 07:00 | 2019-02-14 20:30 | 61.5 | 4160 bus inspection and repair
Montana 2 |  |  |  | 2019-03-20 09:15 | 2019-03-20 14:29 | 5.2333 | Replace acoustics detector
Montana 2 |  |  |  | 2019-03-25 23:05 | 2019-03-26 01:30 | 2.4167 | Balance of plant build and dowload for upgraded control system
Montana 2 |  |  |  | 2020-02-22 15:00 | 2020-02-23 11:55 | 20.9167 | Water Wash
Montana 2 | 2020-02-15 | 2020-03-06 | 480 | 2020-03-07 07:00 | 2020-03-25 13:40 | 438.6667 | Summer Prep
Montana 2 |  |  |  | 2020-07-05 08:00 | 2020-07-05 10:15 | 2.25 | Replaced hydraulic starter pump
Montana 2 |  |  |  | 2020-11-13 08:00 | 2020-11-13 11:30 | 3.5 | Replaced anti- ice valve
Montana 2 |  |  |  | 2020-11-16 02:00 | 2020-11-19 11:38 | 81.6333 | Black start testing
Montana 2 |  |  |  | 2020-12-17 06:00 | 2020-12-20 20:30 | 86.5 | Main gas line section replaced
Montana 2 |  |  |  | 2021-02-03 08:00 | 2021-02-03 16:00 | 8 | Replaced controller Tempering air fan
Montana 2 |  |  |  | 2021-03-13 08:00 | 2021-03-14 | 16 | water wash
Montana 2 |  |  |  | 2021-03-14 | 2021-03-31 16:02 | 424.0333 | Summer prep
Montana 2 |  |  |  | 2021-06-12 06:00 | 2021-06-12 07:45 | 1.75 | Replaced entire VSV turnbuckle assemble
Montana 2 |  |  |  | 2021-08-18 04:00 | 2021-08-18 06:59 | 2.9833 | Variable stator vane bracket replacement
Montana 2 |  |  |  | 2021-11-23 | 2021-11-23 05:29 | 5.4833 | Changing relay settings/breaker status verfication
Montana 2 |  |  |  | 2021-11-29 02:00 | 2021-12-01 | 45.9997 | Black Start Testing
Montana 2 |  |  |  | 2021-12-01 | 2021-12-03 15:29 | 63.4833 | Black Start Testing
Montana 2 | 2021-10-25 | 2021-11-01 | 168 |  |  | 0 | IPT Repair
Montana 3 |  |  |  | 2016-08-27 05:00 | 2016-08-27 12:00 | 7 | Outage for gas line tie in gas compressor "C"
Montana 3 | 2017-02-04 | 2017-02-17 | 312 | 2017-02-21 | 2017-03-01 | 192 | Summer Prep
Montana 3 |  |  |  | 2017-09-18 07:00 | 2017-12-31 23:59 | 2512.9833 | Generator Core Removal
Montana 3 |  |  |  | 2018-01-01 | 2018-01-05 17:19 | 113.3167 | Turbine Balancing J3 J4 and Generator
Montana 3 | 2018-02-17 | 2018-03-02 | 312 | 2018-02-11 07:00 | 2018-02-17 14:39 | 151.65 | Summer Prep
Montana 3 |  |  |  | 2018-05-12 06:00 | 2018-05-12 08:00 | 2 | Repaired cooling water system leak
Montana 3 |  |  |  | 2018-05-25 04:00 | 2018-05-25 06:00 | 2 | Build and download on DCS system
Montana 3 |  |  |  | 2018-05-31 04:00 | 2018-05-31 08:00 | 4 | Power turbine inspection borescope
Montana 3 |  |  |  | 2018-06-02 05:00 | 2018-06-02 09:00 | 4 | Replaced bearing on front west turbine leg
Montana 3 |  |  |  | 2018-08-22 06:30 | 2018-08-22 07:20 | 0.83333 | Replaced O-ring on engine starter supply line
Montana 3 |  |  |  | 2018-10-01 04:00 | 2018-10-01 05:17 | 1.2833 | Preventative maintenanceon on natural gas supply line (Kinder Morgan)
Montana 3 |  |  |  | 2018-10-24 07:00 | 2018-10-24 11:00 | 4 | Re-install anti-icing piping
Montana 3 |  |  |  | 2018-11-02 12:30 | 2018-11-02 15:00 | 2.5 | Perform build and download to incorporate black start logic
Montana 3 |  |  |  | 2018-11-02 15:00 | 2018-11-21 | 441 | replacement of generator coupling
Montana 3 | 2019-01-07 | 2019-01-14 | 168 | 2019-01-08 12:00 | 2019-01-08 15:00 | 3 | Balance of plant build and dowload for upgraded control system
Montana 3 |  |  |  | 2019-01-09 14:30 | 2019-01-09 18:53 | 4.3833 | Balance of plant build and dowload for upgraded control system
Montana 3 |  |  |  | 2019-01-10 08:00 | 2019-01-10 16:30 | 8.5 | Replaced thermal element generator drive end
Montana 3 | 2019-02-04 | 2019-02-14 | 240 | 2019-02-04 07:00 | 2019-02-16 14:22 | 295.3667 | Summer Prep
Montana 3 |  |  |  | 2019-03-06 07:00 | 2019-03-07 | 17 | Generator vibration
Montana 3 |  |  |  | 2019-03-25 23:00 | 2019-03-26 01:30 | 2.5 | Balance of plant build and dowload for upgraded control system
Montana 3 |  |  |  | 2020-01-13 07:00 | 2020-01-13 11:43 | 4.7167 | Balancing Generator
Montana 3 |  |  |  | 2020-01-13 12:39 | 2020-01-13 13:58 | 1.3167 | Balancing Generator
Montana 3 |  |  |  | 2020-01-13 15:37 | 2020-01-13 17:58 | 2.35 | Balancing Generator
Montana 3 |  |  |  | 2020-01-13 18:35 | 2020-01-13 19:55 | 1.3333 | Balancing Generator
Montana 3 |  |  |  | 2020-01-13 23:47 | 2020-01-14 10:50 | 11.05 | Balancing Generator
Montana 3 |  |  |  | 2020-01-14 11:48 | 2020-01-14 17:38 | 5.8333 | Balancing Generator
Montana 3 |  |  |  | 2020-01-14 17:56 | 2020-01-15 09:47 | 15.85 | Balancing Generator
Montana 3 |  |  |  | 2020-01-15 11:34 | 2020-01-15 18:44 | 7.1667 | Balancing Generator
Montana 3 |  |  |  | 2020-01-15 19:28 | 2020-01-16 08:45 | 13.2833 | Balancing Generator
Montana 3 |  |  |  | 2020-01-16 10:06 | 2020-01-16 12:06 | 2 | Balancing Generator
Montana 3 |  |  |  | 2020-01-16 14:47 | 2020-01-16 17:45 | 2.9667 | Balancing Generator
Montana 3 |  |  |  | 2020-01-16 21:26 | 2020-01-16 23:52 | 2.4333 | Balancing Generator
Montana 3 |  |  |  | 2020-01-17 07:21 | 2020-01-17 16:10 | 8.8167 | Balancing Generator
Montana 3 |  |  |  | 2020-01-17 18:08 | 2020-01-17 19:00 | 0.86667 | Balancing Generator
Montana 3 |  |  |  | 2020-02-22 05:00 | 2020-02-22 16:20 | 11.3333 | water wash
Montana 3 | 2020-03-09 | 2020-03-29 | 480 | 2020-04-06 06:30 | 2020-04-16 16:44 | 250.2333 | Summer Prep
Montana 3 |  |  |  | 2020-04-16 17:05 | 2020-04-18 18:30 | 49.4167 | Summer Prep
Montana 3 |  |  |  | 2020-06-04 06:00 | 2020-06-04 09:08 | 3.1333 | Replacing turbine leg strut bearing supercore west side
Montana 3 |  |  |  | 2020-06-12 06:00 | 2020-06-12 12:30 | 6.5 | Replaced power turbine leg strut bearing west side
Montana 3 |  |  |  | 2020-07-25 06:00 | 2020-07-25 10:20 | 4.3333 | Balancing Gen drive end
Montana 3 |  |  |  | 2020-07-25 15:00 | 2020-07-25 16:55 | 1.9167 | Balancing Gen drive end
Montana 3 |  |  |  | 2020-07-26 11:44 | 2020-07-26 15:00 | 3.2667 | Balancing Gen drive end
Montana 3 |  |  |  | 2020-09-28 | 2021-01-01 | 2280 | Generator Rotor Refurbishment to reduce vibrations on J3 J4 and Generator
Montana 3 |  |  |  | 2021-01-01 | 2021-01-28 09:40 | 657.6667 | Generator Rotor Refurbishment to reduce vibraitons on J3 J4 and Generator
Montana 3 |  |  |  | 2021-01-28 12:33 | 2021-01-28 16:59 | 4.4333 | Generator Rotor Refurbishment to reduce vibraitons on J3 J4 and Generator
Montana 3 |  |  |  | 2021-01-28 23:56 | 2021-01-29 13:39 | 13.7167 | Generator Rotor Refurbishment to reduce vibraitons on J3 J4 and Generator
Montana 3 |  |  |  | 2021-01-29 16:06 | 2021-01-29 21:20 | 5.2333 | Generator Rotor Refurbishment to reduce vibraitons on J3 J4 and Generator
Montana 3 |  |  |  | 2021-01-29 21:32 | 2021-01-30 16:39 | 19.1167 | Generator Rotor Refurbishment to reduce vibraitons on J3 J4 and Generator
Montana 3 |  |  |  | 2021-01-30 19:13 | 2021-01-31 23:59 | 28.7667 | Generator Rotor Refurbishment to reduce vibraitons on J3 J4 and Generator
Montana 3 |  |  |  | 2021-02-01 | 2021-02-02 15:57 | 39.95 | Generator Rotor Refurbishment to reduce vibraitons on J3 J4 and Generator
Montana 3 |  |  |  | 2021-02-01 19:00 | 2021-02-04 16:43 | 69.7167 | Generator Rotor Refurbishment to reduce vibraitons on J3 J4 and Generator
Montana 3 |  |  |  | 2021-02-04 17:26 | 2021-02-05 04:20 | 10.9 | Generator Rotor Refurbishment to reduce vibraitons on J3 J4 and Generator
Montana 3 |  |  |  | 2021-02-23 10:00 | 2021-02-23 13:05 | 3.0833 | Verify Pre-stretch power turbine/generator couplin
Montana 3 |  |  |  | 2021-04-05 08:00 | 2021-05-01 | 615.9997 | Summer Prep
Montana 3 |  |  |  | 2021-05-01 00:01 | 2021-05-01 15:38 | 15.6167 | Summer Prep
Montana 3 |  |  |  | 2021-05-01 16:01 | 2021-05-01 21:26 | 5.4167 | Summer Prep
Montana 3 |  |  |  | 2021-05-01 21:32 | 2021-05-02 12:01 | 14.4833 | Summer Prep
Montana 3 | 2021-10-20 | 2021-11-24 | 840 | 2021-10-07 08:00 | 2021-10-30 17:05 | 561.0833 | PT Balancing
Montana 3 |  |  |  | 2021-10-30 18:58 | 2021-10-31 13:54 | 18.9333 | Power Turbine Balance
Montana 3 |  |  |  | 2021-11-23 | 2021-11-23 05:29 | 5.4833 | Changing relay settings/breaker status verfication
Montana 3 |  |  |  | 2021-11-29 02:00 | 2021-12-01 | 45.9997 | Black Start Testing
Montana 3 |  |  |  | 2021-12-01 | 2021-12-03 11:55 | 59.9167 | Black Start Testing
Montana 3 |  |  |  | 2021-12-03 12:11 | 2021-12-03 15:29 | 3.3 | Black Start Generator Test
Montana 4 | 2017-02-11 | 2017-02-24 | 312 | 2017-01-23 07:00 | 2017-02-20 | 665 | Summer Prep
Montana 4 | 2018-02-10 | 2018-02-23 | 312 | 2018-02-11 07:00 | 2018-02-23 15:35 | 296.5833 | Summer Prep
Montana 4 |  |  |  | 2018-05-12 06:00 | 2018-05-12 08:00 | 2 | Repaired cooling water system leak
Montana 4 |  |  |  | 2018-05-25 04:00 | 2018-05-25 06:00 | 2 | Build and download software on DCS system
Montana 4 |  |  |  | 2018-07-16 04:00 | 2018-07-16 08:00 | 4 | LP turbine support leg adjustment
Montana 4 |  |  |  | 2018-10-01 04:00 | 2018-10-01 05:17 | 1.2833 | PM Natural Gas Supply Valves from Gas Supplier (Kinder Morgan)
Montana 4 |  |  |  | 2018-10-24 13:00 | 2018-10-24 15:00 | 2 | Re-install anti-ice piping
Montana 4 |  |  |  | 2018-11-02 12:30 | 2018-11-02 15:00 | 2.5 | Perform build and download to incorporate black start logic
Montana 4 |  |  |  | 2018-11-03 05:30 | 2018-11-07 10:00 | 100.5 | Black start testing
Montana 4 |  |  |  | 2018-11-18 07:00 | 2018-11-19 12:51 | 29.85 | Black start testing
Montana 4 | 2019-01-07 | 2019-01-14 | 168 | 2019-01-08 12:00 | 2019-01-08 15:00 | 3 | Balance of plant build and dowload for upgraded control system
Montana 4 | 2019-01-07 | 2019-01-14 | 168 | 2019-01-10 17:00 | 2019-01-11 18:07 | 25.1167 | Mark VI Control system upgrade
Montana 4 | 2019-02-09 | 2019-02-17 | 192 | 2019-02-09 07:00 | 2019-02-20 | 257 | Summer Prep
Montana 4 |  |  |  | 2019-03-08 07:00 | 2019-03-09 | 17 | Turbine balancing
Montana 4 |  |  |  | 2019-03-25 23:00 | 2019-03-26 01:30 | 2.5 | Balance of plant build and dowload for upgraded control system
Montana 4 |  |  |  | 2020-02-23 10:30 | 2020-02-23 16:53 | 6.3833 | Water Wash
Montana 4 | 2020-03-21 | 2020-04-10 | 480 | 2020-04-11 08:00 | 2020-04-24 09:40 | 313.6667 | Summer Prep
Montana 4 |  |  |  | 2020-05-22 06:00 | 2020-05-22 10:45 | 4.75 | Replace supercore leg strut bearing west side
Montana 4 |  |  |  | 2020-07-27 06:00 | 2020-07-27 14:00 | 8 | Replace supercore leg strut bearing west side Verified alignment on turbine and generator
Montana 4 |  |  |  | 2020-08-28 11:30 | 2020-08-28 14:04 | 2.5667 | Maintenance outage to repair VSV actuator
Montana 4 |  |  |  | 2020-09-28 06:00 | 2020-10-04 10:43 | 148.7167 | Performed an alignment of the Turbine and Generator
Montana 4 |  |  |  | 2020-11-16 02:00 | 2020-11-19 10:46 | 80.7667 | Black Start Testing
Montana 4 |  |  |  | 2020-12-17 06:00 | 2020-12-20 20:30 | 86.5 | Main gas line section replaced
Montana 4 |  |  |  | 2021-01-29 15:30 | 2021-01-29 19:00 | 3.5 | U4 Gen balancing
Montana 4 |  |  |  | 2021-01-29 21:29 | 2021-01-30 19:03 | 21.5667 | U4 Gen balancing
Montana 4 |  |  |  | 2021-01-30 21:29 | 2021-01-31 07:30 | 10.0167 | U4 Gen balancing
Montana 4 |  |  |  | 2021-04-17 08:00 | 2021-05-01 | 327.9997 | Summer prep
Montana 4 |  |  |  | 2021-05-01 00:01 | 2021-05-08 12:06 | 180.0833 | Summer prep
Montana 4 |  |  |  | 2021-09-20 07:00 | 2021-09-27 14:02 | 175.0333 | IPT Exchange
Montana 4 |  |  |  | 2021-11-01 09:40 | 2021-11-01 13:58 | 4.3 | Generator Balancing
Montana 4 |  |  |  | 2021-11-01 15:08 | 2021-11-01 16:02 | 0.9 | Trim Balance Generator
Montana 4 |  |  |  | 2021-11-02 08:25 | 2021-11-02 12:15 | 3.8333 | Trim Balance Generator
Montana 4 |  |  |  | 2021-11-03 06:45 | 2021-11-03 08:54 | 2.15 | Outage for finishing trim balance and replacing guards/covers
Montana 4 |  |  |  | 2021-11-20 05:00 | 2021-11-20 12:19 | 7.3167 | Replace synthetic lube oil and replace VSV bracket bearing
Montana 4 |  |  |  | 2021-11-23 | 2021-11-23 05:29 | 5.4833 | Changing relay settings/breaker status verfication
Montana 4 |  |  |  | 2021-11-29 02:00 | 2021-12-01 | 45.9997 | Black Start Testing
Montana 4 |  |  |  | 2021-12-01 | 2021-12-03 14:38 | 62.6333 | Black Start Testing
Montana 4 | 2021-10-01 | 2021-10-21 | 480 |  |  | 0 | Intermediate Pressure Turbine Maintenance
Montana 4 | 2021-10-01 | 2021-10-21 | 480 |  |  | 0 | IPT Exchange
Newman 1 | 2017-01-21 | 2017-04-14 | 1992 | 2017-01-24 09:00 | 2017-05-24 19:12 | 2890.2 | Summer prep/Turbine overhaul
Newman 1 |  |  |  | 2017-06-02 11:08 | 2017-06-03 21:24 | 34.2667 | Repairs on U1 A BFP suction valve/U1 superheat attemp Main block valve
Newman 1 |  |  |  | 2017-07-14 18:54 | 2017-07-15 19:46 | 24.8667 | Adjustments to the governor linkages
Newman 1 |  |  |  | 2017-08-25 16:51 | 2017-08-30 02:34 | 105.7167 | Boiler tube leak repairs
Newman 1 |  |  |  | 2017-09-07 06:46 | 2017-09-13 | 137.2333 | Turbine latch inspection
Newman 1 |  |  |  | 2017-09-14 01:19 | 2017-09-23 15:21 | 230.0333 | Turbine latching mechanism/control valves
Newman 1 |  |  |  | 2017-09-24 03:32 | 2017-09-24 12:56 | 9.4 | Turbine latch mechanism
Newman 1 |  |  |  | 2017-10-21 20:34 | 2017-10-22 11:54 | 15.3333 | Repair on governor
Newman 1 |  |  |  | 2017-12-09 15:32 | 2017-12-09 17:30 | 1.9667 | Inspect Main steam header line for steam leak-switched from MO to RS
Newman 1 |  |  |  | 2017-12-16 08:25 | 2017-12-20 16:30 | 104.0833 | Boiler inspection/repairs
Newman 1 |  |  |  | 2018-02-27 23:24 | 2018-03-09 16:00 | 232.6 | Boiler Inspection/Repair Boiler Leaks 17 leaks at bottom of the boiler, 14 on the roof section, 1 water wall on 6th floor that needed asbestos abatement
Newman 1 | 2018-02-24 | 2018-03-09 | 312 | 2018-03-12 | 2018-05-01 | 1200 | Summer Prep (moved up summer prep to coincide with generator seal repairs)
Newman 1 |  |  |  | 2018-05-01 | 2018-05-11 20:04 | 260.0667 | Oil Seal repairs on generator outboard brng
Newman 1 |  |  |  | 2018-05-12 09:02 | 2018-05-15 | 62.9667 | Testing of Newly Installed AVR / PSS Equipment
Newman 1 |  |  |  | 2019-01-10 09:20 | 2019-02-03 00:01 | 566.6833 | Boiler tube repair work / MO extended for circulating water line leak repair
Newman 1 | 2020-01-04 | 2020-01-24 | 480 | 2020-01-03 10:33 | 2020-01-25 11:28 | 528.9167 | Summer Prep
Newman 1 |  |  |  | 2020-02-29 11:31 | 2020-03-09 19:00 | 223.4833 | Boiler Roof Tube and Secondary Superheat Leaks
Newman 1 |  |  |  | 2020-07-17 16:00 | 2020-07-27 | 224 | Loss of field in generator due to field fault, Generator H2 seal repair
Newman 1 |  |  |  | 2020-10-18 21:15 | 2020-11-01 04:03 | 318.8 | Maintenance outage to repair boiler water wall tube leak
Newman 1 | 2021-01-09 | 2021-03-10 | 1440 | 2021-01-09 07:00 | 2021-05-12 11:04 | 2956.0667 | Valve Inspection/Summer Prep
Newman 1 |  |  |  | 2021-08-01 01:16 | 2021-08-10 22:59 | 237.7167 | Address boiler hot spot
Newman 1 | 2021-11-27 | 2021-12-17 | 480 | 2021-11-27 | in progress |  | Summer prep
Newman 2 |  |  |  | 2016-03-12 | 2016-03-24 16:00 | 304 | Summer prep
Newman 2 |  |  |  | 2016-08-17 20:45 | 2016-08-22 07:21 | 106.6 | Repair boiler tube leaks
Newman 2 |  |  |  | 2016-10-26 14:38 | 2016-11-02 20:16 | 173.6333 | Boiler leak repairs / circulating water line leak
Newman 2 |  |  |  | 2017-01-19 00:42 | 2017-01-21 20:30 | 67.8 | T3 Transformer Prep Work
Newman 2 | 2017-02-04 | 2017-02-17 | 312 | 2017-03-24 23:04 | 2017-04-07 23:15 | 336.1833 | Summer Prep
Newman 2 |  |  |  | 2017-04-27 00:34 | 2017-05-02 22:05 | 141.5167 | Work on T-6 (Substation)
Newman 2 |  |  |  | 2017-09-08 20:54 | 2017-09-16 17:40 | 188.7667 | Repair superheat leak at the main steam stop valve
Newman 2 |  |  |  | 2017-12-15 04:46 | 2017-12-15 17:19 | 12.55 | Forced Draft Fan controller/positioner replaced
Newman 2 |  |  |  | 2017-12-26 06:00 | 2018-01-01 | 138 | Boiler inspection/repairs
Newman 2 |  |  |  | 2018-01-01 | 2018-01-03 18:13 | 66.2167 | Boiler Repairs Leak on the Roof and Super heat sections Repairs made to both
Newman 2 | 2018-02-03 | 2018-04-13 | 1656 | 2018-01-30 07:00 | 2018-04-13 18:15 | 1763.25 | Major inspection; boiler only
Newman 2 |  |  |  | 2018-04-14 22:30 | 2018-04-16 01:05 | 26.5833 | Balance shot on LP turbine
Newman 2 |  |  |  | 2018-11-07 13:03 | 2018-11-13 19:09 | 150.1 | Turbine Vibration Testing- Balance Shot
Newman 2 |  |  |  | 2019-01-16 11:54 | 2019-01-28 01:12 | 277.3 | Outage to address CO issues involving boiler and burner
Newman 2 |  |  |  | 2019-03-09 11:05 | 2019-03-15 23:00 | 155.9167 | Hp steam leak at turbine
Newman 2 | 2019-03-02 | 2019-03-22 | 480 | 2019-03-15 23:00 | 2019-04-01 | 385 | Summer Prep
Newman 2 | 2020-01-11 | 2020-01-31 | 480 | 2020-01-06 | 2020-02-02 | 648 | Summer Prep
Newman 2 |  |  |  | 2021-01-23 03:32 | 2021-02-01 | 212.4664 | Summer Prep
Newman 2 |  |  |  | 2021-02-01 | 2021-02-17 07:00 | 391 | Summer Prep
Newman 3 | 2016-01-09 | 2016-03-11 | 1512 | 2016-01-08 22:09 | 2016-03-07 | 1393.85 | Control valve repairs / Summer prep
Newman 3 |  |  |  | 2016-04-01 04:45 | 2016-04-01 10:18 | 5.55 | Off line to repair DA make up line leak, returned to service after repair
Newman 3 |  |  |  | 2016-05-12 22:31 | 2016-05-15 22:30 | 71.9833 | Main Stop Valve Repairs
Newman 3 | 2017-01-07 | 2017-05-08 | 2904 | 2017-01-07 | 2017-04-27 18:16 | 2658.2667 | Summer Prep/Turbine Overhaul
Newman 3 |  |  |  | 2017-04-27 20:57 | 2017-05-02 16:28 | 115.5167 | Balance Shot To Reduce Steam Turbine Vibrations
Newman 3 |  |  |  | 2017-05-02 16:36 | 2017-05-02 17:36 | 1 | Boiler trip on low air flow, unit was in testing mode
Newman 3 |  |  |  | 2017-05-02 17:55 | 2017-05-02 18:41 | 0.76667 | Boiler trip on loss of Burner #1, unit was in testing mode
Newman 3 |  |  |  | 2017-06-30 22:55 | 2017-07-01 18:36 | 19.6833 | Condenser inspection/repairs
Newman 3 |  |  |  | 2017-10-20 21:30 | 2017-10-21 12:34 | 15.0667 | Repair of gas valve
Newman 3 |  |  |  | 2018-04-13 22:31 | 2018-04-17 02:07 | 75.6 | Summer Prep
Newman 3 | 2018-02-10 | 2018-02-23 | 312 | 2018-04-17 08:10 | 2018-04-30 09:43 | 313.55 | Summer Prep
Newman 3 |  |  |  | 2018-07-27 01:16 | 2018-07-30 07:07 | 77.85 | Boiler leak repairs
Newman 3 |  |  |  | 2018-10-05 23:16 | 2018-12-10 07:55 | 1568.65 | U3 in Planned Outage for DCS upgrade
Newman 3 | 2019-03-16 | 2019-03-23 |  | 2019-01-28 14:47 | 2019-02-19 18:32 | 531.75 | Summer Prep
Newman 3 | 2020-01-04 | 2020-02-07 | 816 | 2020-01-03 | 2020-02-16 | 1056 | Summer Prep
Newman 3 |  |  |  | 2020-08-14 21:41 | 2020-08-18 20:33 | 94.8667 | Unit removed from service to repair boiler tube leak
Newman 3 |  |  |  | 2020-12-28 07:00 | 2021-01-01 | 89 | Boiler tube leak repairs
Newman 3 |  |  |  | 2021-01-01 | 2021-01-02 09:00 | 33 | Boiler Tube Leak Repairs
Newman 3 | 2021-02-20 | 2021-04-28 | 1608 | 2021-02-22 12:07 | 2021-05-06 20:28 | 1760.35 | Valve Inspection/Summer Prep
Newman 3 |  |  |  | 2021-10-10 18:00 | 2021-10-14 16:29 | 94.4833 | Boiler Tube Leak Repairs
Newman 3 |  |  |  | 2021-10-25 21:32 | 2021-10-29 21:15 | 95.7167 | Outage to inspect and repair air preheater
Newman 4GT-1 |  |  |  | 2015-10-16 17:37 | 2016-03-11 14:02 | 3524.4167 | Investigating cause of high vibrations
Newman 4GT-1 | 2016-04-16 | 2016-04-30 | 336 | 2016-04-07 23:58 | 2016-04-20 08:00 | 296.0333 | Summer Prep
Newman 4GT-1 |  |  |  | 2016-06-02 01:20 | 2016-06-04 20:21 | 67.0167 | Boiler repairs and seal air regulator replacement
Newman 4GT-1 |  |  |  | 2016-08-29 10:47 | 2016-09-06 16:00 | 197.2167 | Boiler inspection and checking HRSG for any damage during dry run mode
Newman 4GT-1 |  |  |  | 2016-09-09 07:00 | 2016-09-11 20:00 | 61 | Intra gas tie in project
Newman 4GT-1 |  |  |  | 2016-09-24 08:00 | 2016-09-26 16:00 | 56 | Cleaning U4 CT basin
Newman 4GT-1 |  |  |  | 2016-10-21 14:19 | 2016-10-24 11:10 | 68.85 | Install balance shot for vibration issue and to repair oil leak
Newman 4GT-1 |  |  |  | 2016-12-19 00:51 | 2016-12-19 18:33 | 17.7 | BFP packing
Newman 4GT-1 |  |  |  | 2017-01-09 21:37 | 2017-01-11 14:40 | 41.05 | Burner Work, Run back
Newman 4GT-1 |  |  |  | 2017-01-24 09:32 | 2017-01-24 14:46 | 5.2333 | Repair Feed Water Regulator HRSG1
Newman 4GT-1 | 2017-02-25 | 2017-03-17 | 480 | 2017-03-03 22:24 | 2017-03-21 11:41 | 421.2833 | Summer Prep
Newman 4GT-1 |  |  |  | 2017-05-03 22:26 | 2017-05-05 19:38 | 45.2 | Exhaust leak
Newman 4GT-1 |  |  |  | 2017-10-19 08:00 | 2017-10-25 | 136 | Aux cooling water system repairs
Newman 4GT-1 | 2018-01-06 | 2018-01-26 | 480 | 2017-12-04 | 2017-12-24 14:00 | 494 | Summer Prep
Newman 4GT-1 | 2021-10-30 | 2021-11-19 | 480 | 2021-10-30 02:38 | 2021-11-20 00:08 | 501.5 | Combustor Inspection
Newman 4-GT1 |  |  |  | 2018-01-15 11:49 | 2018-01-16 15:58 | 28.15 | Repack Pegging Steam Reg and replace DA make up reg
Newman 4-GT1 |  |  |  | 2018-04-15 21:48 | 2018-05-09 15:10 | 569.3667 | Repair exhaust end bearing oil leak
Newman 4-GT1 |  |  |  | 2018-05-18 21:01 | 2018-05-21 07:00 | 57.9833 | Inspection of exhaust bearing elements/ MO to FO on May 21, 2018 at 07:00
Newman 4-GT1 |  |  |  | 2018-06-14 08:45 | 2018-06-15 07:33 | 22.8 | Installation of Insulation Blankets on GT Shell
Newman 4-GT1 |  |  |  | 2018-12-03 12:01 | 2019-01-15 | 1019.9833 | High Turbine Vibration
Newman 4-GT1 | 2019-01-05 | 2019-03-29 | 1992 | 2019-01-15 07:00 | 2019-03-30 | 1769 | Major Inspection
Newman 4-GT1 | 2020-03-07 | 2020-04-17 | 984 | 2020-03-07 | 2020-04-17 | 984 | Turbine Hot Gas and Summer Prep
Newman 4-GT1 |  |  |  | 2020-05-14 | 2020-05-17 | 72 | Outage to repair oil leak on exciter\starting package
Newman 4-GT1 |  |  |  | 2020-06-26 21:05 | 2020-06-27 13:38 | 16.55 | Maint Outage to install balance shot and cooling shroud on exciter
Newman 4-GT1 |  |  |  | 2020-07-02 07:37 | 2020-07-02 11:00 | 3.3833 | Planned outage to install balance shot
Newman 4-GT1 |  |  |  | 2020-07-25 06:56 | 2020-07-25 09:25 | 2.4833 | Removed from service to collect vibration data
Newman 4-GT1 |  |  |  | 2020-10-02 21:28 | 2021-01-01 | 2162.5333 | DCS Upgrade
Newman 4-GT1 |  |  |  | 2021-01-01 | 2021-01-30 | 696 | DCS Upgrade
Newman 4-GT1 |  |  |  | 2021-03-10 19:38 | 2021-03-14 09:54 | 86.2667 | Change Water Injection Orfice
Newman 4-GT1 |  |  |  | 2021-04-07 22:00 | 2021-04-13 09:40 | 131.6667 | Boiler Feed Pump Repairs
Newman 4-GT1 |  |  |  | 2021-11-23 05:00 | 2021-11-23 11:29 | 6.4833 | Repairs on water injection
Newman 4GT-2 | 2016-04-16 | 2016-04-30 | 336 | 2016-04-07 23:48 | 2016-04-28 16:40 | 496.8667 | Summer Prep
Newman 4GT-2 |  |  |  | 2016-09-06 07:00 | 2016-09-15 12:30 | 221.5 | Check HRSG for any damage during dry run mode
Newman 4GT-2 |  |  |  | 2016-09-24 08:00 | 2016-09-26 16:00 | 56 | Cleaning U4 CT basin
Newman 4GT-2 |  |  |  | 2016-10-21 14:30 | 2016-10-24 22:30 | 80 | Install balance shot for vibration issue and to repair oil leak
Newman 4GT-2 |  |  |  | 2017-01-17 08:04 | 2017-01-17 14:56 | 6.8667 | BFP Inboard Bearing Replacment
Newman 4GT-2 | 2017-02-11 | 2017-04-07 | 1320 | 2017-02-10 14:34 | 2017-04-26 | 1785.4333 | GT2 Planned Outage
Newman 4GT-2 |  |  |  | 2017-05-19 22:06 | 2017-05-21 09:15 | 35.15 | Steam flow transmitter repair
Newman 4GT-2 |  |  |  | 2017-07-07 19:57 | 2017-07-08 19:50 | 23.8833 | Exhaust temp issues
Newman 4GT-2 |  |  |  | 2017-08-24 04:45 | 2017-08-24 12:30 | 7.75 | GT2 IGV work
Newman 4GT-2 |  |  |  | 2017-09-22 03:05 | 2017-09-22 08:13 | 5.1333 | Aux water repair to H2 coolers/exciter cooler vent line
Newman 4GT-2 |  |  |  | 2017-10-19 08:00 | 2017-10-25 | 136 | Aux cooling water system repairs
Newman 4GT-2 | 2018-01-13 | 2018-01-26 | 312 | 2017-12-04 | 2017-12-24 14:00 | 494 | Summer Prep
Newman 4GT-2 | 2021-10-30 | 2021-11-19 | 480 | 2021-10-31 20:31 | 2021-11-20 20:31 | 480 | Combustor Inspection
Newman 4-GT2 |  |  |  | 2018-01-16 17:03 | 2018-01-17 14:14 | 21.1833 | Replace Main BFP out board bearing
Newman 4-GT2 |  |  |  | 2018-07-22 01:14 | 2018-07-22 20:40 | 19.4333 | Main BFP replacement
Newman 4-GT2 | 2018-01-13 | 2018-02-02 | 480 | 2019-02-16 07:23 | 2019-03-17 16:43 | 705.3333 | Summer Prep
Newman 4-GT2 |  |  |  | 2019-03-29 09:00 | 2019-04-01 | 63 | Transfer from FO to MO (Scheduled MO to replace the lead seal on condenser)
Newman 4-GT2 | 2020-02-15 | 2020-04-17 | 1488 | 2020-02-18 | 2020-05-01 | 1752 | Turbine Major and Summer Prep
Newman 4-GT2 |  |  |  | 2020-06-27 19:17 | 2020-06-29 17:29 | 46.2 | Maint outage to repair DA make up valve and nozzles
Newman 4-GT2 |  |  |  | 2020-08-01 01:24 | 2020-08-01 14:05 | 12.6833 | Unit removed from service to replace BF pump packing
Newman 4-GT2 |  |  |  | 2020-08-05 08:12 | 2020-08-08 20:41 | 84.4833 | Unit removed from service to repair oil leak in tear drop that is causing fires
Newman 4-GT2 |  |  |  | 2020-10-02 21:36 | 2021-01-01 | 2162.4 | DCS Upgrade
Newman 4-GT2 |  |  |  | 2021-01-01 | 2021-01-26 07:45 | 607.75 | DCS Upgrade
Newman 4-GT2 |  |  |  | 2021-02-02 16:50 | 2021-02-09 12:03 | 163.2167 | Due to the GT1 and ST4 in Forced Outage
Newman 4-GT2 |  |  |  | 2021-03-10 19:34 | 2021-03-14 22:53 | 99.3167 | Exhaust Fan Repair
Newman 4-GT2 |  |  |  | 2021-04-07 22:00 | 2021-04-13 12:32 | 134.5333 | Exhaust Leak Repairs- per plant report
Newman 4-GT2 |  |  |  | 2021-04-14 01:50 | 2021-04-14 14:12 | 12.3667 | Balancing Activities
Newman 4-GT2 |  |  |  | 2021-04-14 21:56 | 2021-04-15 17:54 | 19.9667 | Balancing Activities
Newman 4-GT2 |  |  |  | 2021-04-16 01:08 | 2021-04-16 17:13 | 16.0833 | Balancing Activities
Newman 4-GT2 |  |  |  | 2021-04-16 21:51 | 2021-04-17 18:14 | 20.3833 | Balancing Activities
Newman 4-GT2 |  |  |  | 2021-04-17 23:02 | 2021-04-28 12:01 | 252.9833 | Balancing Activities, HRSG2 Tube Leaks, Manual Power Check Valve Failure
Newman 4-GT2 |  |  |  | 2021-04-28 20:48 | 2021-04-29 11:03 | 14.25 | Balancing Activities
Newman 4-GT2 |  |  |  | 2021-07-30 15:23 | 2021-07-31 20:15 | 28.8667 | Repair HRSG2 HP Circualtion Pump
Newman 4-GT2 |  |  |  | 2021-11-22 05:24 | 2021-11-22 19:50 | 14.4333 | GT2 Taken Offline for repairs
Newman 4-ST | 2016-04-16 | 2016-04-30 | 336 | 2016-04-07 23:42 | 2016-04-20 08:00 | 296.3 | Summer Prep
Newman 4-ST |  |  |  | 2016-10-24 06:57 | 2016-10-24 18:07 | 11.1667 | Install balance shot for vibration issue and to repair oil leak
Newman 4-ST |  |  |  | 2016-11-28 05:20 | 2016-11-28 16:50 | 11.5 | Inverter work
Newman 4-ST | 2017-02-25 | 2017-03-17 | 480 | 2017-03-03 22:14 | 2017-03-22 02:43 | 436.4833 | Summer Prep
Newman 4-ST |  |  |  | 2017-03-31 21:26 | 2017-04-02 06:57 | 33.5167 | Replace Emer DC lube oil pump
Newman 4-ST |  |  |  | 2018-01-10 08:45 | 2018-01-10 15:39 | 6.9 | Post startup balance Shot on U4 STM
Newman 4-ST |  |  |  | 2018-12-19 08:00 | 2018-12-20 14:26 | 30.4333 | Gen Protective Relay Testing
Newman 4-ST | 2018-01-13 | 2018-01-26 | 312 | 2019-02-16 00:20 | 2019-03-18 03:27 | 723.1167 | Summer Prep
Newman 4-ST |  |  |  | 2019-03-19 09:00 | 2019-04-01 | 303 | Transfer from FO to MO (Scheduled MO to replace the lead seal)
Newman 4-ST | 2020-03-07 | 2020-04-17 | 984 | 2020-03-07 | 2020-04-17 | 984 | Summer Prep
Newman 4-ST |  |  |  | 2020-05-14 00:41 | 2020-05-17 09:26 | 80.75 | Outage to repair oil leak on exciter\starting package
Newman 4-ST |  |  |  | 2020-10-02 21:10 | 2021-01-01 | 2162.8333 | DCS Upgrade and Valve Inspection
Newman 4-ST |  |  |  | 2021-03-10 19:37 | 2021-03-15 09:18 | 109.6833 | SJAE and Hogger design change
Newman 4-ST |  |  |  | 2021-04-07 22:00 | 2021-04-14 06:15 | 152.25 | Vacuum Leak Repairs
Newman 4-ST | 2021-10-30 | 2021-11-19 | 480 | 2021-10-31 | 2021-11-21 | 504 | Summer prep
Newman 5GT3 | 2015-10-03 | 2015-10-30 | 672 | 2015-10-23 | 2016-01-15 16:00 | 2032 | Gas Path Inspection and compressor blade repairs
Newman 5GT3 |  |  |  | 2016-01-15 16:00 | 2016-02-05 12:51 | 500.85 | High Vibrations #2 Turbine Bearing (extended planned outage)
Newman 5GT3 |  |  |  | 2016-03-22 08:00 | 2016-03-24 16:29 | 56.4833 | Repairs on the wet compression and fogging system
Newman 5GT-3 |  |  |  | 2016-04-07 06:19 | 2016-04-07 09:31 | 3.2 | Array in bell mouth Area Inspection
Newman 5GT-3 |  |  |  | 2016-04-29 | 2016-04-30 17:00 | 41 | Inter gas tie in
Newman 5GT-3 |  |  |  | 2016-07-01 21:35 | 2016-07-04 13:56 | 64.35 | Boiler tube leak repair
Newman 5GT-3 |  |  |  | 2016-07-23 07:00 | 2016-07-23 08:00 | 1 | Hydraulic oil filter change and thermocouple 12 replace
Newman 5GT-3 |  |  |  | 2016-08-13 03:55 | 2016-08-13 14:03 | 10.1333 | Replace lube oil mist separator blower motor
Newman 5GT-3 | 2016-11-28 | 2017-01-13 | 1104 | 2016-12-19 10:32 | 2017-01-14 | 613.4667 | Summer Prep
Newman 5GT-3 |  |  |  | 2017-04-10 05:50 | 2017-04-30 | 474.1667 | Turbine Aux work/testing and commissioning U5 steam turbine
Newman 5GT-3 |  |  |  | 2017-09-22 22:00 | 2017-09-26 07:39 | 81.65 | Remove blanking plate to return unit to combined cycle
Newman 5GT-3 |  |  |  | 2017-09-30 16:26 | 2017-10-06 | 127.5667 | Offline for lube oil flow inspection on bearings 2 and 4
Newman 5GT-3 |  |  |  | 2017-11-19 | 2017-11-19 12:00 | 12 | Plate Swap
Newman 5GT-3 |  |  |  | 2017-11-21 | 2017-11-28 13:50 | 181.8333 | Block 5 Ongoing Testing
Newman 5GT-3 |  |  |  | 2017-12-04 13:36 | 2017-12-04 14:30 | 0.9 | Controlled shutdown for trippped CCW pump on U5 STM (still in testing mode)
Newman 5GT-3 | 2021-02-06 | 2021-03-10 | 768 | 2021-02-21 11:20 | 2021-03-27 14:18 | 818.9667 | Hot Gas Path Inspection
Newman 5-GT3 |  |  |  | 2018-01-26 06:00 | 2018-01-26 17:28 | 11.4667 | Installation of bypass valves on HP IP drums
Newman 5-GT3 | 2018-03-17 | 2018-03-30 | 312 | 2018-03-16 21:53 | 2018-04-02 19:51 | 405.9667 | Summer Prep
Newman 5-GT3 |  |  |  | 2018-06-02 22:04 | 2018-06-04 07:02 | 32.9667 | HRSG leaks and HP bypass and HRH bypass valve stem repairs
Newman 5-GT3 |  |  |  | 2018-07-21 00:13 | 2018-07-21 17:00 | 16.7833 | Exhaust Leak Repairs on the HRSG side-convert to simple cycle mode
Newman 5-GT3 |  |  |  | 2018-07-26 00:35 | 2018-07-26 15:50 | 15.25 | Converting from simple cycle to combined cycle
Newman 5-GT3 |  |  |  | 2018-11-10 00:30 | 2018-11-16 15:20 | 158.8333 | HRH Leak Repair
Newman 5-GT3 | 2019-03-16 | 2019-05-03 | 1152 | 2019-03-19 11:38 | 2019-04-01 | 300.3667 | Summer Prep/DCS Upgrade
Newman 5-GT3 | 2020-02-08 | 2020-02-28 | 480 | 2020-02-07 | 2020-02-29 | 528 | Summer Prep and Hot Gas Inspection
Newman 5-GT3 |  |  |  | 2020-04-25 21:54 | 2020-04-27 21:38 | 47.7333 | Maintenance Outage to repair attemperator and relief valves
Newman 5-GT3 |  |  |  | 2020-05-02 01:51 | 2020-05-05 01:11 | 71.3333 | Maintenance outage to repair flange steam leak and attemperator
Newman 5-GT3 |  |  |  | 2021-03-27 10:18 | 2021-03-27 21:46 | 11.4667 | Summer Prep and Hot Gas Inspection
Newman 5-GT3 |  |  |  | 2021-03-28 03:36 | 2021-03-29 09:28 | 29.8667 | Summer Prep and Hot Gas Inspection
Newman 5-GT3 |  |  |  | 2021-03-29 17:08 | 2021-03-30 10:58 | 17.8333 | Summer Prep and Hot Gas Inspection
Newman 5-GT3 |  |  |  | 2021-03-30 17:24 | 2021-03-31 03:22 | 9.9667 | Summer Prep and Hot Gas Inspection
Newman 5-GT3 |  |  |  | 2021-03-31 16:05 | 2021-03-31 23:59 | 7.9 | Summer Prep and Hot Gas Inspection
Newman 5-GT3 |  |  |  | 2021-04-01 | 2021-04-05 13:21 | 109.35 | Summer Prep and Hot Gas Inspection
Newman 5-GT3 |  |  |  | 2021-04-23 23:42 | 2021-04-30 23:59 | 168.2833 | Exhaust leak repairs
Newman 5-GT3 |  |  |  | 2021-05-01 00:01 | 2021-05-09 08:15 | 200.2333 | Exhaust leak repairs
Newman 5-GT3 |  |  |  | 2021-06-28 01:08 | 2021-06-29 21:04 | 43.9333 | Replace 3-2 BFP
Newman 5GT4 |  |  |  | 2015-11-09 14:37 | 2016-01-29 14:09 | 1943.5333 | Turbine repairs (compressor blade repairs)
Newman 5GT4 |  |  |  | 2016-01-29 14:56 | 2016-01-29 17:02 | 2.1 | Testing and tuning
Newman 5GT-4 |  |  |  | 2016-04-29 | 2016-04-30 17:00 | 41 | Inter gas tie in
Newman 5GT-4 |  |  |  | 2016-08-22 20:55 | 2016-08-23 13:10 | 16.25 | Exhaust Leak Repairs
Newman 5GT-4 | 2016-11-28 | 2017-01-13 | 1104 | 2016-12-19 09:16 | 2017-01-14 | 614.7333 | Summer Prep
Newman 5GT-4 |  |  |  | 2017-02-25 07:30 | 2017-02-25 12:00 | 4.5 | Bleed valve actuator repair
Newman 5GT-4 |  |  |  | 2017-04-10 05:50 | 2017-04-14 20:52 | 111.0333 | Turbine Aux work/Gas Skid Filter
Newman 5GT-4 |  |  |  | 2017-04-21 13:21 | 2017-04-30 | 202.65 | Combined cycle plate swap and U5 steam turbine startup and testing
Newman 5GT-4 |  |  |  | 2017-08-03 07:00 | 2017-08-03 17:41 | 10.6833 | Borescope of turbine and combustor inspection
Newman 5GT-4 |  |  |  | 2017-09-22 22:00 | 2017-09-26 15:20 | 89.3333 | Remove blanking plate to return unit to combined cycle
Newman 5GT-4 |  |  |  | 2017-09-30 16:32 | 2017-10-06 11:45 | 139.2167 | Offline for lube oil flow inspection on bearings 2 and 5
Newman 5GT-4 |  |  |  | 2017-11-19 | 2017-11-19 12:00 | 12 | Plate Swap
Newman 5GT-4 |  |  |  | 2017-11-21 | 2017-11-28 11:37 | 179.6167 | Block 5 Ongoing Testing
Newman 5GT-4 |  |  |  | 2017-12-04 13:36 | 2017-12-04 14:14 | 0.63333 | Controlled shutdown for trippped CCW pump on U5 STM (still in testing mode)
Newman 5-GT4 |  |  |  | 2020-01-18 08:56 | 2020-01-18 21:22 | 12.4333 | Repairs to Phosphate Line leaking at HP Drum
Newman 5-GT4 | 2020-02-01 | 2020-02-28 | 648 | 2020-01-31 | 2020-02-27 | 648 | Summer Prep
Newman 5-GT4 |  |  |  | 2021-03-18 10:33 | 2021-04-01 | 325.45 | Summer Prep, General Inspection
Newman 5-GT4 |  |  |  | 2021-04-01 | 2021-04-06 15:12 | 135.2 | Summer Prep, General Inspection
Newman 5-GT4 |  |  |  | 2021-06-28 01:00 | 2021-06-30 06:26 | 53.4333 | Replace 3-2 BFP
Newman 5ST |  |  |  | 2015-11-09 14:37 | 2016-01-30 02:52 | 1956.25 | Unit off due to GT3 & GT4 off for inspection & compression repairs
Newman 5ST |  |  |  | 2016-02-16 | 2016-02-19 09:26 | 81.4333 | Maintenance on hot reheat valves / Summer prep
Newman 5ST |  |  |  | 2016-04-29 | 2016-04-30 17:00 | 41 | Inter gas tie in
Newman 5ST |  |  |  | 2017-09-27 15:20 | 2017-09-29 | 32.6667 | Steam turbine testing & tuning
Newman 5ST |  |  |  | 2017-09-29 17:04 | 2017-11-08 12:00 | 954.9333 | Lube oil system inspection to inspect flow to bearings 3 and 4
Newman 5ST |  |  |  | 2017-12-01 09:25 | 2017-12-01 09:50 | 0.41667 | Tripped on false drum level indication (Unit in testing mode, therefore not a FO)
Newman 5ST |  |  |  | 2017-12-04 13:28 | 2017-12-04 14:35 | 1.1167 | Controlled shutdown for trippped CCW pump on U5 STM (still in testing mode)
Newman 5ST |  |  |  | 2018-03-16 21:46 | 2018-04-03 11:55 | 422.15 | Summer Prep
Newman 5ST |  |  |  | 2018-11-09 23:31 | 2018-11-16 17:13 | 161.7 | HRH Leak Repair
Newman 5ST | 2019-03-16 | 2019-05-03 | 1152 | 2019-03-19 21:36 | 2019-04-01 | 290.4 | Summer Prep/DCS Upgrade
Newman 5-ST | 2020-02-08 | 2020-02-28 | 480 | 2020-02-07 | 2020-02-29 | 528 | Summer Prep
Newman 5-ST |  |  |  | 2021-02-15 16:00 | 2021-03-28 02:30 | 970.5 | Summer Prep, HRSG Inspection
Newman 5-ST |  |  |  | 2021-03-28 02:40 | 2021-03-28 03:18 | 0.63333 | Summer Prep testing: Auto Sync Issue
Newman 5-ST |  |  |  | 2021-03-28 03:23 | 2021-03-31 11:43 | 80.3333 | Summer Prep testing, Auto Sync Issue
Newman 5-ST |  |  |  | 2021-03-31 15:50 | 2021-03-31 23:59 | 8.15 | Summer Prep and GT3 Hot Gas Inspection
Newman 5-ST |  |  |  | 2021-04-01 | 2021-04-06 02:55 | 122.9167 | Unit Tripped
Newman 5-ST |  |  |  | 2021-05-21 22:36 | 2021-05-23 13:12 | 38.6 | Substation crew to work on radiators due to extreme heat not circulating properly-mo to repair high GSU transformer temperature-OMC updated per plant report kr
Newman 5-ST |  |  |  | 2021-06-28 01:02 | 2021-06-30 03:01 | 49.9833 | Replace 3-2 BFP
Newman5-GT4 |  |  |  | 2018-01-27 06:00 | 2018-01-27 17:22 | 11.3667 | Installation of bypass valves on HP IP drums
Newman5-GT4 | 2018-03-31 | 2018-04-13 | 312 | 2018-03-12 | 2018-04-02 19:19 | 523.3167 | Summer Prep
Newman5-GT4 |  |  |  | 2018-06-02 22:06 | 2018-06-04 09:29 | 35.3833 | HRSG leaks and HP bypass and HRH bypass valve repairs
Newman5-GT4 |  |  |  | 2018-11-10 00:32 | 2018-11-16 14:00 | 157.4667 | HRH Leak Repair
Newman5-GT4 | 2019-03-16 | 2019-05-03 | 1152 | 2019-03-19 23:41 | 2019-04-01 | 288.3167 | Summer Prep/DCS Upgrade
Rio Grande 6 |  |  |  | 2017-09-18 20:50 | 2017-09-19 16:30 | 19.6667 | Repair attemperator sensing line
Rio Grande 6 |  |  |  | 2017-10-04 07:00 | 2017-10-04 14:30 | 7.5 | Repair gas burner #2 linkage
Rio Grande 6 | 2018-01-13 | 2018-01-26 | 312 | 2018-01-13 00:01 | 2018-02-02 09:19 | 489.3 | Partial summer prep outage
Rio Grande 6 |  |  |  | 2018-08-20 08:00 | 2018-08-20 15:33 | 7.55 | To replace left side lead seal
Rio Grande 6 |  |  |  | 2021-06-29 07:00 | 2021-07-01 12:00 | 53 | Condenser Cleaning
Rio Grande 6 |  |  |  | 2021-07-27 07:00 | 2021-07-28 14:29 | 31.4833 | Reason for outage is to repair AVR on unit 6
Rio Grande 7 |  |  |  | 2016-02-01 | 2016-03-26 12:26 | 1308.4333 | ST valve inspection outage
Rio Grande 7 |  |  |  | 2016-05-17 10:15 | 2016-05-19 14:15 | 52 | Repair hotspot on boiler
Rio Grande 7 |  |  |  | 2016-07-09 08:57 | 2016-07-09 17:55 | 8.9667 | Repair condenser leak
Rio Grande 7 |  |  |  | 2016-09-24 21:02 | 2016-09-25 11:35 | 14.55 | Repair lead seal on the condenser
Rio Grande 7 |  |  |  | 2016-10-03 08:00 | 2016-10-07 15:12 | 103.2 | Repair boiler tube leaks
Rio Grande 7 |  |  |  | 2016-11-08 15:10 | 2016-12-01 | 536.8333 | Summer Prep
Rio Grande 7 | 2017-01-14 | 2017-02-10 | 648 | 2017-01-13 09:14 | 2017-02-09 13:20 | 652.1 | Summer Prep
Rio Grande 7 |  |  |  | 2017-04-07 23:01 | 2017-04-13 12:00 | 132.9833 | Work on 1st Pt Heater
Rio Grande 7 |  |  |  | 2017-09-08 21:22 | 2017-09-12 16:30 | 91.1333 | For Boiler Feed Pump discharge valve repair
Rio Grande 7 |  |  |  | 2017-10-23 07:00 | 2017-10-23 17:00 | 10 | Boiler tube repair and preheater assessment
Rio Grande 7 |  |  |  | 2018-01-05 07:00 | 2018-01-05 16:00 | 9 | Perform Hydro test boiler, preheater inspection and reheat vacuum test
Rio Grande 7 | 2018-01-13 | 2018-02-02 | 480 | 2018-01-12 22:29 | 2018-02-02 18:00 | 499.5167 | Summer Prep
Rio Grande 7 |  |  |  | 2018-02-09 12:21 | 2018-02-10 16:45 | 28.4 | Repair view port on boiler and circ water system leak
Rio Grande 7 |  |  |  | 2018-10-01 07:00 | 2018-10-04 14:00 | 79 | Address GPU relays, 2300v bus and 480v electrical system
Rio Grande 7 |  |  |  | 2018-11-20 08:00 | 2018-11-21 11:40 | 27.6667 | Repair Boiler Tube Leak in Economizer Section
Rio Grande 7 | 2019-02-16 | 2019-03-01 | 312 | 2019-02-16 | 2019-03-04 08:24 | 392.4 | Summer Prep
Rio Grande 7 |  |  |  | 2020-12-14 07:00 | 2020-12-18 10:13 | 99.2167 | To work on Boiler Tube Leaks, DA Level Column Transmitter and Condenser
Rio Grande 7 |  |  |  | 2021-01-04 08:00 | 2021-01-18 15:40 | 343.6667 | Place T-5 and T-6 back to normal configuration
Rio Grande 7 |  |  |  | 2021-02-06 08:00 | 2021-02-28 23:59 | 543.9833 | Summer prep
Rio Grande 7 |  |  |  | 2021-02-06 08:00 | 2021-03-01 | 543.9997 | Summer prep
Rio Grande 7 |  |  |  | 2021-03-01 | 2021-03-01 13:31 | 13.5167 | Summer prep
Rio Grande 7 |  |  |  | 2021-04-23 22:01 | 2021-04-26 08:12 | 58.1833 | Address a minor tube leak on boiler
Rio Grande 7 |  |  |  | 2021-06-25 20:46 | 2021-06-30 22:28 | 121.7 | Repair hot spot on boiler
Rio Grande 7 | 2020-02-24 | 2020-03-15 | 480 | (A) |  |  | Summer Prep
Rio Grande 8 |  |  |  | 2016-02-04 23:05 | 2016-02-05 11:30 | 12.4167 | Repair main stream drain line
Rio Grande 8 |  |  |  | 2016-04-15 09:21 | 2016-04-15 16:15 | 6.9 | Repair steam leak on boiler drain
Rio Grande 8 |  |  |  | 2016-04-27 21:42 | 2016-04-28 12:45 | 15.05 | Repair leak on boiler blowdown
Rio Grande 8 |  |  |  | 2016-08-01 19:16 | 2016-08-04 13:00 | 65.7333 | Repair boiler leaks and preheater issues
Rio Grande 8 | 2016-07-24 | 2016-08-03 | 240 | 2016-11-14 07:00 | 2016-11-19 14:45 | 127.75 | Preheater work
Rio Grande 8 |  |  |  | 2016-12-30 17:28 | 2016-12-31 17:40 | 24.2 | Repair leak on circulating water line
Rio Grande 8 | 2017-02-11 | 2017-02-24 | 312 | 2017-02-13 10:59 | 2017-03-20 15:00 | 844.0167 | Summer Prep
Rio Grande 8 | 2018-01-06 | 2018-03-30 | 1992 | 2018-01-06 01:50 | 2018-05-22 18:22 | 3280.5333 | Planned Outage- LP Turbine Major
Rio Grande 8 |  |  |  | 2018-10-05 07:00 | 2018-10-06 17:00 | 34 | Substation to repair GSU on ISO-Bus and for Rio Grande to repair Feedwater Leak
Rio Grande 8 | 2018-01-06 | 2018-03-30 | 1992 | 2019-01-05 05:00 | 2019-03-30 | 2011 | Summer Prep/DCS upgrade
Rio Grande 8 | 2020-01-11 | 2020-02-14 | 816 | 2020-01-11 | 2020-02-19 | 936 | Boiler Cleaning and Summer Prep
Rio Grande 8 |  |  |  | 2020-04-15 07:50 | 2020-04-17 00:09 | 40.3167 | Repair Low Pressure Heater issue
Rio Grande 8 |  |  |  | 2020-05-15 23:08 | 2020-05-16 17:30 | 18.3667 | Change out MOOG valve for the left side governor valve on turbine
Rio Grande 8 |  |  |  | 2020-08-22 02:01 | 2020-08-24 11:24 | 57.3833 | Repair Boiler Hot Spots
Rio Grande 8 |  |  |  | 2020-10-29 22:15 | 2020-11-08 01:19 | 219.0667 | Perform Boiler Inspection by Babcock & Wilcox
Rio Grande 8 |  |  |  | 2021-03-19 21:44 | 2021-03-31 23:59 | 290.25 | Summer prep
Rio Grande 8 |  |  |  | 2021-04-01 | 2021-04-16 21:08 | 381.1333 | Summer Prep
Rio Grande 8 | 2021-11-13 | 2022-02-11 | 2160 | 2021-11-12 | in progress |  | Major Inspection - HP/IP/LP Turbine & Valve Inspection
Rio Grande 9 | 2016-04-17 | 2016-04-29 | 288 | 2016-04-17 11:30 | 2016-05-02 | 348.5 | Summer Prep
Rio Grande 9 |  |  |  | 2016-06-14 08:10 | 2016-06-16 | 39.8333 | Testing
Rio Grande 9 |  |  |  | 2016-06-17 06:00 | 2016-06-17 08:19 | 2.3167 | Vibration issues
Rio Grande 9 |  |  |  | 2016-06-30 06:09 | 2016-06-30 10:12 | 4.05 | Due to generator vibration issues
Rio Grande 9 |  |  |  | 2016-06-30 11:49 | 2016-06-30 18:36 | 6.7833 | Testing
Rio Grande 9 |  |  |  | 2016-06-30 20:31 | 2016-07-02 | 27.4833 | Due to generator vibration issues
Rio Grande 9 |  |  |  | 2016-07-08 06:00 | 2016-07-08 08:42 | 2.7 | Testing
Rio Grande 9 |  |  |  | 2016-07-09 06:00 | 2016-07-09 08:05 | 2.0833 | Data collection on generator
Rio Grande 9 |  |  |  | 2016-07-22 07:00 | 2016-10-06 | 1817 | Generator inspection, testing and cleaning
Rio Grande 9 |  |  |  | 2016-10-07 07:00 | 2016-10-08 09:11 | 26.1833 | Install covers on rotor coupling
Rio Grande 9 |  |  |  | 2016-10-25 07:00 | 2016-10-25 12:05 | 5.0833 | Repair evaporative water line
Rio Grande 9 |  |  |  | 2016-12-09 08:21 | 2016-12-09 11:22 | 3.0167 | Software upgrade
Rio Grande 9 |  |  |  | 2017-03-11 08:00 | 2017-03-11 15:00 | 7 | MO for Intercooler Inspection
Rio Grande 9 | 2017-03-04 | 2017-03-17 | 312 | 2017-03-25 06:45 | 2017-04-13 | 449.25 | Summer Prep
Rio Grande 9 |  |  |  | 2017-04-28 07:00 | 2017-04-28 12:00 | 5 | Calibrate a Fire Detector LEL
Rio Grande 9 |  |  |  | 2017-05-27 07:00 | 2017-05-30 14:00 | 79 | Repair Inter Cooler leaks and inspect HP compressor
Rio Grande 9 |  |  |  | 2017-06-12 08:00 | 2017-06-12 09:45 | 1.75 | Addressing insulation issues
Rio Grande 9 |  |  |  | 2017-06-26 07:00 | 2017-06-26 08:15 | 1.25 | Repair NOX water injection leak
Rio Grande 9 |  |  |  | 2017-07-07 06:00 | 2017-07-07 16:15 | 10.25 | Perform water wash
Rio Grande 9 |  |  |  | 2017-07-23 07:00 | 2017-07-23 13:35 | 6.5833 | Check a casing leak
Rio Grande 9 |  |  |  | 2017-08-18 05:00 | 2017-08-18 13:00 | 8 | Replace fuel nozzle
Rio Grande 9 |  |  |  | 2017-09-26 06:30 | 2017-09-26 09:15 | 2.75 | Work on Fire Protection System
Rio Grande 9 |  |  |  | 2017-11-21 07:30 | 2017-11-21 08:00 | 0.5 | CEMS software download
Rio Grande 9 |  |  |  | 2017-12-11 07:00 | 2017-12-12 15:14 | 32.2333 | Repair MLO pump "A" bearing & U9 Water Wash
Rio Grande 9 |  |  |  | 2018-01-19 08:00 | 2018-01-19 09:35 | 1.5833 | Ammonia system switch inspection/replacement
Rio Grande 9 |  |  |  | 2018-02-07 08:00 | 2018-02-07 16:35 | 8.5833 | Needed to visually inspect a vibration probe assembly that was showing erratic readings
Rio Grande 9 |  |  |  | 2018-03-29 07:00 | 2018-03-29 14:30 | 7.5 | Remove Kobelco Gas Compressor in prep for HPTC changeout
Rio Grande 9 | 2018-03-31 | 2018-04-20 | 480 | 2018-03-31 07:00 | 2018-04-21 11:53 | 508.8833 | Summer Prep/Hot Section Exchange
Rio Grande 9 |  |  |  | 2018-04-22 08:00 | 2018-04-22 10:48 | 2.8 | Address oil leaks found in supercore
Rio Grande 9 |  |  |  | 2018-05-04 07:00 | 2018-05-06 18:30 | 59.5 | Repair gas leak
Rio Grande 9 |  |  |  | 2018-05-30 06:00 | 2018-05-30 07:30 | 1.5 | Charge Accumulators and inspect Pull Stations
Rio Grande 9 |  |  |  | 2018-06-23 09:00 | 2018-06-23 13:02 | 4.0333 | Inspect SCR and Catalyst
Rio Grande 9 |  |  |  | 2018-07-12 06:00 | 2018-07-12 13:15 | 7.25 | Boroscope Insp/Vibration Probe Repl
Rio Grande 9 |  |  |  | 2018-07-24 07:30 | 2018-07-24 09:39 | 2.15 | Perform hydraulic lift test requested by GE
Rio Grande 9 |  |  |  | 2018-08-02 07:30 | 2018-08-02 08:44 | 1.2333 | Replace SLO chip detectors
Rio Grande 9 |  |  |  | 2018-08-23 10:00 | 2018-08-23 10:52 | 0.86667 | Test Fire Protection System and troubleshoot the inadvertent release of CO2
Rio Grande 9 |  |  |  | 2018-08-30 07:00 | 2018-08-30 09:05 | 2.0833 | Chage Transmitter on Lube Oil Cooling pumps, grease bearings on turbine enclosure fans and to perform the bi-weekly inspection
Rio Grande 9 |  |  |  | 2018-10-12 07:00 | 2018-10-12 08:02 | 1.0333 | Change Temperating Air Fan and Inspection of VCA filter enclosures
Rio Grande 9 |  |  |  | 2018-11-01 07:00 | 2018-11-01 08:25 | 1.4167 | Check an orifice on the water wash system
Rio Grande 9 |  |  |  | 2018-11-08 08:00 | 2018-11-08 15:52 | 7.8667 | Install De-Icing hoses on Supercore
Rio Grande 9 |  |  |  | 2018-12-11 07:00 | 2018-12-11 10:30 | 3.5 | GE techs on site working on the Jacking Oil System
Rio Grande 9 |  |  |  | 2019-01-04 07:00 | 2019-01-05 09:25 | 26.4167 | Controls Upgrade
Rio Grande 9 |  |  |  | 2019-03-11 07:00 | 2019-03-11 11:50 | 4.8333 | Replace Ammonia Pump
Rio Grande 9 |  |  |  | 2020-02-26 08:00 | 2020-02-27 15:00 | 31 | Replace Generator Filters
Rio Grande 9 | 2020-04-11 | 2020-05-01 | 480 | 2020-03-25 | 2020-04-08 | 336 | Summer Prep
Rio Grande 9 |  |  |  | 2020-04-17 08:00 | 2020-04-23 13:10 | 149.1667 | Water Wash and Generator Testing
Rio Grande 9 |  |  |  | 2020-05-19 20:26 | 2020-05-21 09:00 | 36.5667 | Replace Fuel Nozzle
Rio Grande 9 |  |  |  | 2020-05-22 14:20 | 2020-05-22 15:58 | 1.6333 | Input water mapping and ammonia data
Rio Grande 9 |  |  |  | 2020-06-15 20:57 | 2020-06-16 11:13 | 14.2667 | Due to Kinder-Morgan requesting outage to allow for installation of new pipe
Rio Grande 9 |  |  |  | 2020-07-19 22:16 | 2020-07-20 08:55 | 10.65 | Perform Borescope Inspections
Rio Grande 9 |  |  |  | 2020-07-23 20:54 | 2020-07-24 11:32 | 14.6333 | Rescheduled Borescope Inspection due to Vendor not available 7/19/20
Rio Grande 9 |  |  |  | 2020-08-28 21:54 | 2020-08-31 17:38 | 67.7333 | To troubleshoot loss of MW and Water Wash
Rio Grande 9 |  |  |  | 2020-09-14 07:00 | 2021-01-01 | 2609 | To replace lifting hoses on the J3 oil lines
Rio Grande 9 |  |  |  | 2021-01-01 | 2021-01-31 23:59 | 743.9833 | Replace lifting oil hose
Rio Grande 9 |  |  |  | 2021-02-01 | 2021-02-28 23:59 | 671.9833 | Replace lifting oil hose
Rio Grande 9 |  |  |  | 2021-03-01 | 2021-04-01 | 743.9997 | Replace lifting oil hose
Rio Grande 9 |  |  |  | 2021-04-01 | 2021-04-01 05:23 | 5.3833 | Planned Outage
Rio Grande 9 |  |  |  | 2021-04-28 07:52 | 2021-04-28 13:30 | 5.6333 | Address gas flow meter
Rio Grande 9 |  |  |  | 2021-05-10 08:00 | 2021-05-17 14:00 | 174 | 2nd stage IPT cracked blade
Rio Grande 9 |  |  |  | 2021-05-18 06:35 | 2021-05-19 09:45 | 27.1667 | An enclosure seal test will
Rio Grande 9 |  |  |  | 2021-10-01 07:00 | 2021-10-02 15:19 | 32.3167 | Water Wash and Boroscope Inspection
Rio Grande 9 |  |  |  | 2021-10-13 08:30 | 2021-10-13 10:39 | 2.15 | Opportunity outage to troubleshoot intercooler Vfd
Rio Grande 9 |  |  |  | 2021-12-07 08:00 | 2021-12-07 11:13 | 3.2167 | Inspect and clean the Generator inlet air filters
Rio Grande 9 |  |  |  | 2021-12-08 08:00 | 2021-12-08 09:35 | 1.5833 | Inspect and preform PMs on the U9 turbine enclosure fans
Note: | Schedule reflects a combination of planned and maintenance outages.
(A) Rio Grande 7 Summer Prep outage was completed during the generator rewind forced outage
Rio Grande 6 went into inactive reserve 1/8/2019