## La Quinta
Date | 2020-02-10
Location | La Quinta
Reason | Engineers Request
Observed Flow | 1342.35 | gpm
Notes
Hydrant Flowed No. | F-1078
Residual Hydrant No. | F-1108
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 64
Static psi | 79
Residual psi | 78
discharge Coefficient used is 0.90