## La Quinta 2
Date | 2020-03-10
Location | La Quinta
Reason | Engineers Request
Observed Flow | 1331.8216 | gpm
Notes
Hydrant Flowed No. | F - 1108
Residual Hydrant No. | F - 1078
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 63
Static psi | 80
Residual psi | 78
discharge Coefficient used is 0.90