## Magnolia Phase 2
Date | Magnolia Phase 2
Location
Reason | Engineers Request
Observed Flow | 1299.7248 | gpm
Notes
Hydrant Flowed No. | Next Hydrant East of Risidual
Residual Hydrant No. | End of Crossroads
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 60
Static psi | 89
Residual psi | 79
discharge Coefficient used is 0.90