## Blank
Date
Location
Reason | Engineers Request
Observed Flow | 0 | gpm
Notes
Hydrant Flowed No.
Residual Hydrant No.
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi
Static psi
Residual psi
discharge Coefficient used is 0.90

## 1133 South 34
Date | 2018-05-21
Location | 1551 SH 34 South
Reason | Fire System Requirement
Observed Flow | 2488.7835 | gpm
Notes | John Allen with FIRECAD Performed Flow Test
Hydrant Flowed No. | F-383 | 1551 SH 34 South
Residual Hydrant No. | F-832 | 150 Yards South on SH 34
Outlet Size | 2.5
Number of Outlets Open | 2
Pitot psi | 55
Static psi | 95
Residual psi | 83
discharge Coefficient used is 0.90

## Chilie's Flow Test
Date | 2019-01-24
Location | Chilie's American Way & Center Cir
Reason | Engineers Request
Observed Flow | 1299.7248 | gpm
Notes
Hydrant Flowed No. | FH2 | West American Way
Residual Hydrant No. | FH1 | Center Circle & American Way
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 60
Static psi | 85
Residual psi | 75
discharge Coefficient used is 0.90

## Chilie's Flow Test (2)
Date | 2019-01-24
Location | Chilie's American Way & Center Cir
Reason | Engineers Request
Observed Flow | 1299.7248 | gpm
Notes
Hydrant Flowed No. | FH1 | Center Circle & American Way
Residual Hydrant No. | FH2 | West American Way
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 60
Static psi | 85
Residual psi | 75
discharge Coefficient used is 0.90

## FM 2578 & Windso
Date | 2019-01-25
Location | 2578 & Windsor
Reason | Engineers Request
Observed Flow | 1321.2093 | gpm
Notes
Hydrant Flowed No. | F-343 | Center Circle & American Way
Residual Hydrant No. | F-344 | West American Way
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 62
Static psi | 90
Residual psi | 83
discharge Coefficient used is 0.90

## 705 N. Virginia
Date | 2019-01-25
Location | 705 N. Virginia
Reason | Engineers Request
Observed Flow | 1331.8216 | gpm
Notes
Hydrant Flowed No. | F-654 | Center Circle & American Way
Residual Hydrant No. | F-841 | West American Way
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 63
Static psi | 77
Residual psi | 70
discharge Coefficient used is 0.90

## 705 N. Virginia (2)
Date
Location | 705 N. Virginia (2)
Reason | Engineers Request
Observed Flow | 1299.7248 | gpm
Notes
Hydrant Flowed No. | F-841 | Center Circle & American Way
Residual Hydrant No. | F-654 | West American Way
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 60
Static psi | 78
Residual psi | 71
discharge Coefficient used is 0.90

## Fm 148 And Apache
Date | 3-27.19
Location | FM 148 and Apache Trail
Reason | Engineers Request
Observed Flow | 1373.451 | gpm
Notes
Hydrant Flowed No. | F-27 | F-27
Residual Hydrant No. | F-28 | F-28
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 67
Static psi | 87
Residual psi | 78
discharge Coefficient used is 0.90

## Fm148 & Apache
Date | 3-27.19
Location | FM 148 And Apache Trail
Reason | Engineers Request
Observed Flow | 1373.451 | gpm
Notes
Hydrant Flowed No. | F-28
Residual Hydrant No. | F-27
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 67
Static psi | 86
Residual psi | 75
discharge Coefficient used is 0.90

## 200 Apache Trail
Date | 2019-06-06
Location | 200 Apache Trail Russell Stovers
Reason | Engineers Request
Observed Flow | 1331.8216 | gpm
Notes
Hydrant Flowed No. | F-22 | In front of bldg West
Residual Hydrant No. | F-23 | In front of bldg East
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 63
Static psi | 75
Residual psi | 72
discharge Coefficient used is 0.90

## 200 Apache Trail 2
Date | 2019-06-06
Location | 200 Apache Trail Russell Stover
Reason | Engineers Request
Observed Flow | 1331.8216 | gpm
Notes
Hydrant Flowed No. | F-23 | In front of bldg East
Residual Hydrant No. | F-22 | In front of bldg West
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 63
Static psi | 76
Residual psi | 70
discharge Coefficient used is 0.90

## Academy Sports
Date | 2019-06-13
Location | Academy Sports
Reason
Observed Flow | 0 | gpm
Notes
Hydrant Flowed No.
Residual Hydrant No.
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi
Static psi
Residual psi
discharge Coefficient used is 0.90

## Academy Sports 2
Date | 2019-06-13
Location | Academy Sports 2
Reason | Engineers Request
Observed Flow | 1423.7772 | gpm
Notes |  | Physical Location
Hydrant Flowed No. | F-01 | Behind Academy
Residual Hydrant No. | F-02 | Behind Hobby Lobby
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 72
Static psi | 90
Residual psi | 80
discharge Coefficient used is 0.90

## 151 Windsor
Date | 2019-08-20
Location | 151 Windsor
Reason | Engineers Request
Observed Flow | 0 | gpm
Notes
Hydrant Flowed No.
Residual Hydrant No.
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi
Static psi
Residual psi
discharge Coefficient used is 0.90

## New Platinum Ford
Date | 2019-01-25
Location | New Platinum Ford Dealership
Reason | Engineers Request
Observed Flow | 1266.815 | gpm
Notes
Hydrant Flowed No. | Hydrant A
Residual Hydrant No. | Hydrant B
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 57
Static psi | 78
Residual psi | 70
discharge Coefficient used is 0.90

## Danziesen Dairy S. Virginia 1
Date | 2020-03-18
Location | 1149 S Virginia
Reason | Engineers Request
Observed Flow | 1266.815 | gpm
Notes
Hydrant Flowed No. | F-832
Residual Hydrant No. | F-586
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 57
Static psi | 82
Residual psi | 79
discharge Coefficient used is 0.90

## Danziesen Dairy S Virginia 2
Date | 2020-03-18
Location | 1149 S Virginia
Reason | Engineers Request
Observed Flow | 1266.815 | gpm
Notes
Hydrant Flowed No. | F-586
Residual Hydrant No. | F-832
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 57
Static psi | 79
Residual psi | 73
discharge Coefficient used is 0.90

## La Quinta
Date | 2020-02-10
Location | La Quinta
Reason | Engineers Request
Observed Flow | 1342.35 | gpm
Notes
Hydrant Flowed No. | F-1078
Residual Hydrant No. | F-1108
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 64
Static psi | 79
Residual psi | 78
discharge Coefficient used is 0.90

## La Quinta 2
Date | 2020-03-10
Location | La Quinta
Reason | Engineers Request
Observed Flow | 1331.8216 | gpm
Notes
Hydrant Flowed No. | F - 1108
Residual Hydrant No. | F - 1078
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 63
Static psi | 80
Residual psi | 78
discharge Coefficient used is 0.90

## Crossroads Apartment 1
Date | 2020-03-18
Location | Crossroads Apartments 1
Reason | Engineers Request
Observed Flow | 1373.451 | gpm
Notes
Hydrant Flowed No. | F1 | North Hydrant closest to Crossroads
Residual Hydrant No. | F2 | South Hydrant
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 67
Static psi | 85
Residual psi | 77
discharge Coefficient used is 0.90

## Crossroads Apartment 2
Date | 2020-03-18
Location | Crossroads Apartments 1
Reason | Engineers Request
Observed Flow | 1363.1629 | gpm
Notes
Hydrant Flowed No. | F2 | South Hydrant
Residual Hydrant No. | F1 | North Hydrant closest to Crossroads
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 66
Static psi | 80
Residual psi | 75
discharge Coefficient used is 0.90

## MJ Pipline 1
Date | 2020-05-13
Location | Temple St MJ Pipeline Project 1
Reason | Engineers Request
Observed Flow | 1491.3835 | gpm
Notes
Hydrant Flowed No. | F-1046
Residual Hydrant No. | F-1047
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 79
Static psi | 75
Residual psi | 65
discharge Coefficient used is 0.90

## MJ Pipeline 2
Date | 2020-05-13
Location | Temple St MJ pipeline Project 2
Reason | Engineers Request
Observed Flow | 1500.7929 | gpm
Notes
Hydrant Flowed No. | F-1047
Residual Hydrant No. | F-1046
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 80
Static psi | 78
Residual psi | 70
discharge Coefficient used is 0.90

## Poetry Rd 1
Date | 2021-03-03
Location | Poetry Rd
Reason | Engineers Request
Observed Flow | 1087.4278 | gpm
Notes
Hydrant Flowed No. | F - 155
Residual Hydrant No. | F - 157
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 42
Static psi | 60
Residual psi | 55
discharge Coefficient used is 0.90

## Poetry Rd 2
Date | 2021-03-03
Location | Poetry Rd
Reason | Engineers Request
Observed Flow | 1074.4042 | gpm
Notes
Hydrant Flowed No. | F - 257
Residual Hydrant No. | F - 255
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 41
Static psi | 59
Residual psi | 55
discharge Coefficient used is 0.90

## Windsor
Date | 2021-03-19
Location
Reason | Engineers Request
Observed Flow | 1006.7625 | gpm
Notes
Hydrant Flowed No. | F-693 | Corner of Adams
Residual Hydrant No. | F-701 | Entrance to Terrell Senior Living
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 36
Static psi | 65
Residual psi | 45
discharge Coefficient used is 0.90

## Platnium Chevy
Date | 2021-05-25
Location
Reason | Engineers Request
Observed Flow | 1244.3918 | gpm
Notes
Hydrant Flowed No. | F-1
Residual Hydrant No. | F-2
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 55
Static psi | 93
Residual psi | 65
discharge Coefficient used is 0.90

## Blank (2)
Date | 2021-07-14
Location | Proposed Texas Roadhouse
Reason | Engineers Request
Observed Flow | 1582.9631 | gpm
Notes
Hydrant Flowed No. | 1105
Residual Hydrant No. | 1104
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 89
Static psi | 95
Residual psi | 65
discharge Coefficient used is 0.90

## Blank (3)
Date | 2021-07-14
Location | Propposed Texas Roadhouse
Reason | Engineers Request
Observed Flow | 1352.7965 | gpm
Notes
Hydrant Flowed No. | 1104
Residual Hydrant No. | 1105
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 65
Static psi | 87
Residual psi | 81
discharge Coefficient used is 0.90

## Magnolia Phase 2
Date | Magnolia Phase 2
Location
Reason | Engineers Request
Observed Flow | 1299.7248 | gpm
Notes
Hydrant Flowed No. | Next Hydrant East of Risidual
Residual Hydrant No. | End of Crossroads
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 60
Static psi | 89
Residual psi | 79
discharge Coefficient used is 0.90

## Jamison Ct
Date | 2021-11-02
Location | Jamison Court
Reason | Engineers Request
Observed Flow | 1244.3918 | gpm
Notes
Hydrant Flowed No. | F-461
Residual Hydrant No. | F460
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 55
Static psi | 80
Residual psi | 75
discharge Coefficient used is 0.90