## Crossroads Apartment 1
Date | 2020-03-18
Location | Crossroads Apartments 1
Reason | Engineers Request
Observed Flow | 1373.451 | gpm
Notes
Hydrant Flowed No. | F1 | North Hydrant closest to Crossroads
Residual Hydrant No. | F2 | South Hydrant
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 67
Static psi | 85
Residual psi | 77
discharge Coefficient used is 0.90